## General
Future 1: Business As Usual
Information in this file is based on the Google Doc as of 3/17/11. Data change since 2/18/11 are new demands for New England and fixed DR for ENT region (in Feb.) and 3/17/11 minor updates to Table 6, Exhibit 6, Exibit 6A, Exhibit 7, Exhibit 8, and Exhibit 18.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Worksheet Name | Sub-Group | Leader | Coordinator Comments on 1-25-2011 Version | Subteam Leader Comments on 1-25-2011 Version
Exhibit1_2006 load shapes | Demands | King Look | Updated
Exhibit2_Top10hours | Demands | King Look | Updated
Exhibit3_Control Ent to NEEM | NEEM Regions | Mary Ellen Paravalos | Updated
Exhibit4_WindShapes | New Generation | Samir Succar | Updated, Added potential Class 3 2/8/11
Exhibit4_WindShapes | Existing Generation | Doug Kallesen | Onshore updated, offshore awaiting data | Existing Gen subteam has requests of CRA in col G. Otherwise, is deferring to New Gen subteam. SAMIR-if you want any help from us, let me know...Doug K.
Exhibit5_BAs to NEEM Regions | NEEM Regions | Mary Ellen Paravalos | Updated
Exhibit6_ExistingUnits | Existing Generation | Doug Kallesen | Updated 3/17/11 from CRA | OK with Existing Gen subteam --- we understand the previous version had errors due to preivous NEEM region mapping bugs.
Exhibit6a_CoalUnit Detail | Existing Generation | Doug Kallesen | Updated 3/17/11 from CRA
Exhibit7_ForcedNewBuilds | Existing Generation | Doug Kallesen | Updated 3/17/11 from CRA
Exhibit8_ForcedRetirements | Existing Generation | Doug Kallesen | Updated 3/17/11 from CRA
Exhibit9_CapitalCostDetail | New Generation | Samir Succar | Changed Learning rate for Wind and transmission cost so all technologies match. Calculated intermediate costs in table below the main table. Copied the results to the Table 7 sheet.
Exhibit10_RegionalMultipliers | New Generation | Samir Succar | updated regions | Modified NEISO values based on average of cities in the region
Exhibit11_WindCF & Potential | New Generation | Samir Succar | Updated, possible Class 3 and Class 4 capacities added 2/8/11
Exhibit12_NewResourceLimits | New Generation | Samir Succar | Updated additional values (in yellow) 2/3/11
Exhibit13_RetrofitCosts (+Table 8-10) | Existing Generation | Doug Kallesen | No change from previous | OK with Ex Gen, except see our requests of CRA listed under Tables 8-10)
Exhibit13_RetrofitCosts (+Table 8-10) | Environmental | Paul McCurley | No change from previous
Exhibit14_ForcedRetrofits | Existing Generation | Doug Kallesen | Updated | OK with Existing Generation
Exhibit15_NuclearUprates | Existing Generation | Doug Kallesen | Ex Gen inserted new tab from CRA dated 2-3 on 2-8. | OK with Existing Generation
Exhibit16A_HHNaturalGasPrices | Fuel Prices | King Look | CRA split into 16a (annual) and 16b (seasonal). Prices in 16a updated to 2010$ and alternate schedule calculated | CRA updated 16b to use AEO 2011 regional prices.
Exhibit16B_NEEMRegionGasPrices | Fuel Prices | King Look
Exhibit16C_AEORegionGasPrices | Fuel Prices | King Look | Switched from old natural gas basis to listing electric sector natural gas prices by AEO region
Exhibit17_TransferLimits | NEEM Regions | Mary Ellen Paravalos
Exhibit18_WheelCost&TransCost | NEEM Regions | Mary Ellen Paravalos | Updated 3/17/11 from CRA
Exhibit19_CanadianHydro-Wind | NEEM Regions | Mary Ellen Paravalos | Under review, HQ hydro parameters added
Exhibit20 Demand Response Percentages | Demand, EE, DR | King Look | Added 2/8/11. Fixed ENT calculation 3/4/11
Exhibit21_MRN Inputs | Demands | King Look | Updated 2/3/11 for Light Duty trucks
Exhibit22_RPS Summary | Environmental | Paul McCurley/Tyler Ruthven | Separate PDF file
Exhibit23_EPA_RegulationsModeling | Environmental | Paul McCurley/Tyler Ruthven | Not in CRA spreadsheet
Exhibit 24 Carbon Modeling | Environmental | Paul McCurley/Tyler Ruthven | Not in CRA spreadsheet
Exhibit 25 Renewable Incentives | Environmental | Paul McCurley/Tyler Ruthven
Exhibit26 EE Energy Targets | Demands | King Look
Exhibit27 EE Peak Targets | Demands | King Look
Table1_LoadBlocks | Demands | King Look | No change from previous
Table2_Demand | Demands | King Look | Updated 3/3/11 for New England estimates | CRA updated 2020-2050 growth rate to match AEO 2011 growth rate
Table3_Peak | Demands | King Look | Updated 3/3/11 for New England estimates | CRA updated 2020-2050 growth rate to match AEO 2011 growth rate
Table4_OM | Existing Generation | Doug Kallesen | Updated | Proposal for adder to coal VOM for coal ash is given in tab, rest ok with Ex Gen.
Table5_Intermittent Renewable Resource Contributions | New Generation | Samir Succar | Updated, new values for OH and TVA
Table5_Intermittent Renewable Resource Contributions | Existing Generation | Doug Kallesen | Updated, new values for OH and TVA | Existing Gen suteam is deferring to New Gen subteam. SAMIR-if you want any help from us, let me know...Doug K.
Table6_InstalledCapacity | Existing Generation | Doug Kallesen | Updated 3/17/11 from CRA | OK with Existing Gen subteam, but some documentation requests for CRA are noted on tab.
Table 7_NewBuildCostParameters | New Generation | Samir Succar | 2/18/11 Updated costs to match Exhibit 9
Table11_CCSRetro | Existing Generation | Doug Kallesen | No change from previous | OK with Ex Gen but we have requested CRA to better document retirement/retrofit logic for the three policies described in text under Table 11.
Table 12_FCR | Discount rates | Erin Hogan | No change from previous
Table13_CAIRIV | Environmental | Paul McCurley | No change from previous
Table14_IntermittentGenLimits | New Generation | Samir Succar | Updated
Table15_Reserve Margin | NEEM Regions | Mary Ellen Paravalos | Updated
Table15_Reserve Margin | Demands | King Look | Updated
Table16_MMCoalPricesIndicative | Fuel Prices | King Look | No change from previous
Table17_CoalCharacteristics | Fuel Prices | King Look | No change from previous
Table18_MRN-NEEMRegions | NEEM Regions | Mary Ellen Paravalos
Tables19-22 not in spreadsheet
Table23-24_Elasticities | Discount rates | Erin Hogan | Updated
Tables and Figures from pdf but not in Workbook
Label | Sub-Group | Leader
Figure 01 _Circular Flow of Goods and Services and Payment | [none] |  | Not in CRA spreadsheet
Figure 02_MRN-NEEM Iterative Process | [none] |  | Not in CRA spreadsheet
Figure 03_NEEM Regions | NEEM Regions | Paravolos | Not in CRA spreadsheet
Figure 04_Application of CAIR Caps | Environmental Policies | McCurley | Not in CRA spreadsheet
Figure 05_NEEM Coal Production Regions | Fuel & Emission Prices | Look | Not in CRA spreadsheet
Figure 06_Circular Flow of Goods and Services and Payment | [none] |  | Not in CRA spreadsheet
Figure 07_Illustrative Example of How MRN Regions Map to NEEM | Discount rates | Hogan | Not in CRA spreadsheet
Figure 08_GDP Growth Index - United States | Discount rates | Hogan | Not in CRA spreadsheet
Figure 09_VMT for Light-Duty Vehicles | Demand, EE, DR | Look | Not in CRA spreadsheet
Figure 10_PHEV and BEV Penetration | Demand, EE, DR | Look | Not in CRA spreadsheet
Table 08_Example of FGD Retrofit Costs | Environmental Policies / Existing Generation | McCurley/Kallesen | Not in CRA spreadsheet | OK with Ex Gen but we have requested CRA to provide their equation for FGD for other sizes (like they do for Tables 9,10).
Table 09_Example of SCR Retrofit Costs | Environmental Policies / Existing Generation | McCurley/Kallesen | Not in CRA spreadsheet | OK with Ex Gen.
Table 10_Example of HG Retrofit Costs | Environmental Policies / Existing Generation | McCurley/Kallesen | Not in CRA spreadsheet | OK with Ex Gen.
Table 19_MRN Model's Sectors in MRN-NEEM Integrated Model | Discount rates | Erin Hogan | Not in CRA spreadsheet
Table 20_Typical MRN Model's Sectors | Discount rates | Erin Hogan | Not in CRA spreadsheet
Table 21_Average and Marginal State Taxes on Capital and Labor Income | Discount rates | Erin Hogan | Not in CRA spreadsheet
Table 22_Average and Marginal Federal Taxes on Capital and Labor Income | Discount rates | Erin Hogan | Not in CRA spreadsheet
Appendix B_Sectoral mapping of IMPLAN Sectors based on NAICS 2002 | Discount rates | Erin Hogan | Not in CRA spreadsheet
RPS Imports | Environmental | Tyler Ruthven | Moved to Appendix C document
RPS Existing | Environmental | Tyler Ruthven | Moved to Appendix C document
RPS New | Environmental | Tyler Ruthven | Moved to Appendix C document
Assuming Modeling/SSC agree, have CRA drop information that are ouside the EI, e.g., Tables 2, 3, 6, 15, 21, and Appendix A Exhbits 3,5,11,12,15 and 17 (suggestion of Doug Kallesen). | Assuming action at left, add to Table 2&3 (total GWh/MW and weighted average growth rates), Exh 1 & 4-columns of weighted average annual load/capacity factors, Exh 6-8 (grand total, subtotals by Gen Type and NEEM region), Exh 11-separate totals and weighted average capacity factors for onshore and offshore, and Canadian entries. (Doug Kallesen)
Sensitivity Worksheets are in a separate BAU Sensitivities workbook to capture the data that changes from this BAU document. This will allow the BAU document to be locked as finalized once data is complete. (SW Hadley: 2-10-11)
F1S1_Revise_Xfer | NEEM Regions | Mary Ellen Paravalos
F1S2__Xfer_Barriers | NEEM Regions | Mary Ellen Paravalos
F1S3_High_Load | Demands | King Look
F1S4_Low_Load | Demands | King Look
F1S5_High_Gas$ | Fuel Prices | King Look
F1S6_Increase_RPS | Environmental | Paul McCurley
F1S7_High_PHEV | Demands | King Look
F1S8_Low_Ren_Cap$ | New Generation | Samir Succar
Ex Gen: BAU Sensitivities1,2,3,4,6,7 |  | Doug Kallesen
Ex Gen: BAU Sensitivity 5 - High Gas |  | Doug Kallesen
Ex Gen: BAU Sensitivity 8 - Incr Gen Cost |  | Doug Kallesen
Ex Gen: BAU Sensitivity 9 - No new non-CO2 EPA Regs |  | Doug Kallesen
Table 25 HQ and Maritimes Energy transfers

## Exhibit1_2006 load shapes
Appendix A, Exhibit 1 - 2006 Load Shapes
Based on eastern interconnection sorting.
*ExGen added note at bottom on 2006 choice
By Load Blocks - Eastern Interconnection Regions
Average Load during block relative to average of highest block
| Season | Summer | [9 empty] | Shoulder |  |  |  |  | Winter
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20
ENT | 2011 | 1 | 0.99576 | 0.94636 | 0.94637 | 0.91019 | 0.86162 | 0.82448 | 0.77365 | 0.69836 | 0.60079 | 0.82161 | 0.68073 | 0.62881 | 0.59432 | 0.53162 | 0.74692 | 0.68673 | 0.64746 | 0.61253 | 0.56111
FRCC | 2011 | 1 | 0.94335 | 0.91416 | 0.90032 | 0.87603 | 0.8315 | 0.79278 | 0.74336 | 0.67381 | 0.51529 | 0.79997 | 0.6798 | 0.6309 | 0.58262 | 0.4447 | 0.70437 | 0.63153 | 0.58172 | 0.55154 | 0.44971
MAPP_US | 2011 | 1 | 1.0643 | 1.0581 | 1.0048 | 0.96016 | 0.90533 | 0.85245 | 0.78403 | 0.721 | 0.62666 | 0.79245 | 0.85142 | 0.83746 | 0.80628 | 0.71531 | 0.99556 | 1.0108 | 0.98868 | 0.94377 | 0.78191
MISO_IN | 2011 | 1 | 0.98609 | 0.92711 | 0.87542 | 0.84209 | 0.78465 | 0.71636 | 0.65158 | 0.59119 | 0.51439 | 0.69454 | 0.65654 | 0.63156 | 0.59359 | 0.52127 | 0.80565 | 0.7369 | 0.68256 | 0.63651 | 0.55954
MISO_MI | 2011 | 1 | 0.92108 | 0.82932 | 0.77161 | 0.7296 | 0.68985 | 0.64711 | 0.60735 | 0.56479 | 0.48547 | 0.60472 | 0.60174 | 0.58503 | 0.53924 | 0.45008 | 0.7137 | 0.65358 | 0.62175 | 0.57373 | 0.47301
MISO_MO-IL | 2011 | 1 | 0.96388 | 0.88197 | 0.82273 | 0.79535 | 0.73326 | 0.68152 | 0.61715 | 0.54274 | 0.45754 | 0.70523 | 0.5862 | 0.55257 | 0.51751 | 0.44512 | 0.74156 | 0.65334 | 0.60524 | 0.55988 | 0.49172
MISO_W | 2011 | 1 | 1.0583 | 1.0173 | 0.95764 | 0.90558 | 0.83741 | 0.78471 | 0.70206 | 0.63366 | 0.53276 | 0.73538 | 0.70632 | 0.68634 | 0.63836 | 0.54239 | 0.86765 | 0.79815 | 0.77075 | 0.70783 | 0.54465
MISO_WUMS | 2011 | 1 | 0.98451 | 0.90702 | 0.83844 | 0.78661 | 0.74042 | 0.69281 | 0.64586 | 0.59575 | 0.49468 | 0.66725 | 0.65695 | 0.63726 | 0.58782 | 0.48135 | 0.77307 | 0.70772 | 0.67325 | 0.6247 | 0.51286
NE | 2011 | 1 | 1.0313 | 1.0126 | 0.98891 | 0.95118 | 0.90782 | 0.86546 | 0.79473 | 0.71727 | 0.60996 | 0.77237 | 0.70304 | 0.67942 | 0.63498 | 0.5424 | 0.79694 | 0.74238 | 0.72064 | 0.68483 | 0.59064
NEISO | 2011 | 1 | 0.93543 | 0.86035 | 0.78518 | 0.74775 | 0.7034 | 0.65252 | 0.6137 | 0.56474 | 0.44954 | 0.63011 | 0.62418 | 0.59917 | 0.55534 | 0.4354 | 0.71805 | 0.68271 | 0.65612 | 0.60553 | 0.4861
NYISO_A-F | 2011 | 1 | 0.95234 | 0.90181 | 0.84266 | 0.80839 | 0.77326 | 0.73367 | 0.70683 | 0.66956 | 0.56588 | 0.72713 | 0.74181 | 0.71525 | 0.67122 | 0.55914 | 0.82254 | 0.80076 | 0.77586 | 0.73023 | 0.6153
NYISO_G-I | 2011 | 1 | 0.94951 | 0.85163 | 0.78024 | 0.74758 | 0.69779 | 0.64864 | 0.60934 | 0.55725 | 0.44533 | 0.60358 | 0.5864 | 0.55592 | 0.51723 | 0.41074 | 0.65901 | 0.62548 | 0.60735 | 0.56329 | 0.46131
NYISO_J-K | 2011 | 1 | 0.95923 | 0.87411 | 0.79653 | 0.76337 | 0.70546 | 0.64123 | 0.59684 | 0.54024 | 0.42941 | 0.59476 | 0.54972 | 0.5321 | 0.48713 | 0.38344 | 0.57694 | 0.55145 | 0.5451 | 0.51609 | 0.41131
NonRTO_Midwest | 2011 | 1 | 0.98064 | 0.93033 | 0.88805 | 0.85696 | 0.80815 | 0.74991 | 0.69565 | 0.62725 | 0.52924 | 0.74494 | 0.70777 | 0.65788 | 0.61301 | 0.52917 | 0.93256 | 0.83631 | 0.75692 | 0.68718 | 0.60473
PJM_E | 2011 | 1 | 0.95983 | 0.86791 | 0.79966 | 0.76765 | 0.70823 | 0.64267 | 0.59216 | 0.53822 | 0.4387 | 0.58025 | 0.55212 | 0.5262 | 0.4875 | 0.39909 | 0.63502 | 0.60061 | 0.57477 | 0.53323 | 0.44649
PJM_ROM | 2011 | 1 | 0.97114 | 0.90843 | 0.8528 | 0.82693 | 0.78291 | 0.71923 | 0.66908 | 0.61916 | 0.51258 | 0.68344 | 0.67217 | 0.64123 | 0.59686 | 0.4957 | 0.83292 | 0.7765 | 0.7187 | 0.66433 | 0.56544
PJM_ROR | 2011 | 1 | 0.95893 | 0.8888 | 0.83789 | 0.80454 | 0.76036 | 0.70508 | 0.65775 | 0.60644 | 0.51207 | 0.67512 | 0.66137 | 0.63074 | 0.58776 | 0.50056 | 0.81416 | 0.75209 | 0.69437 | 0.64351 | 0.55728
SOCO | 2011 | 1 | 0.97549 | 0.9617 | 0.93821 | 0.90685 | 0.86052 | 0.80086 | 0.73378 | 0.65013 | 0.52775 | 0.74883 | 0.64794 | 0.59541 | 0.55455 | 0.47285 | 0.80086 | 0.70818 | 0.62904 | 0.57883 | 0.51172
SPP_N | 2011 | 1 | 0.98041 | 0.93545 | 0.90736 | 0.86887 | 0.81082 | 0.76371 | 0.6992 | 0.61797 | 0.51008 | 0.75955 | 0.60932 | 0.57362 | 0.53721 | 0.4508 | 0.7124 | 0.63797 | 0.61034 | 0.57657 | 0.49752
SPP_S | 2011 | 1 | 0.99519 | 0.95816 | 0.9462 | 0.89651 | 0.8364 | 0.79208 | 0.73259 | 0.65354 | 0.55215 | 0.77315 | 0.61885 | 0.57877 | 0.54907 | 0.4785 | 0.70411 | 0.63975 | 0.60667 | 0.57536 | 0.518
TVA | 2011 | 1 | 0.98158 | 0.94158 | 0.92584 | 0.88397 | 0.82448 | 0.76345 | 0.705 | 0.62924 | 0.53279 | 0.74599 | 0.68117 | 0.63407 | 0.59765 | 0.52678 | 0.92072 | 0.79935 | 0.70187 | 0.6439 | 0.57986
VACAR | 2011 | 1 | 0.96996 | 0.93697 | 0.89428 | 0.8594 | 0.81069 | 0.7369 | 0.67737 | 0.61023 | 0.4959 | 0.67154 | 0.64054 | 0.58828 | 0.55135 | 0.47235 | 0.84324 | 0.74552 | 0.64747 | 0.59063 | 0.52469
MAPP_CA | 2011 | 1 | 1.0137 | 1.0118 | 0.99346 | 0.9787 | 0.95661 | 0.93377 | 0.90127 | 0.85345 | 0.75318 | 0.89782 | 0.96463 | 0.94882 | 0.91349 | 0.81042 | 1.0777 | 1.0933 | 1.0763 | 1.0434 | 0.93088
IESO | 2011 | 1 | 0.95599 | 0.89414 | 0.85493 | 0.82517 | 0.80008 | 0.76978 | 0.73611 | 0.69934 | 0.60364 | 0.76457 | 0.78562 | 0.76078 | 0.7156 | 0.60337 | 0.88247 | 0.85828 | 0.83043 | 0.7809 | 0.65668
*ExGen researched question raised concerning adequacy of 2006 wind/load shape choice. Reason being that MISO reported an unusually high wind from a fast moving front in their area around the time of the 2006 summer peak load. Would that inappropriately model too much wind during a normally low wind period? MISO staff provided specific peak timing as 5:00 CDT on 7-31, 2006 and info on those high winds at the time. However CRA model's top ten EI peak hours (Exh 2) only have one of the ten as being from July 31, and that being the lowest of the ten. Other top 10 EI hourly loads are during the next two days and July 17, so Ex Gen agreed that there is not significant overlap between the peaks and the high winds to worry about. More details available from Ex Gen, if desired.

## Exhibit2_Top10hours
Appendix A, Exhibit 2 - Top 10 hours (load block 1)
Hours in Top Load Block, B1
Descending Order in 2006 Load Shape
Based on total Eastern Interconnection Load
Hour No. | Date | Hour (1-24)
1 | 2006-08-02 | 17
2 | 2006-08-01 | 17
3 | 2006-08-02 | 16
4 | 2006-08-01 | 16
5 | 2006-08-02 | 18
6 | 2006-08-01 | 18
7 | 2006-08-02 | 15
8 | 2006-08-01 | 15
9 | 2006-07-17 | 17
10 | 2006-08-02 | 14 | Note: the change is b/c of the updated NEISO forecast - it altered the EIC-wide load sorting a small amount.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit3_Control Ent to NEEM
Appendix A, Exhibit 3 - Mapping of Control Entities to NEEM Regions (for load mapping)
Planning Area | NEEM Region
Arizona Electric Power Coop Inc | AZ_NM_SNV
Arizona Public Service Co | AZ_NM_SNV
El Paso Electric Co | AZ_NM_SNV
Nevada Power Co | AZ_NM_SNV
Public Service Co of New Mexico | AZ_NM_SNV
Salt River Project | AZ_NM_SNV
Tucson Electric Power Co | AZ_NM_SNV
WAPA Lower Colorado Region | AZ_NM_SNV
Associated Electric Coop Inc | ENT
City of Conway | ENT
Entergy Services Inc | ENT
North Little Rock AR (City of) | ENT
Sam Rayburn G&T Electric Coop Inc | ENT
Clarksdale Public Utilities Commission | ENT
Louisiana Generating LLC | ENT
ERCOT | ERCOT
Florida Municipal Power Agency | FRCC
Florida Power & Light Co | FRCC
Gainesville Regional Utilities | FRCC
JEA | FRCC
Lakeland Dept of Electric Water Utilities | FRCC
Orlando Utilities Commission | FRCC
Progress Energy (Florida Power Corp.) | FRCC
Seminole Electric Coop Inc | FRCC
St Cloud (City of) | FRCC
Tallahassee FL (City of) | FRCC
Tampa Electric Co | FRCC
Basin Electric Power Cooperative | MAPP_US
Heartland Consumers Power District | MAPP_US
Minnkota Power Coop | MAPP_US
Missouri River Energy Services | MAPP_US
NorthWestern Energy (South Dakota) | MAPP_US
Square Butte Electric Coop | MAPP_US
WAPA Upper Great Plains East | MAPP_US
Big Rivers Electric Corp | MISO_IN
Duke Energy Corp. (INDIANA) | MISO_IN
Hoosier Energy REC, Inc. | MISO_IN
Indiana Municipal Power Agency | MISO_IN
Indianapolis Power & Light Company | MISO_IN
Northern Indiana Public Service Company | MISO_IN
Southern Indiana Gas & Electric Company | MISO_IN
Wabash Valley Power Association | MISO_IN
Consumers Energy Company | MISO_MI
Detroit Edison Company | MISO_MI
Wolverine Power Supply Coop Inc | MISO_MI
Ameren (Illinois Power Co. Control Area) | MISO_MO-IL
Ameren Corporation Control Area | MISO_MO-IL
City of Springfield | MISO_MO-IL
Columbia (MO) Water & Light | MISO_MO-IL
Southern Illinois Power Coop | MISO_MO-IL
Algona Municipal Utilities | MISO_W
Allete (Minnesota Power) | MISO_W
Alliant Energy-West | MISO_W
Ames Municipal Electric System | MISO_W
Atlantic Municipal Utilities | MISO_W
Central Minnesota Municipal Power Agency | MISO_W
Dairyland Power Coop | MISO_W
Great River Energy | MISO_W
Harlan Municipal Utilities | MISO_W
Hutchinson Utilities Commission | MISO_W
Marshall Municipal Utilities | MISO_W
MidAmerican Energy Company | MISO_W
Minnesota Municipal Power Agency | MISO_W
Montana-Dakota Utilities Company | MISO_W
Muscatine Power & Water | MISO_W
New Ulm Public Utilities | MISO_W
Northern States Power Company | MISO_W
Otter Tail Power Company | MISO_W
Pella (City of) | MISO_W
Rochester Public Utilities | MISO_W
Southern Minnesota Municipal Power Agency | MISO_W
Willmar Municipal Utilities Commission | MISO_W
Alliant Energy-East | MISO_WUMS
Madison Gas & Electric Company | MISO_WUMS
Upper Peninsula Power Company | MISO_WUMS
Wisconsin Electric Power Company | MISO_WUMS
Wisconsin Public Service Corporation | MISO_WUMS
WPPI Energy | MISO_WUMS
Hastings Utilities (NE) | NE
Lincoln Electric System | NE
Municipal Energy Agency of Nebraska | NE
Nebraska Public Power District | NE
Omaha Public Power District | NE
NEISO | NEISO
Commonwealth Edison | PJM_ROR
Buckeye Power Inc | NonRTO_Midwest
East Kentucky Power Coop Inc | NonRTO_Midwest
Louisville Gas & Electric Co | NonRTO_Midwest
Ohio Valley Electric Corp | NonRTO_Midwest
Modesto Irrigation District | NP15
Pacific Gas & Electric Co | NP15
Sacramento Municipal Utility District | NP15
Turlock Irrigation District | NP15
Avista Corp | NWPP
Bonneville Power Administration | NWPP
Eugene Water & Electric Board | NWPP
Idaho Power Co | NWPP
NorthWestern Energy | NWPP
PacifiCorp | NWPP
Portland General Electric Co | NWPP
PUD No 1 of Chelan County | NWPP
PUD No 1 of Douglas County | NWPP
PUD No 2 of Grant County | NWPP
Puget Sound Energy Inc | NWPP
Seattle City Light | NWPP
Sierra Pacific Power Co | NWPP
Tacoma Power | NWPP
WAPA Upper Great Plains West | NWPP
NYISO Zone A | NYISO_A-F
NYISO Zone B | NYISO_A-F
NYISO Zone C | NYISO_A-F
NYISO Zone D | NYISO_A-F
NYISO Zone E | NYISO_A-F
NYISO Zone F | NYISO_A-F
NYISO Zone G | NYISO_G-I
NYISO Zone H | NYISO_G-I
NYISO Zone I | NYISO_G-I
NYISO Zone J | NYISO_J-K
NYISO Zone K | NYISO_J-K
Atlantic Electric | PJM_E
Delmarva Power & Light | PJM_E
Jersey Central | PJM_E
PECO | PJM_E
Public Service | PJM_E
Rockland Electric | PJM_E
Baltimore Gas & Electric | PJM_ROM
Metropolitan Edison | PJM_ROM
PennElec | PJM_ROM
PEPCO | PJM_ROM
PP&L and UGI | PJM_ROM
Allegheney Power | PJM_ROR
American Electric Power | PJM_ROR
American Municipal Power-Ohio, Inc. | PJM_ROR
Dayton Power & Light | PJM_ROR
Dominion | PJM_ROR
Duke Energy Corp. (OHIO/KENTUCKY) | PJM_ROR
Duquesne Light Company | PJM_ROR
First Energy | PJM_ROR
Black Hills Corp | RMPA
Colorado Springs Utilities | RMPA
Platte River Power Authority | RMPA
Public Service Co of Colorado | RMPA
Tri State G & T Association Inc | RMPA
WAPA Rocky Mountain Region | RMPA
Alabama Power Co | SOCO
Georgia Power Co | SOCO
Gulf Power Co | SOCO
Mississippi Power Co | SOCO
Oglethorpe Power Corp | SOCO
PowerSouth Energy Coop | SOCO
South Mississippi Electric Power Association | SOCO
Southern Power Co | SOCO
MEAG Power | SOCO
Burbank (City of) | SP15
Imperial Irrigation District | SP15
Los Angeles Dept of Water & Power | SP15
Metropolitan Water District | SP15
San Diego Gas & Electric Co | SP15
Southern California Edison | SP15
City of Independence MO | SPP_N
City Utilities of Springfield (MO) | SPP_N
Empire District Electric Co (The) | SPP_N
Kansas City KS (City of) | SPP_N
Kansas City Power & Light Co | SPP_N
KCP&L Greater Missouri Operations | SPP_N
Sunflower Electric Power Corp | SPP_N
Westar Energy (KPL) | SPP_N
American Electric Power Co Inc (AEP West) | SPP_S
Cleco Corp | SPP_S
Golden Spread Electric Coop Inc | SPP_S
Grand River Dam Authority | SPP_S
Lafayette Utilities System | SPP_S
Louisiana Energy & Power Authority | SPP_S
Northeast Texas Electric Coop Inc | SPP_S
Oklahoma Gas & Electric Co | SPP_S
Oklahoma Municipal Power Authority | SPP_S
Southwestern Power Administration | SPP_S
Southwestern Public Service Co | SPP_S
Tex La Electric Coop of Texas Inc | SPP_S
Western Farmers Electric Coop | SPP_S
Arkansas Electric Cooperative | SPP_S
Fayetteville Public Service | TVA
Tennessee Valley Authority | TVA
Central Electric Power Coop Inc | VACAR
Duke Energy Carolinas LLC | VACAR
Greenville Utilities Commission | VACAR
Progress Energy Carolina | VACAR
South Carolina Electric & Gas | VACAR
South Carolina Public Service Authority | VACAR
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit4_WindShapes
Appendix A, Exhibit 4 - NEEM Wind Shapes (Existing Units and New Installations)
Waiting for a revised table with updated NEEM regions, resorted according to EI load, and including data for missing entries as noted by CRA and other missing entries as noted by the subteam [onshore-MAPP_US, MAPP_CA, & OH; offshore-OH and MAPP_CA]. Also adding a column for annual capacity factor. LASTLY CRA should explain in report its use of EWITS (detailed request at bottom). (Ex Gen)[This note is based on 12-22-10 version of table that included preliminary plant list.]
No change for BAU sensitivities 1-9. (Ex Gen)
Sorted into load blocks based on a EIC load in 2006.
Wind Capacity Factors by Block - Eastern Interconnection
(Blanks indicate no onshore/offshore wind potential in the region)
ONSHORE WIND Class 4+ |  | Summer | [9 empty] | Shoulder |  |  |  |  | Winter |  |  |  |  | Annual
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935 | Capacity Factor
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | (calculated)
ENT | All | 14% | 9% | 13% | 13% | 13% | 17% | 16% | 22% | 27% | 34% | 17% | 30% | 30% | 36% | 47% | 41% | 40% | 36% | 38% | 46% | 0.34
FRCC | All | [20 empty] | 0
IESO | All | 45% | 32% | 21% | 20% | 20% | 19% | 20% | 20% | 23% | 22% | 25% | 33% | 32% | 33% | 33% | 39% | 37% | 38% | 36% | 33% | 0.29
MAPP_CA | All | 45% | 32% | 21% | 20% | 20% | 19% | 20% | 20% | 23% | 22% | 25% | 33% | 32% | 33% | 33% | 39% | 37% | 38% | 36% | 33% | 0.29
MAPP_US | All | 19% | 29% | 28% | 29% | 26% | 26% | 32% | 35% | 37% | 40% | 31% | 38% | 40% | 40% | 44% | 64% | 54% | 50% | 43% | 45% | 0.4
MISO_IN | All | 41% | 30% | 26% | 19% | 21% | 21% | 21% | 22% | 25% | 26% | 44% | 37% | 34% | 35% | 38% | 59% | 39% | 42% | 42% | 48% | 0.33
MISO_MI | All | 63% | 46% | 24% | 21% | 21% | 20% | 20% | 20% | 23% | 24% | 30% | 29% | 29% | 31% | 32% | 64% | 44% | 47% | 44% | 43% | 0.3
MISO_MO-IL | All | 41% | 32% | 23% | 19% | 20% | 22% | 23% | 25% | 27% | 29% | 53% | 40% | 36% | 37% | 41% | 59% | 44% | 42% | 41% | 49% | 0.35
MISO_W | All | 28% | 35% | 27% | 27% | 25% | 24% | 30% | 35% | 35% | 39% | 28% | 36% | 37% | 40% | 41% | 56% | 51% | 42% | 39% | 42% | 0.38
MISO_WUMS | All | 59% | 40% | 23% | 20% | 20% | 21% | 22% | 25% | 27% | 30% | 31% | 32% | 30% | 33% | 38% | 67% | 46% | 41% | 38% | 43% | 0.33
NE | All | 25% | 36% | 29% | 24% | 25% | 26% | 30% | 36% | 35% | 39% | 28% | 37% | 41% | 43% | 46% | 60% | 53% | 48% | 45% | 48% | 0.4
NEISO_CT | All | 29% | 23% | 21% | 18% | 19% | 21% | 16% | 17% | 21% | 22% | 31% | 30% | 28% | 27% | 28% | 44% | 41% | 36% | 34% | 35% | 0.26
NEISO_MA | All | 36% | 26% | 25% | 20% | 22% | 23% | 18% | 20% | 25% | 26% | 38% | 34% | 32% | 31% | 32% | 54% | 47% | 42% | 40% | 41% | 0.31
NEISO_ME | All | 27% | 17% | 19% | 20% | 22% | 25% | 20% | 21% | 27% | 29% | 43% | 39% | 32% | 35% | 38% | 58% | 49% | 46% | 44% | 47% | 0.34
NEISO_NH | All | 38% | 21% | 19% | 18% | 20% | 22% | 18% | 19% | 26% | 29% | 40% | 37% | 34% | 35% | 36% | 57% | 48% | 46% | 45% | 45% | 0.33
NEISO_RI | All | 38% | 23% | 20% | 17% | 19% | 19% | 15% | 14% | 19% | 19% | 32% | 22% | 21% | 22% | 24% | 32% | 31% | 30% | 29% | 29% | 0.22
NEISO_VT | All | 49% | 26% | 22% | 19% | 21% | 23% | 19% | 20% | 28% | 30% | 39% | 36% | 36% | 35% | 36% | 56% | 49% | 49% | 47% | 47% | 0.34
NEISO (Note B) | All | 0.36 | 0.21 | 0.2 | 0.19 | 0.21 | 0.24 | 0.19 | 0.2 | 0.27 | 0.29 | 0.41 | 0.37 | 0.34 | 0.35 | 0.37 | 0.57 | 0.49 | 0.46 | 0.45 | 0.46 | 0.336
NonRTO_Midwest | All | 5% | 9% | 16% | 12% | 14% | 14% | 15% | 15% | 19% | 22% | 17% | 25% | 27% | 26% | 32% | 34% | 29% | 33% | 35% | 41% | 0.26
NYISO_A-F | All | 59% | 38% | 27% | 21% | 21% | 21% | 18% | 21% | 26% | 26% | 35% | 30% | 34% | 34% | 35% | 49% | 48% | 48% | 49% | 46% | 0.33
NYISO_G-I | All | 51% | 40% | 36% | 30% | 32% | 33% | 26% | 26% | 29% | 26% | 49% | 37% | 36% | 35% | 33% | 52% | 49% | 44% | 41% | 43% | 0.34
NYISO_J-K | All | 50% | 35% | 32% | 30% | 32% | 32% | 28% | 23% | 27% | 24% | 51% | 34% | 33% | 32% | 32% | 48% | 42% | 38% | 38% | 39% | 0.32
PJM_E | All | 13% | 11% | 15% | 14% | 14% | 16% | 16% | 16% | 18% | 16% | 24% | 25% | 26% | 25% | 24% | 39% | 34% | 30% | 31% | 31% | 0.23
PJM_ROM | All | 17% | 17% | 17% | 13% | 14% | 16% | 15% | 17% | 21% | 21% | 30% | 26% | 30% | 30% | 31% | 52% | 48% | 43% | 43% | 43% | 0.28
PJM_ROR | All | 38% | 30% | 22% | 17% | 18% | 19% | 19% | 21% | 25% | 25% | 40% | 33% | 32% | 33% | 35% | 62% | 43% | 44% | 43% | 46% | 0.32
SOCO (Note A) | All | 5% | 4% | 9% | 11% | 10% | 11% | 13% | 15% | 22% | 26% | 11% | 32% | 31% | 28% | 40% | 27% | 30% | 33% | 36% | 47% | 0.29
SPP_N | All | 60% | 40% | 28% | 31% | 30% | 29% | 31% | 34% | 33% | 38% | 39% | 38% | 38% | 45% | 47% | 46% | 44% | 37% | 39% | 45% | 0.39
SPP_S | All | 64% | 41% | 27% | 33% | 33% | 29% | 30% | 32% | 32% | 38% | 38% | 38% | 37% | 46% | 49% | 46% | 42% | 38% | 39% | 45% | 0.39
TVA | All | 5% | 4% | 9% | 11% | 10% | 11% | 13% | 15% | 22% | 26% | 11% | 32% | 31% | 28% | 40% | 27% | 30% | 33% | 36% | 47% | 0.29
VACAR | All | 18% | 12% | 25% | 28% | 22% | 23% | 25% | 22% | 25% | 23% | 15% | 29% | 31% | 30% | 35% | 42% | 35% | 35% | 35% | 39% | 0.3
Note A: CRA shows no Class 4+ wind resource for SOCO but ReEDs has 8 MW. Wind shape values based on TVA.
Note B:Values shown below were calculated two ways. One set is weighted based on CRA use of all wind sites in NEISO from EWITS. An alternative weights amounts based on the potential state-by-state Class 4+resources that CRA identified. Both are shown below. The table above shows the state-by-state weighting.
State-weighted NEISO |  | 0.36 | 0.21 | 0.2 | 0.19 | 0.21 | 0.24 | 0.19 | 0.2 | 0.27 | 0.29 | 0.41 | 0.37 | 0.34 | 0.35 | 0.37 | 0.57 | 0.49 | 0.46 | 0.45 | 0.46 | 0.336
EWITS-weighted NEISO |  | 34% | 21% | 21% | 19% | 21% | 23% | 19% | 20% | 26% | 27% | 40% | 36% | 32% | 33% | 35% | 54% | 47% | 44% | 42% | 44% | 0.321
OFFSHORE WIND |  | Summer | [9 empty] | Shoulder |  |  |  |  | Winter
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20
ENT | All
FRCC | All
IESO | All | 0.68 | 0.44 | 0.25 | 0.26 | 0.26 | 0.25 | 0.22 | 0.26 | 0.32 | 0.32 | 0.36 | 0.38 | 0.41 | 0.43 | 0.42 | 0.42 | 0.48 | 0.5 | 0.5 | 47% | 0.38
MAPP_CA | All
MAPP_US | All
MISO_IN | All | 66% | 48% | 29% | 21% | 24% | 24% | 24% | 27% | 25% | 25% | 64% | 44% | 38% | 40% | 40% | 59% | 43% | 43% | 42% | 48% | 0.35
MISO_MI | All | 48% | 45% | 34% | 26% | 28% | 27% | 30% | 29% | 30% | 30% | 41% | 37% | 34% | 36% | 37% | 69% | 50% | 49% | 46% | 44% | 0.357
MISO_MO-IL | All
MISO_W | All
MISO_WUMS | All | 46% | 41% | 33% | 27% | 27% | 26% | 31% | 29% | 28% | 30% | 45% | 35% | 31% | 35% | 36% | 63% | 44% | 41% | 38% | 40% | 0.338
NE | All
NEISO_CT | All | 0.72 | 0.53 | 0.44 | 0.38 | 0.38 | 0.36 | 0.29 | 0.25 | 0.31 | 0.23 | 0.64 | 0.37 | 0.39 | 0.35 | 0.32 | 0.62 | 0.54 | 0.48 | 0.46 | 43% | 0.35
NEISO_MA | All | 74% | 59% | 52% | 45% | 44% | 46% | 40% | 37% | 43% | 40% | 73% | 41% | 46% | 44% | 45% | 65% | 53% | 54% | 55% | 52% | 0.456
NEISO_ME | All | 53% | 38% | 42% | 44% | 48% | 43% | 37% | 33% | 41% | 35% | 56% | 40% | 39% | 39% | 36% | 60% | 49% | 45% | 47% | 45% | 0.399
NEISO_NH | All | 0.57 | 0.4 | 0.4 | 0.35 | 0.41 | 0.36 | 0.3 | 0.3 | 0.36 | 0.32 | 0.43 | 0.38 | 0.37 | 0.35 | 0.34 | 0.58 | 0.49 | 0.43 | 0.43 | 42% | 0.365
NEISO_RI | All | 0.81 | 0.65 | 0.52 | 0.5 | 0.5 | 0.45 | 0.41 | 0.35 | 0.39 | 0.33 | 0.75 | 0.4 | 0.44 | 0.43 | 0.4 | 0.64 | 0.55 | 0.52 | 0.52 | 48% | 0.427
NEISO_VT | All
NonRTO_Midwest | All
NYISO_A-F | All | 68% | 44% | 25% | 26% | 26% | 25% | 22% | 26% | 32% | 32% | 36% | 38% | 41% | 43% | 42% | 42% | 48% | 50% | 50% | 47% | 0.38 | a
NYISO_G-I | All
NYISO_J-K | All | 71% | 0.58 | 0.48 | 0.49 | 0.48 | 0.45 | 0.42 | 0.33 | 0.37 | 0.29 | 0.67 | 0.4 | 0.44 | 0.42 | 0.38 | 0.65 | 0.55 | 0.49 | 0.49 | 46% | 0.407
PJM_E | All | 57% | 49% | 42% | 43% | 44% | 44% | 42% | 35% | 37% | 31% | 67% | 40% | 44% | 43% | 41% | 64% | 53% | 47% | 51% | 46% | 0.414
PJM_ROM | All | 38% | 41% | 37% | 42% | 39% | 42% | 40% | 34% | 35% | 30% | 61% | 36% | 41% | 41% | 41% | 57% | 47% | 44% | 49% | 46% | 0.396
PJM_ROR | All | 30% | 32% | 35% | 38% | 36% | 38% | 37% | 31% | 32% | 29% | 49% | 40% | 41% | 40% | 41% | 52% | 45% | 42% | 46% | 45% | 0.381
SOCO | All
SPP_N | All
SPP_S | All
TVA | All
VACAR | All | 0.45 | 0.27 | 0.44 | 0.5 | 0.4 | 0.41 | 0.4 | 0.36 | 0.35 | 0.3 | 0.23 | 0.41 | 0.42 | 0.42 | 0.44 | 0.51 | 0.46 | 0.42 | 0.42 | 42% | 0.394
a - IESO data used
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
*CRA should make an explanation in report that more fully gives the meaning of footnote 8 on NREL wind data source (instead of just saying “EWITS”). For example, explaining that CRA used the NREL data “straight out” [this seems to be what Ralph Luciani said on the Modeling phone call on 1-12] as developed by AWS Truewind for typical generators at “X”-meter hub height, averaged over all identified sites with class ”Y” resource or better, and accounting for the relevant operational factors of wake losses, the impact of gusts, availability and other factors, as described under “Methodology” at http://www.nrel.gov/wind/integrationdatasets/eastern/methodology.html . [Or stating that the footnote means that CRA just used the subset of EWITS sites that comprise a subset of all the NREL sites?][This note is based on 12-22-10 version of table that included preliminary plant list.]
Proposed Class 3 Wind Shapes - Based on calculating ratio of Class 3 avg CF (32%) to the weighted avg CF for Class 4+ (Class 4=36%, Class 5=41.8%, Class 6=44%, Class 7=46%) using NREL estimates of Class 3 - 7 wind by region. Each class 4+ wind factor in table above is multiplied by the calculated ratio, shown in Exhibit 11. (S. Hadley 2/8/11)
ONSHORE WIND Class 3 |  | Summer | [9 empty] | Shoulder |  |  |  |  | Winter |  |  |  |  | Annual
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935 | Capacity Factor
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | (calculated)
ENT | All | 0.12 | 0.08 | 0.12 | 0.11 | 0.12 | 0.15 | 0.14 | 0.19 | 0.24 | 0.3 | 0.15 | 0.26 | 0.26 | 0.32 | 0.41 | 0.36 | 0.35 | 0.32 | 0.33 | 0.41 | 0.3
FRCC (Note A) | All | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
IESO (Note B) | All | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAPP_CA (Note B) | All | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAPP_US | All | 0.16 | 0.25 | 0.24 | 0.25 | 0.23 | 0.22 | 0.28 | 0.3 | 0.31 | 0.34 | 0.27 | 0.32 | 0.34 | 0.34 | 0.37 | 0.55 | 0.46 | 0.42 | 0.37 | 0.39 | 0.34
MISO_IN | All | 0.36 | 0.26 | 0.23 | 0.17 | 0.18 | 0.19 | 0.18 | 0.2 | 0.22 | 0.23 | 0.39 | 0.33 | 0.3 | 0.31 | 0.34 | 0.52 | 0.34 | 0.38 | 0.37 | 0.42 | 0.29
MISO_MI | All | 0.56 | 0.4 | 0.21 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.2 | 0.21 | 0.27 | 0.25 | 0.26 | 0.27 | 0.28 | 0.56 | 0.39 | 0.41 | 0.39 | 0.38 | 0.27
MISO_MO_IL | All | 0.37 | 0.28 | 0.21 | 0.16 | 0.18 | 0.2 | 0.2 | 0.22 | 0.24 | 0.26 | 0.47 | 0.36 | 0.32 | 0.33 | 0.37 | 0.52 | 0.39 | 0.37 | 0.37 | 0.43 | 0.31
MISO_W | All | 0.24 | 0.29 | 0.23 | 0.23 | 0.21 | 0.2 | 0.25 | 0.29 | 0.29 | 0.33 | 0.24 | 0.3 | 0.31 | 0.34 | 0.35 | 0.47 | 0.43 | 0.36 | 0.33 | 0.35 | 0.32
MISO_WUMS | All | 0.51 | 0.35 | 0.2 | 0.17 | 0.17 | 0.18 | 0.19 | 0.22 | 0.23 | 0.26 | 0.27 | 0.28 | 0.26 | 0.29 | 0.33 | 0.58 | 0.4 | 0.35 | 0.33 | 0.38 | 0.28
NE | All | 0.22 | 0.31 | 0.26 | 0.21 | 0.22 | 0.23 | 0.26 | 0.32 | 0.31 | 0.34 | 0.25 | 0.32 | 0.36 | 0.38 | 0.41 | 0.53 | 0.47 | 0.42 | 0.39 | 0.42 | 0.36
NEISO_CT | All | 0.24 | 0.19 | 0.18 | 0.15 | 0.16 | 0.17 | 0.14 | 0.14 | 0.17 | 0.18 | 0.26 | 0.25 | 0.23 | 0.23 | 0.23 | 0.37 | 0.34 | 0.3 | 0.28 | 0.29 | 0.22
NEISO_MA | All | 0.3 | 0.21 | 0.21 | 0.17 | 0.18 | 0.19 | 0.15 | 0.16 | 0.21 | 0.21 | 0.31 | 0.28 | 0.27 | 0.26 | 0.27 | 0.45 | 0.39 | 0.35 | 0.33 | 0.34 | 0.25
NEISO_ME | All | 0.22 | 0.14 | 0.16 | 0.17 | 0.18 | 0.2 | 0.17 | 0.17 | 0.22 | 0.24 | 0.36 | 0.32 | 0.27 | 0.29 | 0.32 | 0.48 | 0.41 | 0.38 | 0.36 | 0.39 | 0.28
NEISO_NH | All | 0.32 | 0.17 | 0.16 | 0.15 | 0.17 | 0.18 | 0.15 | 0.16 | 0.22 | 0.24 | 0.33 | 0.31 | 0.28 | 0.29 | 0.3 | 0.47 | 0.4 | 0.38 | 0.37 | 0.38 | 0.27
NEISO_RI | All | 0.31 | 0.19 | 0.17 | 0.14 | 0.16 | 0.16 | 0.12 | 0.12 | 0.16 | 0.16 | 0.26 | 0.18 | 0.18 | 0.18 | 0.2 | 0.27 | 0.26 | 0.25 | 0.24 | 0.24 | 0.19
NEISO_VT | All | 0.4 | 0.21 | 0.18 | 0.16 | 0.17 | 0.19 | 0.16 | 0.16 | 0.23 | 0.25 | 0.32 | 0.3 | 0.3 | 0.29 | 0.3 | 0.47 | 0.41 | 0.41 | 0.39 | 0.39 | 0.28
NEISO (Note D) | All | 0.3 | 0.17 | 0.17 | 0.16 | 0.18 | 0.2 | 0.16 | 0.17 | 0.22 | 0.24 | 0.34 | 0.31 | 0.28 | 0.29 | 0.3 | 0.47 | 0.4 | 0.38 | 0.37 | 0.38 | 0.279
NonRTO_Midwest | All | 0.05 | 0.08 | 0.14 | 0.1 | 0.12 | 0.12 | 0.13 | 0.13 | 0.16 | 0.19 | 0.15 | 0.21 | 0.23 | 0.22 | 0.28 | 0.29 | 0.25 | 0.28 | 0.3 | 0.35 | 0.22
NYISO_A-F | All | 0.5 | 0.32 | 0.23 | 0.18 | 0.18 | 0.18 | 0.15 | 0.18 | 0.22 | 0.22 | 0.3 | 0.25 | 0.29 | 0.29 | 0.3 | 0.42 | 0.41 | 0.41 | 0.41 | 0.39 | 0.28
NYISO_G-I | All | 0.42 | 0.33 | 0.3 | 0.24 | 0.26 | 0.27 | 0.21 | 0.21 | 0.24 | 0.21 | 0.4 | 0.31 | 0.29 | 0.29 | 0.27 | 0.43 | 0.4 | 0.36 | 0.34 | 0.36 | 0.28
NYISO_J-K | All | 0.44 | 0.31 | 0.28 | 0.26 | 0.28 | 0.28 | 0.24 | 0.21 | 0.24 | 0.21 | 0.45 | 0.3 | 0.29 | 0.28 | 0.29 | 0.43 | 0.37 | 0.33 | 0.34 | 0.35 | 0.28
PJM_E | All | 0.12 | 0.1 | 0.13 | 0.12 | 0.13 | 0.14 | 0.14 | 0.14 | 0.16 | 0.14 | 0.21 | 0.22 | 0.23 | 0.22 | 0.21 | 0.35 | 0.3 | 0.26 | 0.28 | 0.27 | 0.2
PJM_ROM | All | 0.14 | 0.14 | 0.14 | 0.11 | 0.12 | 0.14 | 0.13 | 0.14 | 0.18 | 0.18 | 0.26 | 0.22 | 0.25 | 0.25 | 0.26 | 0.45 | 0.41 | 0.37 | 0.37 | 0.36 | 0.24
PJM_ROR | All | 0.32 | 0.26 | 0.19 | 0.15 | 0.15 | 0.16 | 0.16 | 0.18 | 0.21 | 0.21 | 0.33 | 0.28 | 0.27 | 0.28 | 0.3 | 0.52 | 0.36 | 0.37 | 0.36 | 0.39 | 0.27
SOCO (Note C) | All | 0.04 | 0.03 | 0.08 | 0.09 | 0.08 | 0.09 | 0.11 | 0.13 | 0.18 | 0.21 | 0.09 | 0.26 | 0.26 | 0.23 | 0.32 | 0.22 | 0.24 | 0.27 | 0.3 | 0.39 | 0.24
SPP_N | All | 0.5 | 0.33 | 0.24 | 0.26 | 0.26 | 0.24 | 0.26 | 0.29 | 0.28 | 0.32 | 0.33 | 0.32 | 0.32 | 0.38 | 0.4 | 0.38 | 0.37 | 0.31 | 0.32 | 0.38 | 0.33
SPP_S | All | 0.56 | 0.36 | 0.24 | 0.29 | 0.29 | 0.25 | 0.26 | 0.29 | 0.28 | 0.33 | 0.33 | 0.33 | 0.32 | 0.4 | 0.43 | 0.41 | 0.36 | 0.34 | 0.34 | 0.4 | 0.34
TVA | All | 0.04 | 0.03 | 0.08 | 0.09 | 0.08 | 0.09 | 0.11 | 0.13 | 0.18 | 0.21 | 0.09 | 0.26 | 0.26 | 0.23 | 0.32 | 0.22 | 0.24 | 0.27 | 0.3 | 0.39 | 0.24
VACAR | All | 0.15 | 0.1 | 0.21 | 0.23 | 0.18 | 0.19 | 0.2 | 0.18 | 0.21 | 0.19 | 0.13 | 0.24 | 0.26 | 0.25 | 0.29 | 0.35 | 0.29 | 0.29 | 0.29 | 0.33 | 0.25
Note A: FRCC has no Class 3 capacity
Note B: IESO and MAPP_CA are not in ReEDS data. Their capacity potential is left at CRA values in Class 4+
Note C: CRA has no wind shape for Class 4+ in SOCO so using TVA wind shapes
Note D: As with the Clase 4+ data above, two values were calculated. The EWITS-weighted set is based on ratioing the weighted values CRA used from all wind sites in NEISO from EWITS. The ratioed values for Class 3 using the calculated by weighting based on the potential state-by-state Class 4+resources that CRA identified are also in the table above.
State-weighted NEISO |  | 0.3 | 0.17 | 0.17 | 0.16 | 0.18 | 0.2 | 0.16 | 0.17 | 0.22 | 0.24 | 0.34 | 0.31 | 0.28 | 0.29 | 0.3 | 0.47 | 0.4 | 0.38 | 0.37 | 0.38 | 0.279
EWITS-site weighted NEISO |  | 0.28 | 0.17 | 0.17 | 0.16 | 0.18 | 0.19 | 0.16 | 0.16 | 0.21 | 0.23 | 0.33 | 0.29 | 0.27 | 0.27 | 0.29 | 0.45 | 0.39 | 0.36 | 0.35 | 0.36 | 0.266

## Exhibit5_BAs to NEEM Regions
Appendix A, Exhibit 5 - Mapping of BA's to NEEM Regions (for generator mapping)
Plant Balancing Authority Area Name | NEEM Region(s)
Alberta Electric System Operator | ALB
Allegheny Power Service | PJM_ROR
Alliant Energy | MISO_W
Alliant Energy East | MISO_WUMS
Ameren | MISO_MO-IL
American Electric Power | PJM_ROR
American Electric Power West | SPP_S
Aquila Networks MPS | SPP_N
Arizona Public Service Co | AZ_NM_SNV
Associated Electric Coop Inc | ENT
Avista Corp | NWPP
Big Rivers Electric Corp | MISO_IN
Bonneville Power Administration | NWPP
British Columbia Hydro & Power Authority | BC
British Columbia Transmission Corp | BC
California Independent System Operator | NP15, SP15
Central & Southwest Services | SPP_S
Central Illinois Light Co | MISO_MO-IL
Cleco Corp | SPP_S
Columbia Water & Light | MISO_MO-IL
Commonwealth Edison Co | PJM_ROR
Dairyland Power Coop | MISO_W
Dayton Power & Light | PJM_ROR
Duke Energy Carolinas LLC | VACAR
Duke Energy Corp (INDIANA) | MISO_IN
Duke Energy Corp (OHIO/KENTUCKY) | PJM_ROR
Duquesne Light | PJM_ROR
East Kentucky Power Coop Inc | NonRTO_Midwest
El Paso Electric | AZ_NM_SNV
Electric Energy Inc | MISO_MO-IL
Empire District Electric Co | SPP_N
Entergy | ENT
ERCOT ISO | ERCOT
FirstEnergy | PJM_ROR
Florida Municipal Power Pool | FRCC
Florida Power & Light | FRCC
Gainesville Regional Utilities | FRCC
Grand River Dam Authority | SPP_S
Great River Energy | MISO_W
Homestead (City of) | FRCC
Hoosier Energy | MISO_IN
Idaho Power Co | NWPP
IESO (Ontario) | IESO
Illinois Power Co | MISO_MO-IL
Imperial Irrigation District | SP15
Independence MO (City of) | SPP_N
Indianapolis Power & Light Co | MISO_IN
JEA | FRCC
Kansas City KS (City of) | SPP_N
Kansas City Power & Light | SPP_N
KGE A Westar Energy Co | SPP_N
Lafayette Utilities System | SPP_S
Lake Worth Utilities | FRCC
Lincoln Electric System | NE
Los Angeles Dept of Water & Power | SP15
Louisiana Energy & Power Authority | SPP_S
Louisiana Generating LLC | ENT
Louisville Gas & Electric Co | NonRTO_Midwest
Madison Gas & Electric Co | MISO_WUMS
Michigan Electric Coordinated System | MISO_MI
MidAmerican Energy Co | MISO_W
Mid-Columbia (includes CHPD,GCPD,DOPD) | NWPP
Minnesota Power Co | MISO_W
Muscatine Power & Water | MISO_W
Nebraska Public Power District | NE
Nevada Power Co | AZ_NM_SNV
New England ISO | NEISO
New Smyrna Beach Utilities Commission | FRCC
New York ISO | NYISO_A-F, NYISO_G-I, NYISO_J-K
Northern Indiana Public Service Co | MISO_IN
Northern States Power | MISO_W
Northwestern Energy | NWPP
Oglethorpe Power Corp | SOCO
Ohio Valley Electric Corp | NonRTO_Midwest
Oklahoma Gas & Electric Co | SPP_S
Omaha Public Power District | NE
Otter Tail Power Co | MISO_W
PacifiCorp | NWPP
PacifiCorp East | NWPP
PacifiCorp West | NWPP
PJM Interconnection | PJM_E, PJM_ROM, PJM_ROR
Portland General Electric | NWPP
PowerSouth Energy Coop | SOCO
Progress Energy Carolina East | VACAR
Progress Energy Carolina West | VACAR
Progress Energy Florida | FRCC
Public Service Co of Colorado | RMPA
Public Service Co of New Mexico | AZ_NM_SNV
PUD No 1 of Douglas County | NWPP
PUD No 2 of Grant County | NWPP
Puget Sound Energy Inc | NWPP
Sacramento Municipal Utility District | NP15
Salt River Project | AZ_NM_SNV
Seattle City Light | NWPP
Seminole Electric Coop Inc | FRCC
Sierra Pacific Power Co | NWPP
South Carolina Electric & Gas Co | VACAR
South Carolina Public Service Authority | VACAR
South Mississippi Electric Power Association | SOCO
Southern Co Services Inc | SOCO
Southern Illinois Power Coop | MISO_MO-IL
Southern Indiana Gas & Electric Co | MISO_IN
Southern Minnesota Municipal Power | MISO_W
Southwestern Power Administration | SPP_S
Southwestern Public Service Co | SPP_S
Springfield IL City Water Light & Power | MISO_MO-IL
Sunflower Electric Power Corp | SPP_N
Tacoma Power | NWPP
Tallahassee FL (City of) | FRCC
Tampa Electric Co | FRCC
Tennessee Valley Authority | TVA
Tucson Electric Power Co | AZ_NM_SNV
TXU Electric Co | ERCOT
Upper Peninsula Power Co | MISO_WUMS
Virginia Electric & Power Co | PJM_ROR
WAPA Desert Southwest Region | AZ_NM_SNV
WAPA Rocky Mountain Region | RMPA
WAPA Upper Great Plains Region East | MAPP_US
WAPA Upper Great Plains Region West | NWPP
Westar Energy | SPP_N
Western Farmers Electric Coop | SPP_S
Westplains Energy (KS) | SPP_N
Wisconsin Electric Power | MISO_WUMS
Wisconsin Public Service Corp | MISO_WUMS
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit 6_ExistingUnits
Appendix A, Exhibit 6 - Existing Units |  |  | This is CRA's 3/17/11 version
LEGEND
Capacity Description | Aggregated/Stand Alone | Gen Type | NEEM Region | Summer Capacity MW | Wtd. Avg. Forced Outage Rate | Wtd. Avg. Planned Outage Days | Gen Type | Description
Big Cajun 2 | Stand Alone | Coal | ENT | 1743 | 7.7% | 34.4 | CC | Combined Cycle - Natural Gas
Independence (AR) | Stand Alone | Coal | ENT | 1678 | 3.6% | 31.6 | Coal | Steam Turbine - Coal
New Madrid (Memphis) | Stand Alone | Coal | ENT | 1160 | 7.7% | 34.4 | CT | Combustion Turbine - Natural Gas or Oil
Roy S Nelson | Stand Alone | Coal | ENT | 550 | 7.7% | 34.4 | GEO | Geothermal
Thomas Hill | Stand Alone | Coal | ENT | 945 | 6.2% | 32.2 | HY | Hydro - Conventional
White Bluff | Stand Alone | Coal | ENT | 1655 | 3.6% | 31.6 | LFG | Landfill Gas
Big Bend (FL) | Stand Alone | Coal | FRCC | 1550 | 6.7% | 31.1 | NU | Nuclear
C D McIntosh Jr | Stand Alone | Coal | FRCC | 342 | 6.4% | 29.9 | PS | Hydro - Pumped Storage
Cedar Bay Generating Co LP | Stand Alone | Coal | FRCC | 250 | 6% | 28.3 | PV | Solar - Photovoltaic
Crystal River | Stand Alone | Coal | FRCC | 2388 | 6.6% | 33.3 | ST | Solar - Solar Thermal/Conc Solar Power
Deerhaven Generating Station | Stand Alone | Coal | FRCC | 228 | 6% | 28.3 | STOG | Steam Turbine - Oil/Gas
Indiantown Cogeneration Facility | Stand Alone | Coal | FRCC | 330 | 6.4% | 29.9 | STWD | Steam Turbine - Wood
Northside Generating | Stand Alone | Coal | FRCC | 550 | 6% | 28.3 | WT | Wind Turbine
Polk Station | Stand Alone | Coal | FRCC | 235 | 6% | 28.3
Seminole (FL) | Stand Alone | Coal | FRCC | 1316 | 6.3% | 33.8
St Johns River Power Park | Stand Alone | Coal | FRCC | 1252 | 6.3% | 33.8
Stanton Energy Center | Stand Alone | Coal | FRCC | 886 | 7.7% | 34.4
Atikokan GS | Stand Alone | Coal | IESO | 211 | 6% | 28.3
Lambton GS | Stand Alone | Coal | IESO | 1961 | 7.7% | 34.4
Nanticoke | Stand Alone | Coal | IESO | 3938 | 7.7% | 34.4
Antelope Valley | Stand Alone | Coal | MAPP_US | 900 | 6.7% | 29.8
Coal Creek | Stand Alone | Coal | MAPP_US | 1114 | 5.8% | 25.2
Coyote | Stand Alone | Coal | MAPP_US | 427 | 5.8% | 25.2
Laramie River | Stand Alone | Coal | MAPP_US | 565 | 7.7% | 34.4
Leland Olds 1 & 2 | Stand Alone | Coal | MAPP_US | 669 | 5.8% | 25.2
Milton R Young | Stand Alone | Coal | MAPP_US | 697 | 5.8% | 25.2
A B Brown | Stand Alone | Coal | MISO_IN | 490 | 6% | 28.3
AES Petersburg (IN) | Stand Alone | Coal | MISO_IN | 1752 | 7.5% | 33.6
Bailly | Stand Alone | Coal | MISO_IN | 320 | 6.4% | 29.9
D B Wilson | Stand Alone | Coal | MISO_IN | 417 | 7.7% | 34.4
F B Culley | Stand Alone | Coal | MISO_IN | 270 | 6% | 28.3
Gibson Station | Stand Alone | Coal | MISO_IN | 3131 | 6.3% | 33.8
Harding Street | Stand Alone | Coal | MISO_IN | 435 | 7.7% | 34.4
Merom | Stand Alone | Coal | MISO_IN | 955 | 7.7% | 34.4
Michigan City | Stand Alone | Coal | MISO_IN | 469 | 7.7% | 34.4
R M Schahfer | Stand Alone | Coal | MISO_IN | 1625 | 7.1% | 32.4
Robert D Green | Stand Alone | Coal | MISO_IN | 454 | 6% | 28.3
Wabash River | Stand Alone | Coal | MISO_IN | 592 | 6.2% | 29.2
Belle River | Stand Alone | Coal | MISO_MI | 1270 | 6.3% | 33.8
D E Karn | Stand Alone | Coal | MISO_MI | 515 | 6% | 28.3
J H Campbell | Stand Alone | Coal | MISO_MI | 1440 | 4.7% | 30.6
Monroe (MI) | Stand Alone | Coal | MISO_MI | 3115 | 6.3% | 33.8
River Rouge | Stand Alone | Coal | MISO_MI | 523 | 6% | 28.3
St Clair | Stand Alone | Coal | MISO_MI | 752 | 7.1% | 32.6
Trenton Channel | Stand Alone | Coal | MISO_MI | 520 | 7.7% | 34.4
Baldwin Energy Complex | Stand Alone | Coal | MISO_MO-IL | 1764 | 7.7% | 34.4
Coffeen | Stand Alone | Coal | MISO_MO-IL | 900 | 7.2% | 32.7
Dallman | Stand Alone | Coal | MISO_MO-IL | 200 | 6% | 28.3
Duck Creek | Stand Alone | Coal | MISO_MO-IL | 358 | 6.4% | 29.9
E D Edwards | Stand Alone | Coal | MISO_MO-IL | 598 | 6.2% | 29.2
Havana | Stand Alone | Coal | MISO_MO-IL | 438 | 7.7% | 34.4
Hennepin Power Station | Stand Alone | Coal | MISO_MO-IL | 215 | 6% | 28.3
Labadie | Stand Alone | Coal | MISO_MO-IL | 2406 | 6.6% | 33.9
Meramec | Stand Alone | Coal | MISO_MO-IL | 603 | 6.2% | 29.2
Meredosia | Stand Alone | Coal | MISO_MO-IL | 203 | 6% | 28.3
Newton (IL) | Stand Alone | Coal | MISO_MO-IL | 1201 | 7% | 34.1
Rush Island | Stand Alone | Coal | MISO_MO-IL | 1181 | 7% | 34.1
Sioux | Stand Alone | Coal | MISO_MO-IL | 993 | 7.7% | 34.4
Wood River (IL) | Stand Alone | Coal | MISO_MO-IL | 355 | 6.4% | 29.9
Allen S King Plant | Stand Alone | Coal | MISO_W | 528 | 7.7% | 34.4
Big Stone | Stand Alone | Coal | MISO_W | 475 | 7.7% | 34.4
Clay Boswell | Stand Alone | Coal | MISO_W | 886 | 7.2% | 32.6
Genoa No3 | Stand Alone | Coal | MISO_W | 351 | 6.4% | 29.9
George Neal North | Stand Alone | Coal | MISO_W | 810 | 7.1% | 32.2
George Neal South | Stand Alone | Coal | MISO_W | 644 | 6.3% | 33.8
John P Madgett | Stand Alone | Coal | MISO_W | 393 | 6.4% | 29.9
Lansing | Stand Alone | Coal | MISO_W | 262 | 6% | 28.3
Louisa | Stand Alone | Coal | MISO_W | 745 | 6.3% | 33.8
M L Kapp | Stand Alone | Coal | MISO_W | 212 | 6% | 28.3
Ottumwa (IA IPL) | Stand Alone | Coal | MISO_W | 710 | 6.3% | 33.8
Sherburne County | Stand Alone | Coal | MISO_W | 2243 | 5.2% | 32.9
Walter Scott Jr Energy Center | Stand Alone | Coal | MISO_W | 1490 | 4.8% | 32.6
Columbia (WI) | Stand Alone | Coal | MISO_WUMS | 1118 | 7.7% | 34.4
Edgewater (WI) | Stand Alone | Coal | MISO_WUMS | 734 | 7.1% | 32.5
Oak Creek Power Plant | Stand Alone | Coal | MISO_WUMS | 615 | 6.3% | 33.8
Pleasant Prairie | Stand Alone | Coal | MISO_WUMS | 1216 | 6.3% | 33.8
South Oak Creek | Stand Alone | Coal | MISO_WUMS | 1135 | 6.1% | 28.7
Weston | Stand Alone | Coal | MISO_WUMS | 870 | 7.2% | 32.7
Gerald Gentleman | Stand Alone | Coal | NE | 1365 | 6.3% | 33.8
Nebraska City | Stand Alone | Coal | NE | 1328 | 6% | 29.4
North Omaha | Stand Alone | Coal | NE | 224 | 6% | 28.3
Brayton PT | Stand Alone | Coal | NEISO | 1100 | 6.2% | 31.3
Bridgeport Station | Stand Alone | Coal | NEISO | 383 | 6.4% | 29.9
Merrimack | Stand Alone | Coal | NEISO | 320 | 6.4% | 29.9
Cane Run | Stand Alone | Coal | NonRTO_Midwest | 240 | 6% | 28.3
Clifty Creek | Stand Alone | Coal | NonRTO_Midwest | 1203 | 6% | 28.3
E W Brown | Stand Alone | Coal | NonRTO_Midwest | 429 | 7.7% | 34.4
Elmer Smith | Stand Alone | Coal | NonRTO_Midwest | 261 | 6% | 28.3
Ghent | Stand Alone | Coal | NonRTO_Midwest | 1918 | 7.7% | 34.4
Hugh L Spurlock | Stand Alone | Coal | NonRTO_Midwest | 1381 | 6.7% | 30.9
J Sherman Cooper | Stand Alone | Coal | NonRTO_Midwest | 225 | 6% | 28.3
Kyger Creek | Stand Alone | Coal | NonRTO_Midwest | 200 | 6% | 28.3
Mill Creek (KY) | Stand Alone | Coal | NonRTO_Midwest | 1472 | 6.8% | 31.4
Trimble Station (LGE) | Stand Alone | Coal | NonRTO_Midwest | 1243 | 6.9% | 34
AES Somerset LLC | Stand Alone | Coal | NYISO_A-F | 684 | 6.3% | 33.8
Cayuga | Stand Alone | Coal | MISO_IN | 995 | 7.7% | 34.4
Danskammer Generating Station | Stand Alone | Coal | NYISO_G-I | 233 | 6% | 28.3
Carneys Point Generating Plant | Stand Alone | Coal | PJM_E | 262 | 6% | 28.3
Eddystone Generating Station | Stand Alone | Coal | PJM_E | 588 | 6.2% | 29.2
Hudson Generating Station | Stand Alone | Coal | PJM_E | 568 | 7.7% | 34.4
Indian River Generating Station (DE) | Stand Alone | Coal | PJM_E | 436 | 7.7% | 34.4
Logan Generating Plant | Stand Alone | Coal | PJM_E | 219 | 6% | 28.3
Mercer Generating Station | Stand Alone | Coal | PJM_E | 648 | 6.4% | 29.9
Brandon Shores | Stand Alone | Coal | PJM_ROM | 1286 | 6.3% | 33.8
Chalk Point | Stand Alone | Coal | PJM_ROM | 683 | 6.4% | 29.9
Conemaugh | Stand Alone | Coal | PJM_ROM | 1700 | 3.6% | 31.6
Herbert A Wagner | Stand Alone | Coal | PJM_ROM | 324 | 6.4% | 29.9
Homer City Station | Stand Alone | Coal | PJM_ROM | 1884 | 6.3% | 33.8
Keystone (PA) | Stand Alone | Coal | PJM_ROM | 1700 | 3.6% | 31.6
Montour | Stand Alone | Coal | PJM_ROM | 1525 | 6.3% | 33.8
Morgantown Generating Station | Stand Alone | Coal | PJM_ROM | 1244 | 6.3% | 33.8
Portland (PA) | Stand Alone | Coal | PJM_ROM | 243 | 6% | 28.3
PPL Brunner Island | Stand Alone | Coal | PJM_ROM | 1442 | 6.3% | 31.9
Seward | Stand Alone | Coal | PJM_ROM | 521 | 7.7% | 34.4
Ashtabula | Stand Alone | Coal | PJM_ROR | 244 | 6% | 28.3
Avon Lake | Stand Alone | Coal | PJM_ROR | 625 | 6.3% | 33.8
Bay Shore | Stand Alone | Coal | PJM_ROR | 215 | 6% | 28.3
Big Sandy | Stand Alone | Coal | PJM_ROR | 1060 | 4.2% | 30.8
Birchwood Power Facility | Stand Alone | Coal | PJM_ROR | 238 | 6% | 28.3
Bruce Mansfield | Stand Alone | Coal | PJM_ROR | 2510 | 3.6% | 31.6
Cardinal | Stand Alone | Coal | PJM_ROR | 1800 | 7.2% | 34.2
Chesapeake | Stand Alone | Coal | PJM_ROR | 217 | 6% | 28.3
Chesterfield | Stand Alone | Coal | PJM_ROR | 982 | 6.3% | 32.5
Cheswick Power Plant | Stand Alone | Coal | PJM_ROR | 580 | 7.7% | 34.4
Clinch River | Stand Alone | Coal | PJM_ROR | 690 | 6% | 28.3
Clover | Stand Alone | Coal | PJM_ROR | 865 | 7.7% | 34.4
Conesville | Stand Alone | Coal | PJM_ROR | 1530 | 6.3% | 31.9
Crawford (IL) | Stand Alone | Coal | PJM_ROR | 532 | 6.2% | 29.3
East Bend | Stand Alone | Coal | PJM_ROR | 600 | 6.3% | 33.8
Eastlake (OH) | Stand Alone | Coal | PJM_ROR | 837 | 7.2% | 32.7
Fisk Street | Stand Alone | Coal | PJM_ROR | 326 | 6.4% | 29.9
Fort Martin | Stand Alone | Coal | PJM_ROR | 1107 | 7.7% | 34.4
Gavin | Stand Alone | Coal | PJM_ROR | 2640 | 7.6% | 35.3
Glen Lyn | Stand Alone | Coal | PJM_ROR | 235 | 6% | 28.3
Harrison (WV) | Stand Alone | Coal | PJM_ROR | 1954 | 6.3% | 33.8
Hatfields Ferry Power Station | Stand Alone | Coal | PJM_ROR | 1590 | 7.7% | 34.4
J M Stuart | Stand Alone | Coal | PJM_ROR | 2340 | 7.7% | 34.4
John E Amos | Stand Alone | Coal | PJM_ROR | 2900 | 5.4% | 33.3
Joliet 29 | Stand Alone | Coal | PJM_ROR | 1036 | 7.7% | 34.4
Joliet 9 | Stand Alone | Coal | PJM_ROR | 314 | 6.4% | 29.9
Kammer | Stand Alone | Coal | PJM_ROR | 600 | 6% | 28.3
Kanawha River | Stand Alone | Coal | PJM_ROR | 400 | 6% | 28.3
Killen Station | Stand Alone | Coal | PJM_ROR | 600 | 6.3% | 33.8
Kincaid Generation LLC | Stand Alone | Coal | PJM_ROR | 1158 | 7.7% | 34.4
Lake Shore | Stand Alone | Coal | PJM_ROR | 245 | 6% | 28.3
Miami Fort | Stand Alone | Coal | PJM_ROR | 1000 | 7.7% | 34.4
Mitchell (WV) | Stand Alone | Coal | PJM_ROR | 1560 | 6.3% | 33.8
Mitchell Power Station | Stand Alone | Coal | PJM_ROR | 277 | 6% | 28.3
Mountaineer | Stand Alone | Coal | PJM_ROR | 1310 | 7.6% | 35.3
MT Storm | Stand Alone | Coal | PJM_ROR | 1560 | 7.7% | 34.4
Muskingum River | Stand Alone | Coal | PJM_ROR | 995 | 7% | 31.9
Phil Sporn | Stand Alone | Coal | PJM_ROR | 440 | 7.7% | 34.4
Pleasants | Stand Alone | Coal | PJM_ROR | 1278 | 6.3% | 33.8
Powerton | Stand Alone | Coal | PJM_ROR | 1538 | 6.3% | 33.8
Rockport | Stand Alone | Coal | PJM_ROR | 2600 | 7.6% | 35.3
State Line Energy | Stand Alone | Coal | PJM_ROR | 318 | 6.4% | 29.9
Tanners Creek | Stand Alone | Coal | PJM_ROR | 700 | 7.2% | 32.7
W H Sammis | Stand Alone | Coal | PJM_ROR | 1500 | 6.3% | 33
W H Zimmer | Stand Alone | Coal | PJM_ROR | 1300 | 7.6% | 35.3
Walter C Beckjord | Stand Alone | Coal | PJM_ROR | 652 | 7.1% | 32.2
Waukegan | Stand Alone | Coal | PJM_ROR | 689 | 6.4% | 29.9
Will County | Stand Alone | Coal | PJM_ROR | 761 | 7.1% | 32.4
Bowen | Stand Alone | Coal | SOCO | 3221 | 4.8% | 32.6
Charles R Lowman | Stand Alone | Coal | SOCO | 470 | 6% | 28.3
Crist | Stand Alone | Coal | SOCO | 774 | 7.2% | 32.7
E C Gaston | Stand Alone | Coal | SOCO | 1862 | 4.9% | 29.8
Gorgas 2 & 3 | Stand Alone | Coal | SOCO | 677 | 6.3% | 33.8
Greene County (AL) | Stand Alone | Coal | SOCO | 497 | 6% | 28.3
Hammond | Stand Alone | Coal | SOCO | 503 | 7.7% | 34.4
Harllee Branch | Stand Alone | Coal | SOCO | 1607 | 7.1% | 32.5
Jack McDonough | Stand Alone | Coal | SOCO | 503 | 6% | 28.3
Jack Watson | Stand Alone | Coal | SOCO | 706 | 7.1% | 32.4
James H Miller Jr | Stand Alone | Coal | SOCO | 2752 | 6.3% | 33.8
James M Barry Electric Generating Plant | Stand Alone | Coal | SOCO | 1345 | 6.3% | 31.7
Scherer | Stand Alone | Coal | SOCO | 3405 | 3.6% | 31.6
Victor J Daniel Jr | Stand Alone | Coal | SOCO | 1020 | 7.7% | 34.4
Wansley (GPC) | Stand Alone | Coal | SOCO | 1752 | 3.6% | 31.6
Yates | Stand Alone | Coal | SOCO | 707 | 6.4% | 29.9
Hawthorne (MO) | Stand Alone | Coal | SPP_N | 563 | 7.7% | 34.4
Holcomb East | Stand Alone | Coal | SPP_N | 362 | 6.4% | 29.9
Iatan | Stand Alone | Coal | SPP_N | 651 | 6.3% | 33.8
Jeffrey Energy Center | Stand Alone | Coal | SPP_N | 2170 | 6.3% | 33.8
La Cygne | Stand Alone | Coal | SPP_N | 1418 | 6.3% | 33.8
Lawrence Energy Center (KS) | Stand Alone | Coal | SPP_N | 373 | 6.4% | 29.9
Nearman Creek | Stand Alone | Coal | SPP_N | 229 | 6% | 28.3
Sibley (MO) | Stand Alone | Coal | SPP_N | 401 | 7.7% | 34.4
Brame Energy Center | Stand Alone | Coal | SPP_S | 1112 | 7.7% | 34.4
Dolet Hills | Stand Alone | Coal | SPP_S | 672 | 5.8% | 25.2
Flint Creek (AR) | Stand Alone | Coal | SPP_S | 528 | 7.7% | 34.4
Grda 1 & 2 | Stand Alone | Coal | SPP_S | 1010 | 7.7% | 34.4
Harrington | Stand Alone | Coal | SPP_S | 1041 | 6.4% | 29.9
Hugo (OK) | Stand Alone | Coal | SPP_S | 440 | 7.7% | 34.4
Muskogee | Stand Alone | Coal | SPP_S | 1530 | 7.7% | 34.4
Northeastern | Stand Alone | Coal | SPP_S | 920 | 7.7% | 34.4
Oklaunion | Stand Alone | Coal | SPP_S | 533 | 6% | 28.3
Pirkey | Stand Alone | Coal | SPP_S | 675 | 5.8% | 25.2
Sikeston | Stand Alone | Coal | SPP_S | 233 | 6% | 28.3
Sooner | Stand Alone | Coal | SPP_S | 1046 | 7.7% | 34.4
Tolk | Stand Alone | Coal | SPP_S | 1080 | 7.7% | 34.4
Welsh Station | Stand Alone | Coal | SPP_S | 1584 | 7.7% | 34.4
Allen Steam Plant (TN) | Stand Alone | Coal | TVA | 741 | 6% | 28.3
Bull Run (TN) | Stand Alone | Coal | TVA | 870 | 3.6% | 31.6
Colbert | Stand Alone | Coal | TVA | 472 | 7.7% | 34.4
Cumberland (TN) | Stand Alone | Coal | TVA | 2478 | 7.6% | 35.3
Gallatin (TN) | Stand Alone | Coal | TVA | 976 | 6% | 28.3
Paradise (KY) | Stand Alone | Coal | TVA | 2201 | 5.1% | 32.8
Red Hills Generating Facility | Stand Alone | Coal | TVA | 440 | 5.8% | 25.2
Widows Creek | Stand Alone | Coal | TVA | 938 | 7.7% | 34.4
Belews Creek | Stand Alone | Coal | VACAR | 2270 | 7.6% | 35.3
Cliffside | Stand Alone | Coal | VACAR | 562 | 7.7% | 34.4
Cope | Stand Alone | Coal | VACAR | 420 | 7.7% | 34.4
Cross | Stand Alone | Coal | VACAR | 2320 | 7.3% | 34.2
G G Allen | Stand Alone | Coal | VACAR | 815 | 6% | 28.3
L V Sutton | Stand Alone | Coal | VACAR | 403 | 7.7% | 34.4
Lee | Stand Alone | Coal | VACAR | 246 | 6% | 28.3
Marshall (NC DUKE) | Stand Alone | Coal | VACAR | 2110 | 6.3% | 32.4
Mayo | Stand Alone | Coal | VACAR | 742 | 6.3% | 33.8
Roxboro | Stand Alone | Coal | VACAR | 2424 | 6.3% | 33.2
Wateree | Stand Alone | Coal | VACAR | 700 | 6.4% | 29.9
Williams (SC SCGC) | Stand Alone | Coal | VACAR | 615 | 6.3% | 33.8
Winyah | Stand Alone | Coal | VACAR | 1155 | 6% | 28.3
ENT Aggregated CC | Aggregated | CC | ENT | 13885 | 6.1% | 24.7
ENT Aggregated Coal | Aggregated | Coal | ENT | 578 | 6.9% | 26.8
ENT Aggregated CT | Aggregated | CT | ENT | 2960 | 8.4% | 15.4
ENT Aggregated HY | Aggregated | HY | ENT | 744 | 4.9% | 0
ENT Aggregated LFG | Aggregated | LFG | ENT | 8 | 5% | 18.3
ENT Aggregated NU | Aggregated | NU | ENT | 5252 | 3.2% | 28.6
ENT Aggregated PS | Aggregated | PS | ENT | 59 | 0% | 0
ENT Aggregated STOG | Aggregated | STOG | ENT | 14865 | 6.7% | 32.1
ENT Aggregated STWD | Aggregated | STWD | ENT | 206 | 10% | 36.5
ENT Aggregated WT | Aggregated | WT | ENT | 107 | 0% | 0
FRCC Aggregated CC | Aggregated | CC | FRCC | 21784 | 6.1% | 24.7
FRCC Aggregated Coal | Aggregated | Coal | FRCC | 136 | 6.6% | 27.3
FRCC Aggregated CT | Aggregated | CT | FRCC | 10714 | 8.8% | 14
FRCC Aggregated HY | Aggregated | HY | FRCC | 55 | 4.9% | 0
FRCC Aggregated LFG | Aggregated | LFG | FRCC | 486 | 5% | 18.3
FRCC Aggregated NU | Aggregated | NU | FRCC | 3902 | 3.2% | 28.6
FRCC Aggregated PV | Aggregated | PV | FRCC | 51 | 60% | 36.5
FRCC Aggregated STOG | Aggregated | STOG | FRCC | 9833 | 6.7% | 32.1
FRCC Aggregated STWD | Aggregated | STWD | FRCC | 195 | 10% | 36.5
IESO Aggregated CC | Aggregated | CC | IESO | 5943 | 6.1% | 24.7
IESO Aggregated Coal | Aggregated | Coal | IESO | 306 | 6.6% | 27.3
IESO Aggregated CT | Aggregated | CT | IESO | 760 | 8.8% | 13.8
IESO Aggregated HY | Aggregated | HY | IESO | 8004 | 4.9% | 0
IESO Aggregated LFG | Aggregated | LFG | IESO | 103 | 5% | 18.3
IESO Aggregated NU | Aggregated | NU | IESO | 13018 | 6.9% | 28.6
IESO Aggregated PS | Aggregated | PS | IESO | 123 | 0% | 0
IESO Aggregated PV | Aggregated | PV | IESO | 30 | 60% | 36.5
IESO Aggregated STOG | Aggregated | STOG | IESO | 2126 | 6.7% | 32.1
IESO Aggregated STWD | Aggregated | STWD | IESO | 139 | 10% | 36.5
IESO Aggregated WT | Aggregated | WT | IESO | 1280 | 0% | 0
MAPP_CA Aggregated CC | Aggregated | CC | MAPP_CA | 730 | 6.1% | 24.7
MAPP_CA Aggregated Coal | Aggregated | Coal | MAPP_CA | 1746 | 7% | 26.7
MAPP_CA Aggregated CT | Aggregated | CT | MAPP_CA | 563 | 8.3% | 15.8
MAPP_CA Aggregated HY | Aggregated | HY | MAPP_CA | 5834 | 4.9% | 0
MAPP_CA Aggregated STOG | Aggregated | STOG | MAPP_CA | 126 | 6.7% | 32.1
MAPP_CA Aggregated WT | Aggregated | WT | MAPP_CA | 275 | 0% | 0
MAPP_US Aggregated CC | Aggregated | CC | MAPP_US | 289 | 6.1% | 24.7
MAPP_US Aggregated Coal | Aggregated | Coal | MAPP_US | 289 | 7.8% | 25.5
MAPP_US Aggregated CT | Aggregated | CT | MAPP_US | 1056 | 9% | 13
MAPP_US Aggregated GEO | Aggregated | GEO | MAPP_US | 44 | 8% | 0
MAPP_US Aggregated HY | Aggregated | HY | MAPP_US | 2186 | 4.9% | 0
MAPP_US Aggregated LFG | Aggregated | LFG | MAPP_US | 2 | 5% | 18.3
MAPP_US Aggregated STOG | Aggregated | STOG | MAPP_US | 36 | 6.7% | 32.1
MAPP_US Aggregated WT | Aggregated | WT | MAPP_US | 1268 | 0% | 0
MISO_IN Aggregated CC | Aggregated | CC | MISO_IN | 1396 | 6.1% | 24.7
MISO_IN Aggregated Coal | Aggregated | Coal | MISO_IN | 2842 | 6.9% | 26.8
MISO_IN Aggregated CT | Aggregated | CT | MISO_IN | 3415 | 8.5% | 14.9
MISO_IN Aggregated HY | Aggregated | HY | MISO_IN | 75 | 4.9% | 0
MISO_IN Aggregated LFG | Aggregated | LFG | MISO_IN | 37 | 5% | 18.3
MISO_IN Aggregated STOG | Aggregated | STOG | MISO_IN | 279 | 6.7% | 32.1
MISO_IN Aggregated WT | Aggregated | WT | MISO_IN | 535 | 0% | 0
MISO_MI Aggregated CC | Aggregated | CC | MISO_MI | 4338 | 6.1% | 24.7
MISO_MI Aggregated Coal | Aggregated | Coal | MISO_MI | 2657 | 6.9% | 26.9
MISO_MI Aggregated CT | Aggregated | CT | MISO_MI | 4094 | 8.6% | 14.7
MISO_MI Aggregated HY | Aggregated | HY | MISO_MI | 141 | 4.9% | 0
MISO_MI Aggregated LFG | Aggregated | LFG | MISO_MI | 163 | 5% | 18.3
MISO_MI Aggregated NU | Aggregated | NU | MISO_MI | 1889 | 3.2% | 28.6
MISO_MI Aggregated PS | Aggregated | PS | MISO_MI | 1872 | 0% | 0
MISO_MI Aggregated STOG | Aggregated | STOG | MISO_MI | 2852 | 6.7% | 32.1
MISO_MI Aggregated STWD | Aggregated | STWD | MISO_MI | 163 | 10% | 36.5
MISO_MI Aggregated WT | Aggregated | WT | MISO_MI | 161 | 0% | 0
MISO_MO-IL Aggregated CC | Aggregated | CC | MISO_MO-IL | 1058 | 6.1% | 24.7
MISO_MO-IL Aggregated Coal | Aggregated | Coal | MISO_MO-IL | 2549 | 6.9% | 26.9
MISO_MO-IL Aggregated CT | Aggregated | CT | MISO_MO-IL | 5360 | 8.6% | 14.6
MISO_MO-IL Aggregated HY | Aggregated | HY | MISO_MO-IL | 352 | 4.9% | 0
MISO_MO-IL Aggregated LFG | Aggregated | LFG | MISO_MO-IL | 18 | 5% | 18.3
MISO_MO-IL Aggregated NU | Aggregated | NU | MISO_MO-IL | 2233 | 3.2% | 28.6
MISO_MO-IL Aggregated PS | Aggregated | PS | MISO_MO-IL | 440 | 0% | 0
MISO_MO-IL Aggregated STOG | Aggregated | STOG | MISO_MO-IL | 592 | 6.7% | 32.1
MISO_MO-IL Aggregated WT | Aggregated | WT | MISO_MO-IL | 378 | 0% | 0
MISO_W Aggregated CC | Aggregated | CC | MISO_W | 3024 | 6.1% | 24.7
MISO_W Aggregated Coal | Aggregated | Coal | MISO_W | 3071 | 7.3% | 26.2
MISO_W Aggregated CT | Aggregated | CT | MISO_W | 6677 | 9% | 13
MISO_W Aggregated HY | Aggregated | HY | MISO_W | 497 | 4.9% | 0
MISO_W Aggregated LFG | Aggregated | LFG | MISO_W | 205 | 5% | 18.3
MISO_W Aggregated NU | Aggregated | NU | MISO_W | 2267 | 3.2% | 28.6
MISO_W Aggregated STOG | Aggregated | STOG | MISO_W | 173 | 6.7% | 32.1
MISO_W Aggregated STWD | Aggregated | STWD | MISO_W | 313 | 10% | 36.5
MISO_W Aggregated WT | Aggregated | WT | MISO_W | 5558 | 0% | 0
MISO_WUMS Aggregated CC | Aggregated | CC | MISO_WUMS | 2724 | 6.1% | 24.7
MISO_WUMS Aggregated Coal | Aggregated | Coal | MISO_WUMS | 1857 | 7.4% | 26.1
MISO_WUMS Aggregated CT | Aggregated | CT | MISO_WUMS | 3720 | 8.6% | 14.7
MISO_WUMS Aggregated HY | Aggregated | HY | MISO_WUMS | 336 | 4.9% | 0
MISO_WUMS Aggregated LFG | Aggregated | LFG | MISO_WUMS | 71 | 5% | 18.3
MISO_WUMS Aggregated NU | Aggregated | NU | MISO_WUMS | 1582 | 3.2% | 28.6
MISO_WUMS Aggregated STOG | Aggregated | STOG | MISO_WUMS | 359 | 6.7% | 32.1
MISO_WUMS Aggregated STWD | Aggregated | STWD | MISO_WUMS | 105 | 10% | 36.5
MISO_WUMS Aggregated WT | Aggregated | WT | MISO_WUMS | 560 | 0% | 0
NE Aggregated CC | Aggregated | CC | NE | 358 | 6.1% | 24.7
NE Aggregated Coal | Aggregated | Coal | NE | 961 | 7% | 26.8
NE Aggregated CT | Aggregated | CT | NE | 1631 | 8.7% | 14.1
NE Aggregated HY | Aggregated | HY | NE | 167 | 4.9% | 0
NE Aggregated LFG | Aggregated | LFG | NE | 6 | 5% | 18.3
NE Aggregated NU | Aggregated | NU | NE | 1252 | 3.2% | 28.6
NE Aggregated STOG | Aggregated | STOG | NE | 270 | 6.7% | 32.1
NE Aggregated WT | Aggregated | WT | NE | 142 | 0% | 0
NEISO Aggregated CC | Aggregated | CC | NEISO | 11463 | 6.1% | 24.7
NEISO Aggregated Coal | Aggregated | Coal | NEISO | 767 | 7% | 26.7
NEISO Aggregated CT | Aggregated | CT | NEISO | 2384 | 9.4% | 11.5
NEISO Aggregated HY | Aggregated | HY | NEISO | 1933 | 4.9% | 0
NEISO Aggregated LFG | Aggregated | LFG | NEISO | 532 | 5% | 18.3
NEISO Aggregated NU | Aggregated | NU | NEISO | 4645 | 3.2% | 28.6
NEISO Aggregated PS | Aggregated | PS | NEISO | 1674 | 0% | 0
NEISO Aggregated PV | Aggregated | PV | NEISO | 2 | 60% | 36.5
NEISO Aggregated STOG | Aggregated | STOG | NEISO | 6236 | 6.7% | 32.1
NEISO Aggregated STWD | Aggregated | STWD | NEISO | 609 | 10% | 36.5
NEISO Aggregated WT | Aggregated | WT | NEISO | 202 | 0% | 0
NonRTO_Midwest Aggregated Coal | Aggregated | Coal | NonRTO_Midwest | 2059 | 6.8% | 26.9
NonRTO_Midwest Aggregated CT | Aggregated | CT | NonRTO_Midwest | 3365 | 8.3% | 15.8
NonRTO_Midwest Aggregated HY | Aggregated | HY | NonRTO_Midwest | 143 | 4.9% | 0
NonRTO_Midwest Aggregated LFG | Aggregated | LFG | NonRTO_Midwest | 14 | 5% | 18.3
NonRTO_Midwest Aggregated WT | Aggregated | WT | NonRTO_Midwest | 66 | 0% | 0
NYISO_A-F Aggregated CC | Aggregated | CC | NYISO_A-F | 3594 | 6.1% | 24.7
NYISO_A-F Aggregated Coal | Aggregated | Coal | NYISO_A-F | 1568 | 6.9% | 26.8
NYISO_A-F Aggregated CT | Aggregated | CT | NYISO_A-F | 260 | 8.6% | 14.5
NYISO_A-F Aggregated HY | Aggregated | HY | NYISO_A-F | 4395 | 4.9% | 0
NYISO_A-F Aggregated LFG | Aggregated | LFG | NYISO_A-F | 166 | 5% | 18.3
NYISO_A-F Aggregated NU | Aggregated | NU | NYISO_A-F | 3197 | 3.2% | 28.6
NYISO_A-F Aggregated PS | Aggregated | PS | NYISO_A-F | 1412 | 0% | 0
NYISO_A-F Aggregated STOG | Aggregated | STOG | NYISO_A-F | 1701 | 6.7% | 32.1
NYISO_A-F Aggregated STWD | Aggregated | STWD | NYISO_A-F | 86 | 10% | 36.5
NYISO_A-F Aggregated WT | Aggregated | WT | NYISO_A-F | 1283 | 0% | 0
NYISO_G-I Aggregated CC | Aggregated | CC | NYISO_G-I | 1157 | 6.1% | 24.7
NYISO_G-I Aggregated Coal | Aggregated | Coal | NYISO_G-I | 136 | 6.6% | 27.3
NYISO_G-I Aggregated CT | Aggregated | CT | NYISO_G-I | 152 | 9.5% | 10.8
NYISO_G-I Aggregated HY | Aggregated | HY | NYISO_G-I | 32 | 4.9% | 0
NYISO_G-I Aggregated LFG | Aggregated | LFG | NYISO_G-I | 64 | 5% | 18.3
NYISO_G-I Aggregated NU | Aggregated | NU | NYISO_G-I | 2045 | 3.2% | 28.6
NYISO_G-I Aggregated STOG | Aggregated | STOG | NYISO_G-I | 2431 | 6.7% | 32.1
NYISO_J-K Aggregated CC | Aggregated | CC | NYISO_J-K | 3658 | 6.1% | 24.7
NYISO_J-K Aggregated CT | Aggregated | CT | NYISO_J-K | 4948 | 9.2% | 12
NYISO_J-K Aggregated LFG | Aggregated | LFG | NYISO_J-K | 124 | 5% | 18.3
NYISO_J-K Aggregated STOG | Aggregated | STOG | NYISO_J-K | 6799 | 6.7% | 32.1
PJM_E Aggregated CC | Aggregated | CC | PJM_E | 7649 | 6.1% | 24.7
PJM_E Aggregated Coal | Aggregated | Coal | PJM_E | 1132 | 7% | 26.7
PJM_E Aggregated CT | Aggregated | CT | PJM_E | 6899 | 9.2% | 12.3
PJM_E Aggregated HY | Aggregated | HY | PJM_E | 258 | 4.9% | 0
PJM_E Aggregated LFG | Aggregated | LFG | PJM_E | 462 | 5% | 18.3
PJM_E Aggregated NU | Aggregated | NU | PJM_E | 8472 | 3.2% | 28.6
PJM_E Aggregated PS | Aggregated | PS | PJM_E | 400 | 0% | 0
PJM_E Aggregated PV | Aggregated | PV | PJM_E | 22 | 60% | 36.5
PJM_E Aggregated STOG | Aggregated | STOG | PJM_E | 3252 | 6.7% | 32.1
PJM_E Aggregated WT | Aggregated | WT | PJM_E | 10 | 0% | 0
PJM_ROM Aggregated CC | Aggregated | CC | PJM_ROM | 3986 | 6.1% | 24.7
PJM_ROM Aggregated Coal | Aggregated | Coal | PJM_ROM | 3829 | 7% | 26.7
PJM_ROM Aggregated CT | Aggregated | CT | PJM_ROM | 3555 | 9.4% | 11.3
PJM_ROM Aggregated HY | Aggregated | HY | PJM_ROM | 1236 | 4.9% | 0
PJM_ROM Aggregated LFG | Aggregated | LFG | PJM_ROM | 338 | 5% | 18.3
PJM_ROM Aggregated NU | Aggregated | NU | PJM_ROM | 5036 | 3.2% | 28.6
PJM_ROM Aggregated PS | Aggregated | PS | PJM_ROM | 1513 | 0% | 0
PJM_ROM Aggregated PV | Aggregated | PV | PJM_ROM | 4 | 60% | 36.5
PJM_ROM Aggregated STOG | Aggregated | STOG | PJM_ROM | 4109 | 6.7% | 32.1
PJM_ROM Aggregated STWD | Aggregated | STWD | PJM_ROM | 70 | 10% | 36.5
PJM_ROM Aggregated WT | Aggregated | WT | PJM_ROM | 731 | 0% | 0
PJM_ROR Aggregated CC | Aggregated | CC | PJM_ROR | 10542 | 6.1% | 24.7
PJM_ROR Aggregated Coal | Aggregated | Coal | PJM_ROR | 10420 | 7% | 26.8
PJM_ROR Aggregated CT | Aggregated | CT | PJM_ROR | 21073 | 8.5% | 15.1
PJM_ROR Aggregated HY | Aggregated | HY | PJM_ROR | 1604 | 4.9% | 0
PJM_ROR Aggregated LFG | Aggregated | LFG | PJM_ROR | 482 | 5% | 18.3
PJM_ROR Aggregated NU | Aggregated | NU | PJM_ROR | 20000 | 3.2% | 28.6
PJM_ROR Aggregated PS | Aggregated | PS | PJM_ROR | 3081 | 0% | 0
PJM_ROR Aggregated PV | Aggregated | PV | PJM_ROR | 24 | 60% | 36.5
PJM_ROR Aggregated STOG | Aggregated | STOG | PJM_ROR | 2122 | 6.7% | 32.1
PJM_ROR Aggregated STWD | Aggregated | STWD | PJM_ROR | 194 | 10% | 36.5
PJM_ROR Aggregated WT | Aggregated | WT | PJM_ROR | 2597 | 0% | 0
SOCO Aggregated CC | Aggregated | CC | SOCO | 14812 | 6.1% | 24.7
SOCO Aggregated Coal | Aggregated | Coal | SOCO | 3535 | 6.8% | 27
SOCO Aggregated CT | Aggregated | CT | SOCO | 12062 | 8.5% | 15
SOCO Aggregated HY | Aggregated | HY | SOCO | 4194 | 4.9% | 0
SOCO Aggregated LFG | Aggregated | LFG | SOCO | 37 | 5% | 18.3
SOCO Aggregated NU | Aggregated | NU | SOCO | 5771 | 3.2% | 28.6
SOCO Aggregated PS | Aggregated | PS | SOCO | 1675 | 0% | 0
SOCO Aggregated STOG | Aggregated | STOG | SOCO | 854 | 6.7% | 32.1
SOCO Aggregated STWD | Aggregated | STWD | SOCO | 668 | 10% | 36.5
SPP_N Aggregated CC | Aggregated | CC | SPP_N | 1386 | 6.1% | 24.7
SPP_N Aggregated Coal | Aggregated | Coal | SPP_N | 1716 | 7.1% | 26.6
SPP_N Aggregated CT | Aggregated | CT | SPP_N | 5596 | 8.8% | 14
SPP_N Aggregated HY | Aggregated | HY | SPP_N | 21 | 4.9% | 0
SPP_N Aggregated LFG | Aggregated | LFG | SPP_N | 7 | 5% | 18.3
SPP_N Aggregated NU | Aggregated | NU | SPP_N | 1160 | 3.2% | 28.6
SPP_N Aggregated STOG | Aggregated | STOG | SPP_N | 1748 | 6.7% | 32.1
SPP_N Aggregated WT | Aggregated | WT | SPP_N | 1227 | 0% | 0
SPP_S Aggregated CC | Aggregated | CC | SPP_S | 10917 | 6.1% | 24.7
SPP_S Aggregated Coal | Aggregated | Coal | SPP_S | 736 | 7% | 26.7
SPP_S Aggregated CT | Aggregated | CT | SPP_S | 3564 | 8.4% | 15.6
SPP_S Aggregated HY | Aggregated | HY | SPP_S | 2108 | 4.9% | 0
SPP_S Aggregated LFG | Aggregated | LFG | SPP_S | 19 | 5% | 18.3
SPP_S Aggregated PS | Aggregated | PS | SPP_S | 446 | 0% | 0
SPP_S Aggregated STOG | Aggregated | STOG | SPP_S | 10570 | 6.7% | 32.1
SPP_S Aggregated STWD | Aggregated | STWD | SPP_S | 84 | 10% | 36.5
SPP_S Aggregated WT | Aggregated | WT | SPP_S | 2297 | 0% | 0
TVA Aggregated CC | Aggregated | CC | TVA | 4463 | 6.1% | 24.7
TVA Aggregated Coal | Aggregated | Coal | TVA | 6043 | 6.6% | 27.3
TVA Aggregated CT | Aggregated | CT | TVA | 5949 | 8.3% | 15.8
TVA Aggregated HY | Aggregated | HY | TVA | 5111 | 4.9% | 0
TVA Aggregated LFG | Aggregated | LFG | TVA | 13 | 5% | 18.3
TVA Aggregated NU | Aggregated | NU | TVA | 6697 | 3.2% | 28.6
TVA Aggregated PS | Aggregated | PS | TVA | 1743 | 0% | 0
TVA Aggregated STWD | Aggregated | STWD | TVA | 5 | 10% | 36.5
TVA Aggregated WT | Aggregated | WT | TVA | 29 | 0% | 0
VACAR Aggregated CC | Aggregated | CC | VACAR | 3524 | 6.1% | 24.7
VACAR Aggregated Coal | Aggregated | Coal | VACAR | 5354 | 7% | 26.7
VACAR Aggregated CT | Aggregated | CT | VACAR | 9576 | 8.6% | 14.7
VACAR Aggregated HY | Aggregated | HY | VACAR | 2122 | 4.9% | 0
VACAR Aggregated LFG | Aggregated | LFG | VACAR | 63 | 5% | 18.3
VACAR Aggregated NU | Aggregated | NU | VACAR | 11430 | 3.2% | 28.6
VACAR Aggregated PS | Aggregated | PS | VACAR | 2616 | 0% | 0
VACAR Aggregated PV | Aggregated | PV | VACAR | 16 | 60% | 36.5
VACAR Aggregated STOG | Aggregated | STOG | VACAR | 92 | 6.7% | 32.1
VACAR Aggregated STWD | Aggregated | STWD | VACAR | 281 | 10% | 36.5
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit_6A_CoalUnitDetail
Appendix A, Exhibit 6A - Existing Coal Units with Additional Detail | [9 empty] | Emissions Control | FGD | Flue Gas Desulfurization
Updated 3/17/11 from CRA | [10 empty] | SCR | Selective Catalytic Reduction
[11 empty] | SNCR | Selective Non-Catalytic Reduction
[11 empty] | ACI | Advanced Carbon Injection
[11 empty] | ESP | Electrostatic Precipitator
[11 empty] | FF | Fabric Filter
Capacity Description | Unit (if applicable) | Aggregated/Stand Alone | Gen Type | NEEM Region | Summer Capacity MW | Wtd. Avg. Forced Outage Rate | Wtd. Avg. Planned Outage Days | SO2 Control Equipment (only Wet Lime is MACT-compliant for EIPC) | NOx Control Equipment | Particulate Matter Control Equipment (need FF to be MACT compliant for EIPC) | Mercury Control Equipment | Planned SO2 Control Equipment | Planned Nox Control Equipment | Planned Hg Control Equipment | Planned SO2 Control Equipment Year | Planned NOx Control Equipment Year | Planned Hg Control Equipment Year | Equipped with Cooling Towers (316B Compliant) | Coal Combustion Residuals
Big Cajun 2 | ST1 | Stand Alone | Coal | ENT | 580 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Big Cajun 2 | ST2 | Stand Alone | Coal | ENT | 575 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Big Cajun 3 | ST3 | Stand Alone | Coal | ENT | 588 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Independence (AR) | 1 | Stand Alone | Coal | ENT | 836 | 0.036 | 31.6 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Independence (AR) | 2 | Stand Alone | Coal | ENT | 842 | 0.036 | 31.6 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
New Madrid (Memphis) | 1 | Stand Alone | Coal | ENT | 580 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
New Madrid (Memphis) | 2 | Stand Alone | Coal | ENT | 580 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Roy S Nelson | 6 | Stand Alone | Coal | ENT | 550 | 0.077 | 34.4 | Other |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Thomas Hill | 2 | Stand Alone | Coal | ENT | 275 | 0.062 | 32.2 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Thomas Hill | 3 | Stand Alone | Coal | ENT | 670 | 0.062 | 32.2 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
White Bluff | 1 | Stand Alone | Coal | ENT | 815 | 0.036 | 31.6 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
White Bluff | 2 | Stand Alone | Coal | ENT | 840 | 0.036 | 31.6 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Big Bend (FL) | ST1 | Stand Alone | Coal | FRCC | 379 | 0.067 | 31.1 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Big Bend (FL) | ST2 | Stand Alone | Coal | FRCC | 373 | 0.067 | 31.1 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Big Bend (FL) | ST3 | Stand Alone | Coal | FRCC | 381 | 0.067 | 31.1 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Big Bend (FL) | ST4 | Stand Alone | Coal | FRCC | 417 | 0.067 | 31.1 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
C D McIntosh Jr | 3 | Stand Alone | Coal | FRCC | 342 | 0.064 | 29.9 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Cedar Bay Generating Co LP | GEN1 | Stand Alone | Coal | FRCC | 250 | 0.06 | 28.3 | Other | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
Crystal River | 1 | Stand Alone | Coal | FRCC | 375 | 0.066 | 33.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Crystal River | 2 | Stand Alone | Coal | FRCC | 494 | 0.066 | 33.3 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Crystal River | ST4 | Stand Alone | Coal | FRCC | 732 | 0.066 | 33.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Crystal River | 5 | Stand Alone | Coal | FRCC | 787 | 0.066 | 33.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Deerhaven Generating Station | 2 | Stand Alone | Coal | FRCC | 228 | 0.06 | 28.3 | Dry Lime FGD | SCR | ESP & FF | [7 empty] | Yes | Unit will have VOM adder
Indiantown Cogeneration Facility | GEN1 | Stand Alone | Coal | FRCC | 330 | 0.064 | 29.9 | Dry Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Northside Generating | 1 | Stand Alone | Coal | FRCC | 275 | 0.06 | 28.3 | Dry Lime FGD | SNCR | FF | [7 empty] | No | Unit will have VOM adder
Northside Generating | 2 | Stand Alone | Coal | FRCC | 275 | 0.06 | 28.3 | Dry Lime FGD | SNCR | FF | [7 empty] | No | Unit will have VOM adder
Polk Station | 1 | Stand Alone | Coal | FRCC | 235 | 0.06 | 28.3 | [10 empty] | No | Unit will have VOM adder
Seminole (FL) | 1 | Stand Alone | Coal | FRCC | 658 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Seminole (FL) | 2 | Stand Alone | Coal | FRCC | 658 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
St Johns River Power Park | 1 | Stand Alone | Coal | FRCC | 626 | 0.063 | 33.8 | Dual Alkali | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
St Johns River Power Park | 2 | Stand Alone | Coal | FRCC | 626 | 0.063 | 33.8 | Dual Alkali | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Stanton Energy Center | 1 | Stand Alone | Coal | FRCC | 440 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Stanton Energy Center | 2 | Stand Alone | Coal | FRCC | 446 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Atikokan GS | 1 | Stand Alone | Coal | IESO | 211 | 0.06 | 28.3 | [10 empty] | No | Unit will have VOM adder
Lambton GS | 1 | Stand Alone | Coal | IESO | 485 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Lambton GS | 2 | Stand Alone | Coal | IESO | 485 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Lambton GS | 3 | Stand Alone | Coal | IESO | 489 | 0.077 | 34.4 | Wet Lime FGD | SCR | [8 empty] | No | Unit will have VOM adder
Lambton GS | 4 | Stand Alone | Coal | IESO | 502 | 0.077 | 34.4 | Wet Lime FGD | SCR | [8 empty] | No | Unit will have VOM adder
Nanticoke | 1 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 2 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 3 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 4 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 5 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 6 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 | [10 empty] | No | Unit will have VOM adder
Nanticoke | 7 | Stand Alone | Coal | IESO | 508 | 0.077 | 34.4 |  | SCR | [8 empty] | No | Unit will have VOM adder
Nanticoke | 8 | Stand Alone | Coal | IESO | 490 | 0.077 | 34.4 |  | SCR | [8 empty] | No | Unit will have VOM adder
Boundary Dam | 6 | Stand Alone | Coal | MAPP_CA | 273 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
Poplar River | 1 | Stand Alone | Coal | MAPP_CA | 281 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
Poplar River | 2 | Stand Alone | Coal | MAPP_CA | 281 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
Shand | 1 | Stand Alone | Coal | MAPP_CA | 276 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
Antelope Valley | 1 | Stand Alone | Coal | MAPP_US | 450 | 0.067 | 29.8 | Dry Lime FGD |  | FF | [7 empty] | Yes | Unit will have VOM adder
Antelope Valley | 2 | Stand Alone | Coal | MAPP_US | 450 | 0.067 | 29.8 | Dry Lime FGD |  | FF | [7 empty] | Yes | Unit will have VOM adder
Coal Creek | 1 | Stand Alone | Coal | MAPP_US | 554 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Coal Creek | 2 | Stand Alone | Coal | MAPP_US | 560 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Coyote | 1 | Stand Alone | Coal | MAPP_US | 427 | 0.058 | 25.2 | Dry Lime FGD |  | FF | [7 empty] | Yes | Unit will have VOM adder
Laramie River | 1 | Stand Alone | Coal | MAPP_US | 565 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Leland Olds 1 & 2 | 1 | Stand Alone | Coal | MAPP_US | 221 | 0.058 | 25.2 |  |  | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Leland Olds 1 & 2 | 2 | Stand Alone | Coal | MAPP_US | 448 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Milton R Young | ST1 | Stand Alone | Coal | MAPP_US | 250 | 0.058 | 25.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Milton R Young | ST2 | Stand Alone | Coal | MAPP_US | 447 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
A B Brown | ST1 | Stand Alone | Coal | MISO_IN | 245 | 0.06 | 28.3 | Dual Alkali | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
A B Brown | ST2 | Stand Alone | Coal | MISO_IN | 245 | 0.06 | 28.3 | Dual Alkali | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
AES Petersburg (IN) | ST1 | Stand Alone | Coal | MISO_IN | 232 | 0.075 | 33.6 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
AES Petersburg (IN) | ST2 | Stand Alone | Coal | MISO_IN | 435 | 0.075 | 33.6 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
AES Petersburg (IN) | ST3 | Stand Alone | Coal | MISO_IN | 540 | 0.075 | 33.6 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
AES Petersburg (IN) | 4 | Stand Alone | Coal | MISO_IN | 545 | 0.075 | 33.6 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Bailly | 8 | Stand Alone | Coal | MISO_IN | 320 | 0.064 | 29.9 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cayuga | 1 | Stand Alone | Coal | NYISO_A-F | 500 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Cayuga | 2 | Stand Alone | Coal | NYISO_A-F | 495 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
D B Wilson | UN1 | Stand Alone | Coal | MISO_IN | 417 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
F B Culley | 3 | Stand Alone | Coal | MISO_IN | 270 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | No | Unit will have VOM adder
Gibson Station | 1 | Stand Alone | Coal | MISO_IN | 630 | 0.063 | 33.8 | Wet Lime FGD | SCR | [8 empty] | No | Unit will have VOM adder
Gibson Station | 2 | Stand Alone | Coal | MISO_IN | 630 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Gibson Station | 3 | Stand Alone | Coal | MISO_IN | 630 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Gibson Station | 4 | Stand Alone | Coal | MISO_IN | 622 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Gibson Station | 5 | Stand Alone | Coal | MISO_IN | 619 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Harding Street | 7 | Stand Alone | Coal | MISO_IN | 435 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Merom | 1 | Stand Alone | Coal | MISO_IN | 476 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Merom | 2 | Stand Alone | Coal | MISO_IN | 479 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Michigan City | 12 | Stand Alone | Coal | MISO_IN | 469 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
R M Schahfer | 14 | Stand Alone | Coal | MISO_IN | 431 | 0.071 | 32.4 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
R M Schahfer | 15 | Stand Alone | Coal | MISO_IN | 472 | 0.071 | 32.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
R M Schahfer | 17 | Stand Alone | Coal | MISO_IN | 361 | 0.071 | 32.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
R M Schahfer | 18 | Stand Alone | Coal | MISO_IN | 361 | 0.071 | 32.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Robert D Green | GEN1 | Stand Alone | Coal | MISO_IN | 231 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Robert D Green | GEN2 | Stand Alone | Coal | MISO_IN | 223 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Wabash River | 6 | Stand Alone | Coal | MISO_IN | 318 | 0.062 | 29.2 | [10 empty] | No | Unit will have VOM adder
Wabash River | IGCC | Stand Alone | Coal | MISO_IN | 274 | 0.062 | 29.2 | Other | [9 empty] | No | Unit will have VOM adder
Belle River | ST1 | Stand Alone | Coal | MISO_MI | 635 | 0.063 | 33.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Belle River | ST2 | Stand Alone | Coal | MISO_MI | 635 | 0.063 | 33.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
D E Karn | 1 | Stand Alone | Coal | MISO_MI | 255 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
D E Karn | 2 | Stand Alone | Coal | MISO_MI | 260 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
J H Campbell | 1 | Stand Alone | Coal | MISO_MI | 260 | 0.047 | 30.6 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
J H Campbell | 2 | Stand Alone | Coal | MISO_MI | 355 | 0.047 | 30.6 |  |  | ESP |  |  | SCR |  |  | 2013 |  | No | Unit will have VOM adder
J H Campbell | 3 | Stand Alone | Coal | MISO_MI | 825 | 0.047 | 30.6 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Monroe (MI) | 1 | Stand Alone | Coal | MISO_MI | 770 | 0.063 | 33.8 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Monroe (MI) | 2 | Stand Alone | Coal | MISO_MI | 785 | 0.063 | 33.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Monroe (MI) | 3 | Stand Alone | Coal | MISO_MI | 785 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Monroe (MI) | 4 | Stand Alone | Coal | MISO_MI | 775 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
River Rouge | 2 | Stand Alone | Coal | MISO_MI | 251 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
River Rouge | 3 | Stand Alone | Coal | MISO_MI | 272 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
St Clair | 6 | Stand Alone | Coal | MISO_MI | 312 | 0.071 | 32.6 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
St Clair | 7 | Stand Alone | Coal | MISO_MI | 440 | 0.071 | 32.6 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Trenton Channel | 9 | Stand Alone | Coal | MISO_MI | 520 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Baldwin Energy Complex | 1 | Stand Alone | Coal | MISO_MO-IL | 586 | 0.077 | 34.4 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Baldwin Energy Complex | 2 | Stand Alone | Coal | MISO_MO-IL | 586 | 0.077 | 34.4 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Baldwin Energy Complex | 3 | Stand Alone | Coal | MISO_MO-IL | 592 | 0.077 | 34.4 | Dry Lime FGD |  | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Coffeen | 1 | Stand Alone | Coal | MISO_MO-IL | 340 | 0.072 | 32.7 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Coffeen | 2 | Stand Alone | Coal | MISO_MO-IL | 560 | 0.072 | 32.7 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Dallman | 4 | Stand Alone | Coal | MISO_MO-IL | 200 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | No | Unit will have VOM adder
Duck Creek | 1 | Stand Alone | Coal | MISO_MO-IL | 358 | 0.064 | 29.9 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
E D Edwards | 2 | Stand Alone | Coal | MISO_MO-IL | 263 | 0.062 | 29.2 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
E D Edwards | 3 | Stand Alone | Coal | MISO_MO-IL | 335 | 0.062 | 29.2 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Havana | 6 | Stand Alone | Coal | MISO_MO-IL | 438 | 0.077 | 34.4 |  | SCR | ESP & FF | ACI | Dry Lime FGD |  |  | 2013 |  |  | No | Unit will have VOM adder
Hennepin Power Station | 2 | Stand Alone | Coal | MISO_MO-IL | 215 | 0.06 | 28.3 |  |  | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Labadie | 1 | Stand Alone | Coal | MISO_MO-IL | 605 | 0.066 | 33.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Labadie | 2 | Stand Alone | Coal | MISO_MO-IL | 594 | 0.066 | 33.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Labadie | 3 | Stand Alone | Coal | MISO_MO-IL | 603 | 0.066 | 33.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Labadie | 4 | Stand Alone | Coal | MISO_MO-IL | 604 | 0.066 | 33.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Meramec | 3 | Stand Alone | Coal | MISO_MO-IL | 261 | 0.062 | 29.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Meramec | 4 | Stand Alone | Coal | MISO_MO-IL | 342 | 0.062 | 29.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Meredosia | 3 | Stand Alone | Coal | MISO_MO-IL | 203 | 0.06 | 28.3 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Newton (IL) | 1 | Stand Alone | Coal | MISO_MO-IL | 603 | 0.07 | 34.1 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Newton (IL) | 2 | Stand Alone | Coal | MISO_MO-IL | 598 | 0.07 | 34.1 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Rush Island | 1 | Stand Alone | Coal | MISO_MO-IL | 600 | 0.07 | 34.1 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Rush Island | 2 | Stand Alone | Coal | MISO_MO-IL | 581 | 0.07 | 34.1 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Sioux | 1 | Stand Alone | Coal | MISO_MO-IL | 495 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Sioux | 2 | Stand Alone | Coal | MISO_MO-IL | 498 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Wood River (IL) | 5 | Stand Alone | Coal | MISO_MO-IL | 355 | 0.064 | 29.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Allen S King Plant | 1 | Stand Alone | Coal | MISO_W | 528 | 0.077 | 34.4 | Dry Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Big Stone | ST1 | Stand Alone | Coal | MISO_W | 475 | 0.077 | 34.4 |  |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
Clay Boswell | 3 | Stand Alone | Coal | MISO_W | 351 | 0.072 | 32.6 | Wet Lime FGD | SCR | FF | ACI | [6 empty] | No | Unit will have VOM adder
Clay Boswell | 4 | Stand Alone | Coal | MISO_W | 535 | 0.072 | 32.6 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Genoa No3 | ST3 | Stand Alone | Coal | MISO_W | 351 | 0.064 | 29.9 | Dry Lime FGD |  | ESP & FF |  |  |  | ACI |  |  | 2012 | No | Unit will have VOM adder
George Neal North | 2 | Stand Alone | Coal | MISO_W | 295 | 0.071 | 32.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
George Neal North | 3 | Stand Alone | Coal | MISO_W | 515 | 0.071 | 32.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
George Neal South | 4 | Stand Alone | Coal | MISO_W | 644 | 0.063 | 33.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
John P Madgett | 1 | Stand Alone | Coal | MISO_W | 393 | 0.064 | 29.9 |  |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
Lansing | 4 | Stand Alone | Coal | MISO_W | 262 | 0.06 | 28.3 |  | SCR | ESP & FF | [7 empty] | No | Unit will have VOM adder
Louisa | 1 | Stand Alone | Coal | MISO_W | 745 | 0.063 | 33.8 | Dry Lime FGD |  | ESP & FF | [7 empty] | Yes | Unit will have VOM adder
M L Kapp | 2 | Stand Alone | Coal | MISO_W | 212 | 0.06 | 28.3 | Other |  | ESP | [7 empty] | No | Unit will have VOM adder
Ottumwa (IA IPL) | 1 | Stand Alone | Coal | MISO_W | 710 | 0.063 | 33.8 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Sherburne County | 1 | Stand Alone | Coal | MISO_W | 697 | 0.052 | 32.9 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Sherburne County | 2 | Stand Alone | Coal | MISO_W | 682 | 0.052 | 32.9 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Sherburne County | 3 | Stand Alone | Coal | MISO_W | 864 | 0.052 | 32.9 | Dry Lime FGD |  | FF | [7 empty] | Yes | Unit will have VOM adder
Walter Scott Jr Energy Center | ST3 | Stand Alone | Coal | MISO_W | 690 | 0.048 | 32.6 | Dry Lime FGD |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
Walter Scott Jr Energy Center | ST4 | Stand Alone | Coal | MISO_W | 800 | 0.048 | 32.6 | Dry Lime FGD | SCR | FF | ACI | [6 empty] | No | Unit will have VOM adder
Columbia (WI) | 1 | Stand Alone | Coal | MISO_WUMS | 554 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Columbia (WI) | 2 | Stand Alone | Coal | MISO_WUMS | 564 | 0.077 | 34.4 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Edgewater (WI) | 4 | Stand Alone | Coal | MISO_WUMS | 320 | 0.071 | 32.5 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Edgewater (WI) | 5 | Stand Alone | Coal | MISO_WUMS | 414 | 0.071 | 32.5 |  |  | ESP | ACI |  | SCR |  |  | 2013 |  | No | Unit will have VOM adder
Oak Creek Power Plant | 1 | Stand Alone | Coal | MISO_WUMS | 615 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | No | Unit will have VOM adder
Pleasant Prairie | 1 | Stand Alone | Coal | MISO_WUMS | 604 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Pleasant Prairie | 2 | Stand Alone | Coal | MISO_WUMS | 612 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
South Oak Creek | 5 | Stand Alone | Coal | MISO_WUMS | 261 | 0.061 | 28.7 |  |  | ESP |  | Wet Lime FGD | SCR |  | 2013 | 2013 |  | No | Unit will have VOM adder
South Oak Creek | 6 | Stand Alone | Coal | MISO_WUMS | 264 | 0.061 | 28.7 |  |  | ESP |  | Wet Lime FGD | SCR |  | 2013 | 2013 |  | No | Unit will have VOM adder
South Oak Creek | 7 | Stand Alone | Coal | MISO_WUMS | 298 | 0.061 | 28.7 |  |  | ESP |  | Wet Lime FGD | SCR |  | 2013 | 2013 |  | No | Unit will have VOM adder
South Oak Creek | 8 | Stand Alone | Coal | MISO_WUMS | 312 | 0.061 | 28.7 |  |  | ESP |  | Wet Lime FGD | SCR |  | 2013 | 2013 |  | No | Unit will have VOM adder
Weston | 3 | Stand Alone | Coal | MISO_WUMS | 333 | 0.072 | 32.7 |  |  | FF | ACI | [6 empty] | No | Unit will have VOM adder
Weston | 4 | Stand Alone | Coal | MISO_WUMS | 537 | 0.072 | 32.7 | Dry Lime FGD | SCR | FF | ACI | [6 empty] | No | Unit will have VOM adder
Gerald Gentleman | 1 | Stand Alone | Coal | NE | 665 | 0.063 | 33.8 |  |  | FF | [7 empty] | No | Unit will have VOM adder
Gerald Gentleman | 2 | Stand Alone | Coal | NE | 700 | 0.063 | 33.8 |  |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
Nebraska City | 1 | Stand Alone | Coal | NE | 646 | 0.06 | 29.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Nebraska City | 2 | Stand Alone | Coal | NE | 682 | 0.06 | 29.4 | Dry Lime FGD | SCR | FF | ACI | [6 empty] | No | Unit will have VOM adder
North Omaha | 5 | Stand Alone | Coal | NE | 224 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Brayton PT | GEN1 | Stand Alone | Coal | NEISO | 244 | 0.062 | 31.3 | Dry Lime FGD | SCR | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Brayton PT | GEN2 | Stand Alone | Coal | NEISO | 244 | 0.062 | 31.3 | Dry Lime FGD |  | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Brayton PT | GEN3 | Stand Alone | Coal | NEISO | 612 | 0.062 | 31.3 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Bridgeport Station | 3 | Stand Alone | Coal | NEISO | 383 | 0.064 | 29.9 |  |  | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Merrimack | 2 | Stand Alone | Coal | NEISO | 320 | 0.064 | 29.9 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Cane Run | 6 | Stand Alone | Coal | NonRTO_Midwest | 240 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Clifty Creek | 1 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Clifty Creek | 2 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Clifty Creek | 3 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Clifty Creek | 4 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Clifty Creek | 5 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
Clifty Creek | 6 | Stand Alone | Coal | NonRTO_Midwest | 201 | 0.06 | 28.3 |  |  | ESP |  | Wet Lime FGD |  |  | 2012 |  |  | No | Unit will have VOM adder
E W Brown | 3 | Stand Alone | Coal | NonRTO_Midwest | 429 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Elmer Smith | 2 | Stand Alone | Coal | NonRTO_Midwest | 261 | 0.06 | 28.3 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Ghent | 1 | Stand Alone | Coal | NonRTO_Midwest | 475 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Ghent | 2 | Stand Alone | Coal | NonRTO_Midwest | 484 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Ghent | 3 | Stand Alone | Coal | NonRTO_Midwest | 480 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Ghent | 4 | Stand Alone | Coal | NonRTO_Midwest | 479 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Hugh L Spurlock | 1 | Stand Alone | Coal | NonRTO_Midwest | 325 | 0.067 | 30.9 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Hugh L Spurlock | 2 | Stand Alone | Coal | NonRTO_Midwest | 510 | 0.067 | 30.9 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Hugh L Spurlock | 3 | Stand Alone | Coal | NonRTO_Midwest | 268 | 0.067 | 30.9 | Other | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
Hugh L Spurlock | 4 | Stand Alone | Coal | NonRTO_Midwest | 278 | 0.067 | 30.9 | Other | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
J Sherman Cooper | 2 | Stand Alone | Coal | NonRTO_Midwest | 225 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Kyger Creek | 1 | Stand Alone | Coal | NonRTO_Midwest | 200 | 0.06 | 28.3 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2011 |  |  | No | Unit will have VOM adder
Mill Creek (KY) | 1 | Stand Alone | Coal | NonRTO_Midwest | 303 | 0.068 | 31.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Mill Creek (KY) | 2 | Stand Alone | Coal | NonRTO_Midwest | 301 | 0.068 | 31.4 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Mill Creek (KY) | 3 | Stand Alone | Coal | NonRTO_Midwest | 391 | 0.068 | 31.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Mill Creek (KY) | 4 | Stand Alone | Coal | NonRTO_Midwest | 477 | 0.068 | 31.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Trimble Station (LGE) | 1 | Stand Alone | Coal | NonRTO_Midwest | 511 | 0.069 | 34 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Trimble Station (LGE) | ST2 | Stand Alone | Coal | NonRTO_Midwest | 732 | 0.069 | 34 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | Yes | Unit will have VOM adder
AES Somerset LLC | GEN1 | Stand Alone | Coal | NYISO_A-F | 684 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Danskammer Generating Station | 4 | Stand Alone | Coal | NYISO_G-I | 233 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Carneys Point Generating Plant | GEN1 | Stand Alone | Coal | PJM_E | 262 | 0.06 | 28.3 | Dry Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Eddystone Generating Station | 1 | Stand Alone | Coal | PJM_E | 279 | 0.062 | 29.2 | Magnesium Oxide | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Eddystone Generating Station | 2 | Stand Alone | Coal | PJM_E | 309 | 0.062 | 29.2 | Magnesium Oxide | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Hudson Generating Station | 2 | Stand Alone | Coal | PJM_E | 568 | 0.077 | 34.4 | Dry Lime FGD | SCR | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Indian River Generating Station (DE) | 4 | Stand Alone | Coal | PJM_E | 436 | 0.077 | 34.4 |  | SNCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Logan Generating Plant | GEN1 | Stand Alone | Coal | PJM_E | 219 | 0.06 | 28.3 | Dry Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Mercer Generating Station | 1 | Stand Alone | Coal | PJM_E | 324 | 0.064 | 29.9 |  | SCR | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Mercer Generating Station | 2 | Stand Alone | Coal | PJM_E | 324 | 0.064 | 29.9 |  | SCR | ESP & FF | ACI | [6 empty] | No | Unit will have VOM adder
Brandon Shores | 1 | Stand Alone | Coal | PJM_ROM | 643 | 0.063 | 33.8 | Wet Lime FGD | SCR | FF | ACI | [6 empty] | Yes | Unit will have VOM adder
Brandon Shores | 2 | Stand Alone | Coal | PJM_ROM | 643 | 0.063 | 33.8 | Wet Lime FGD | SCR | FF | ACI | [6 empty] | Yes | Unit will have VOM adder
Chalk Point | ST1 | Stand Alone | Coal | PJM_ROM | 341 | 0.064 | 29.9 | Wet Lime FGD | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Chalk Point | ST2 | Stand Alone | Coal | PJM_ROM | 342 | 0.064 | 29.9 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Conemaugh | 1 | Stand Alone | Coal | PJM_ROM | 850 | 0.036 | 31.6 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Conemaugh | 2 | Stand Alone | Coal | PJM_ROM | 850 | 0.036 | 31.6 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Herbert A Wagner | 3 | Stand Alone | Coal | PJM_ROM | 324 | 0.064 | 29.9 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Homer City Station | 1 | Stand Alone | Coal | PJM_ROM | 620 | 0.063 | 33.8 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Homer City Station | 2 | Stand Alone | Coal | PJM_ROM | 614 | 0.063 | 33.8 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Homer City Station | 3 | Stand Alone | Coal | PJM_ROM | 650 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Keystone (PA) | 1 | Stand Alone | Coal | PJM_ROM | 850 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Keystone (PA) | 2 | Stand Alone | Coal | PJM_ROM | 850 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Montour | MT1 | Stand Alone | Coal | PJM_ROM | 759 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Montour | MT2 | Stand Alone | Coal | PJM_ROM | 766 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Morgantown Generating Station | ST1 | Stand Alone | Coal | PJM_ROM | 624 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Morgantown Generating Station | ST2 | Stand Alone | Coal | PJM_ROM | 620 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Portland (PA) | 2 | Stand Alone | Coal | PJM_ROM | 243 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
PPL Brunner Island | BI1 | Stand Alone | Coal | PJM_ROM | 320 | 0.063 | 31.9 | Wet Lime FGD |  | FF | [7 empty] | No | Unit will have VOM adder
PPL Brunner Island | BI2 | Stand Alone | Coal | PJM_ROM | 374 | 0.063 | 31.9 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
PPL Brunner Island | BI3 | Stand Alone | Coal | PJM_ROM | 748 | 0.063 | 31.9 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Seward | FB1 | Stand Alone | Coal | PJM_ROM | 521 | 0.077 | 34.4 | Other | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
Ashtabula | 5 | Stand Alone | Coal | PJM_ROR | 244 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Avon Lake | 9 | Stand Alone | Coal | PJM_ROR | 625 | 0.063 | 33.8 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Bay Shore | 4 | Stand Alone | Coal | PJM_ROR | 215 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Big Sandy | 1 | Stand Alone | Coal | PJM_ROR | 260 | 0.042 | 30.8 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Big Sandy | 2 | Stand Alone | Coal | PJM_ROR | 800 | 0.042 | 30.8 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Birchwood Power Facility | 1 | Stand Alone | Coal | PJM_ROR | 238 | 0.06 | 28.3 | Dry Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Bruce Mansfield | 1 | Stand Alone | Coal | PJM_ROR | 830 | 0.036 | 31.6 | Wet Lime FGD | SCR | [8 empty] | Yes | Unit will have VOM adder
Bruce Mansfield | 2 | Stand Alone | Coal | PJM_ROR | 830 | 0.036 | 31.6 | Wet Lime FGD | SCR | [8 empty] | Yes | Unit will have VOM adder
Bruce Mansfield | 3 | Stand Alone | Coal | PJM_ROR | 850 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Cardinal | 1 | Stand Alone | Coal | PJM_ROR | 580 | 0.072 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cardinal | 2 | Stand Alone | Coal | PJM_ROR | 590 | 0.072 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cardinal | 3 | Stand Alone | Coal | PJM_ROR | 630 | 0.072 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Chesapeake | ST4 | Stand Alone | Coal | PJM_ROR | 217 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Chesterfield | 5 | Stand Alone | Coal | PJM_ROR | 324 | 0.063 | 32.5 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Chesterfield | 6 | Stand Alone | Coal | PJM_ROR | 658 | 0.063 | 32.5 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | No | Unit will have VOM adder
Cheswick Power Plant | 1 | Stand Alone | Coal | PJM_ROR | 580 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Clinch River | 1 | Stand Alone | Coal | PJM_ROR | 230 | 0.06 | 28.3 |  | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Clinch River | 2 | Stand Alone | Coal | PJM_ROR | 230 | 0.06 | 28.3 |  | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Clinch River | 3 | Stand Alone | Coal | PJM_ROR | 230 | 0.06 | 28.3 |  | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Clover | 1 | Stand Alone | Coal | PJM_ROR | 431 | 0.077 | 34.4 | Wet Lime FGD | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
Clover | 2 | Stand Alone | Coal | PJM_ROR | 434 | 0.077 | 34.4 | Wet Lime FGD | SNCR | FF | [7 empty] | Yes | Unit will have VOM adder
Conesville | 4 | Stand Alone | Coal | PJM_ROR | 780 | 0.063 | 31.9 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Conesville | 5 | Stand Alone | Coal | PJM_ROR | 375 | 0.063 | 31.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Conesville | 6 | Stand Alone | Coal | PJM_ROR | 375 | 0.063 | 31.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Crawford (IL) | 7 | Stand Alone | Coal | PJM_ROR | 213 | 0.062 | 29.3 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Crawford (IL) | 8 | Stand Alone | Coal | PJM_ROR | 319 | 0.062 | 29.3 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
East Bend | 2 | Stand Alone | Coal | PJM_ROR | 600 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Eastlake (OH) | 4 | Stand Alone | Coal | PJM_ROR | 240 | 0.072 | 32.7 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Eastlake (OH) | 5 | Stand Alone | Coal | PJM_ROR | 597 | 0.072 | 32.7 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Fisk Street | 19 | Stand Alone | Coal | PJM_ROR | 326 | 0.064 | 29.9 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Fort Martin | 1 | Stand Alone | Coal | PJM_ROR | 552 | 0.077 | 34.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Fort Martin | 2 | Stand Alone | Coal | PJM_ROR | 555 | 0.077 | 34.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Gavin | 1 | Stand Alone | Coal | PJM_ROR | 1320 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Gavin | 2 | Stand Alone | Coal | PJM_ROR | 1320 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Glen Lyn | 6 | Stand Alone | Coal | PJM_ROR | 235 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Harrison (WV) | 1 | Stand Alone | Coal | PJM_ROR | 652 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Harrison (WV) | 2 | Stand Alone | Coal | PJM_ROR | 651 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Harrison (WV) | 3 | Stand Alone | Coal | PJM_ROR | 651 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Hatfields Ferry Power Station | 1 | Stand Alone | Coal | PJM_ROR | 530 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Hatfields Ferry Power Station | 2 | Stand Alone | Coal | PJM_ROR | 530 | 0.077 | 34.4 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Hatfields Ferry Power Station | 3 | Stand Alone | Coal | PJM_ROR | 530 | 0.077 | 34.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | Yes | Unit will have VOM adder
J M Stuart | 1 | Stand Alone | Coal | PJM_ROR | 585 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
J M Stuart | 2 | Stand Alone | Coal | PJM_ROR | 585 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
J M Stuart | 3 | Stand Alone | Coal | PJM_ROR | 585 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
J M Stuart | 4 | Stand Alone | Coal | PJM_ROR | 585 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
John E Amos | 1 | Stand Alone | Coal | PJM_ROR | 800 | 0.054 | 33.3 |  | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
John E Amos | 2 | Stand Alone | Coal | PJM_ROR | 800 | 0.054 | 33.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
John E Amos | 3 | Stand Alone | Coal | PJM_ROR | 1300 | 0.054 | 33.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Joliet 29 | 7 | Stand Alone | Coal | PJM_ROR | 518 | 0.077 | 34.4 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Joliet 29 | 8 | Stand Alone | Coal | PJM_ROR | 518 | 0.077 | 34.4 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Joliet 9 | 6 | Stand Alone | Coal | PJM_ROR | 314 | 0.064 | 29.9 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Kammer | 1 | Stand Alone | Coal | PJM_ROR | 200 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Kammer | 2 | Stand Alone | Coal | PJM_ROR | 200 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Kammer | 3 | Stand Alone | Coal | PJM_ROR | 200 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Kanawha River | 1 | Stand Alone | Coal | PJM_ROR | 200 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Kanawha River | 2 | Stand Alone | Coal | PJM_ROR | 200 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Killen Station | 2 | Stand Alone | Coal | PJM_ROR | 600 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Kincaid Generation LLC | 1 | Stand Alone | Coal | PJM_ROR | 579 | 0.077 | 34.4 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Kincaid Generation LLC | 2 | Stand Alone | Coal | PJM_ROR | 579 | 0.077 | 34.4 |  | SCR | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Lake Shore | 18 | Stand Alone | Coal | PJM_ROR | 245 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Miami Fort | 7 | Stand Alone | Coal | PJM_ROR | 500 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Miami Fort | 8 | Stand Alone | Coal | PJM_ROR | 500 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Mitchell (WV) | 1 | Stand Alone | Coal | PJM_ROR | 770 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Mitchell (WV) | 2 | Stand Alone | Coal | PJM_ROR | 790 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Mitchell Power Station | 3 | Stand Alone | Coal | PJM_ROR | 277 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Mountaineer | 1 | Stand Alone | Coal | PJM_ROR | 1310 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
MT Storm | 1 | Stand Alone | Coal | PJM_ROR | 524 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
MT Storm | 2 | Stand Alone | Coal | PJM_ROR | 524 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
MT Storm | 3 | Stand Alone | Coal | PJM_ROR | 512 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Muskingum River | 3 | Stand Alone | Coal | PJM_ROR | 205 | 0.07 | 31.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Muskingum River | 4 | Stand Alone | Coal | PJM_ROR | 205 | 0.07 | 31.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Muskingum River | 5 | Stand Alone | Coal | PJM_ROR | 585 | 0.07 | 31.9 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Phil Sporn | 5 | Stand Alone | Coal | PJM_ROR | 440 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Pleasants | 1 | Stand Alone | Coal | PJM_ROR | 639 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Pleasants | 2 | Stand Alone | Coal | PJM_ROR | 639 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Powerton | 5 | Stand Alone | Coal | PJM_ROR | 769 | 0.063 | 33.8 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Powerton | 6 | Stand Alone | Coal | PJM_ROR | 769 | 0.063 | 33.8 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Rockport | 1 | Stand Alone | Coal | PJM_ROR | 1300 | 0.076 | 35.3 |  |  | ESP | ACI | [6 empty] | Yes | Unit will have VOM adder
Rockport | 2 | Stand Alone | Coal | PJM_ROR | 1300 | 0.076 | 35.3 |  |  | ESP | ACI | [6 empty] | Yes | Unit will have VOM adder
State Line Energy | ST4 | Stand Alone | Coal | PJM_ROR | 318 | 0.064 | 29.9 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Tanners Creek | 3 | Stand Alone | Coal | PJM_ROR | 200 | 0.072 | 32.7 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Tanners Creek | 4 | Stand Alone | Coal | PJM_ROR | 500 | 0.072 | 32.7 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
W H Sammis | 5 | Stand Alone | Coal | PJM_ROR | 300 | 0.063 | 33 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
W H Sammis | 6 | Stand Alone | Coal | PJM_ROR | 600 | 0.063 | 33 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
W H Sammis | 7 | Stand Alone | Coal | PJM_ROR | 600 | 0.063 | 33 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
W H Zimmer | ST1 | Stand Alone | Coal | PJM_ROR | 1300 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Walter C Beckjord | 5 | Stand Alone | Coal | PJM_ROR | 238 | 0.071 | 32.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Walter C Beckjord | 6 | Stand Alone | Coal | PJM_ROR | 414 | 0.071 | 32.2 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Waukegan | 7 | Stand Alone | Coal | PJM_ROR | 328 | 0.064 | 29.9 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Waukegan | 8 | Stand Alone | Coal | PJM_ROR | 361 | 0.064 | 29.9 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Will County | 3 | Stand Alone | Coal | PJM_ROR | 251 | 0.071 | 32.4 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Will County | 4 | Stand Alone | Coal | PJM_ROR | 510 | 0.071 | 32.4 |  |  | ESP | ACI | [6 empty] | No | Unit will have VOM adder
Bowen | 1 | Stand Alone | Coal | SOCO | 713 | 0.048 | 32.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Bowen | 2 | Stand Alone | Coal | SOCO | 718 | 0.048 | 32.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Bowen | 3 | Stand Alone | Coal | SOCO | 895 | 0.048 | 32.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Bowen | 4 | Stand Alone | Coal | SOCO | 895 | 0.048 | 32.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Charles R Lowman | 2 | Stand Alone | Coal | SOCO | 235 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Charles R Lowman | 3 | Stand Alone | Coal | SOCO | 235 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Crist | 6 | Stand Alone | Coal | SOCO | 302 | 0.072 | 32.7 | Wet Lime FGD | SNCR | ESP |  |  | SCR |  |  | 2013 |  | No | Unit will have VOM adder
Crist | 7 | Stand Alone | Coal | SOCO | 472 | 0.072 | 32.7 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
E C Gaston | 1 | Stand Alone | Coal | SOCO | 254 | 0.049 | 29.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
E C Gaston | 2 | Stand Alone | Coal | SOCO | 256 | 0.049 | 29.8 |  |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
E C Gaston | 3 | Stand Alone | Coal | SOCO | 254 | 0.049 | 29.8 |  |  | ESP & FF | [7 empty] | No | Unit will have VOM adder
E C Gaston | ST4 | Stand Alone | Coal | SOCO | 256 | 0.049 | 29.8 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
E C Gaston | 5 | Stand Alone | Coal | SOCO | 842 | 0.049 | 29.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Gorgas 2 & 3 | 10 | Stand Alone | Coal | SOCO | 677 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Greene County (AL) | 1 | Stand Alone | Coal | SOCO | 254 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Greene County (AL) | 2 | Stand Alone | Coal | SOCO | 243 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Hammond | 4 | Stand Alone | Coal | SOCO | 503 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Harllee Branch | 1 | Stand Alone | Coal | SOCO | 266 | 0.071 | 32.5 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Harllee Branch | 2 | Stand Alone | Coal | SOCO | 325 | 0.071 | 32.5 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Harllee Branch | 3 | Stand Alone | Coal | SOCO | 509 | 0.071 | 32.5 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Harllee Branch | 4 | Stand Alone | Coal | SOCO | 507 | 0.071 | 32.5 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Jack McDonough | 1 | Stand Alone | Coal | SOCO | 251 | 0.06 | 28.3 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Jack McDonough | 2 | Stand Alone | Coal | SOCO | 252 | 0.06 | 28.3 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Jack Watson | 4 | Stand Alone | Coal | SOCO | 230 | 0.071 | 32.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Jack Watson | 5 | Stand Alone | Coal | SOCO | 476 | 0.071 | 32.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
James H Miller Jr | 1 | Stand Alone | Coal | SOCO | 684 | 0.063 | 33.8 |  | SCR | ESP |  | Wet Lime FGD |  |  | 2013 |  |  | Yes | Unit will have VOM adder
James H Miller Jr | 2 | Stand Alone | Coal | SOCO | 686 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
James H Miller Jr | 3 | Stand Alone | Coal | SOCO | 690 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
James H Miller Jr | 4 | Stand Alone | Coal | SOCO | 691 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
James M Barry Electric Generating Plant | 3 | Stand Alone | Coal | SOCO | 249 | 0.063 | 31.7 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
James M Barry Electric Generating Plant | 4 | Stand Alone | Coal | SOCO | 362 | 0.063 | 31.7 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
James M Barry Electric Generating Plant | 5 | Stand Alone | Coal | SOCO | 734 | 0.063 | 31.7 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Scherer | 1 | Stand Alone | Coal | SOCO | 837 | 0.036 | 31.6 |  |  | ESP & FF | ACI | Wet Lime FGD | SCR |  | 2014 | 2014 |  | Yes | Unit will have VOM adder
Scherer | 2 | Stand Alone | Coal | SOCO | 843 | 0.036 | 31.6 |  |  | ESP & FF | ACI | Wet Lime FGD | SCR |  | 2014 | 2013 |  | Yes | Unit will have VOM adder
Scherer | 3 | Stand Alone | Coal | SOCO | 875 | 0.036 | 31.6 |  |  | ESP & FF | ACI | Wet Lime FGD | SCR |  | 2014 | 2011 |  | Yes | Unit will have VOM adder
Scherer | 4 | Stand Alone | Coal | SOCO | 850 | 0.036 | 31.6 |  |  | ESP & FF | ACI | Wet Lime FGD | SCR |  | 2014 | 2014 |  | Yes | Unit will have VOM adder
Victor J Daniel Jr | 1 | Stand Alone | Coal | SOCO | 510 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Victor J Daniel Jr | 2 | Stand Alone | Coal | SOCO | 510 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Wansley (GPC) | 1 | Stand Alone | Coal | SOCO | 863 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Wansley (GPC) | 2 | Stand Alone | Coal | SOCO | 889 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Yates | 6 | Stand Alone | Coal | SOCO | 352 | 0.064 | 29.9 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Yates | 7 | Stand Alone | Coal | SOCO | 355 | 0.064 | 29.9 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Hawthorne (MO) | 5 | Stand Alone | Coal | SPP_N | 563 | 0.077 | 34.4 | Dry Lime FGD | SCR | FF | [7 empty] | No | Unit will have VOM adder
Holcomb East | 1 | Stand Alone | Coal | SPP_N | 362 | 0.064 | 29.9 | Dry Lime FGD |  | FF | [7 empty] | Yes | Unit will have VOM adder
Iatan | 1 | Stand Alone | Coal | SPP_N | 651 | 0.063 | 33.8 | Wet Lime FGD | SCR | FF | ACI | [6 empty] | No | Unit will have VOM adder
Jeffrey Energy Center | 1 | Stand Alone | Coal | SPP_N | 720 | 0.063 | 33.8 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Jeffrey Energy Center | 2 | Stand Alone | Coal | SPP_N | 730 | 0.063 | 33.8 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Jeffrey Energy Center | 3 | Stand Alone | Coal | SPP_N | 720 | 0.063 | 33.8 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
La Cygne | 1 | Stand Alone | Coal | SPP_N | 736 | 0.063 | 33.8 | Wet Lime FGD | SCR | [8 empty] | No | Unit will have VOM adder
La Cygne | 2 | Stand Alone | Coal | SPP_N | 682 | 0.063 | 33.8 | Other |  | ESP | [7 empty] | No | Unit will have VOM adder
Lawrence Energy Center (KS) | 5 | Stand Alone | Coal | SPP_N | 373 | 0.064 | 29.9 | [10 empty] | Yes | Unit will have VOM adder
Nearman Creek | ST1 | Stand Alone | Coal | SPP_N | 229 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Sibley (MO) | 3 | Stand Alone | Coal | SPP_N | 401 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Brame Energy Center | 2 | Stand Alone | Coal | SPP_S | 517 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Brame Energy Center | 3 | Stand Alone | Coal | SPP_S | 595 | 0.077 | 34.4 | Dry Lime FGD | SNCR | FF | [7 empty] | No | Unit will have VOM adder
Dolet Hills | 1 | Stand Alone | Coal | SPP_S | 672 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Flint Creek (AR) | 1 | Stand Alone | Coal | SPP_S | 528 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Grda 1 & 2 | 1 | Stand Alone | Coal | SPP_S | 490 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Grda 1 & 2 | 2 | Stand Alone | Coal | SPP_S | 520 | 0.077 | 34.4 | Dry Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Harrington | 1 | Stand Alone | Coal | SPP_S | 347 | 0.064 | 29.9 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Harrington | 2 | Stand Alone | Coal | SPP_S | 347 | 0.064 | 29.9 |  |  | FF | [7 empty] | Yes | Unit will have VOM adder
Harrington | 3 | Stand Alone | Coal | SPP_S | 347 | 0.064 | 29.9 |  |  | FF | [7 empty] | Yes | Unit will have VOM adder
Hugo (OK) | ST 1 | Stand Alone | Coal | SPP_S | 440 | 0.077 | 34.4 | [10 empty] | Yes | Unit will have VOM adder
Muskogee | 4 | Stand Alone | Coal | SPP_S | 511 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Muskogee | 5 | Stand Alone | Coal | SPP_S | 517 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Muskogee | 6 | Stand Alone | Coal | SPP_S | 502 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Northeastern | 3 | Stand Alone | Coal | SPP_S | 460 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Northeastern | 4 | Stand Alone | Coal | SPP_S | 460 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Oklaunion | 1 | Stand Alone | Coal | SPP_S | 533 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Pirkey | 1 | Stand Alone | Coal | SPP_S | 675 | 0.058 | 25.2 | Wet Lime FGD |  | ESP | [7 empty] | No | Unit will have VOM adder
Sikeston | 1 | Stand Alone | Coal | SPP_S | 233 | 0.06 | 28.3 | Wet Lime FGD |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Sooner | 1 | Stand Alone | Coal | SPP_S | 522 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Sooner | 2 | Stand Alone | Coal | SPP_S | 524 | 0.077 | 34.4 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Tolk | 1 | Stand Alone | Coal | SPP_S | 535 | 0.077 | 34.4 |  |  | FF | [7 empty] | Yes | Unit will have VOM adder
Tolk | 2 | Stand Alone | Coal | SPP_S | 545 | 0.077 | 34.4 |  |  | FF | [7 empty] | Yes | Unit will have VOM adder
Welsh Station | 1 | Stand Alone | Coal | SPP_S | 528 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Welsh Station | 2 | Stand Alone | Coal | SPP_S | 528 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Welsh Station | 3 | Stand Alone | Coal | SPP_S | 528 | 0.077 | 34.4 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Allen Steam Plant (TN) | 1 | Stand Alone | Coal | TVA | 247 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Allen Steam Plant (TN) | 2 | Stand Alone | Coal | TVA | 247 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Allen Steam Plant (TN) | 3 | Stand Alone | Coal | TVA | 247 | 0.06 | 28.3 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Bull Run (TN) | 1 | Stand Alone | Coal | TVA | 870 | 0.036 | 31.6 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Colbert | 5 | Stand Alone | Coal | TVA | 472 | 0.077 | 34.4 |  | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cumberland (TN) | 1 | Stand Alone | Coal | TVA | 1239 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cumberland (TN) | 2 | Stand Alone | Coal | TVA | 1239 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Gallatin (TN) | 1 | Stand Alone | Coal | TVA | 225 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Gallatin (TN) | 2 | Stand Alone | Coal | TVA | 225 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Gallatin (TN) | 3 | Stand Alone | Coal | TVA | 263 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Gallatin (TN) | 4 | Stand Alone | Coal | TVA | 263 | 0.06 | 28.3 |  |  | ESP | [7 empty] | No | Unit will have VOM adder
Paradise (KY) | 1 | Stand Alone | Coal | TVA | 628 | 0.051 | 32.8 | Wet Lime FGD | SCR | [8 empty] | Yes | Unit will have VOM adder
Paradise (KY) | 2 | Stand Alone | Coal | TVA | 602 | 0.051 | 32.8 | Wet Lime FGD | SCR | [8 empty] | Yes | Unit will have VOM adder
Paradise (KY) | 3 | Stand Alone | Coal | TVA | 971 | 0.051 | 32.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Red Hills Generating Facility | RHGF | Stand Alone | Coal | TVA | 440 | 0.058 | 25.2 | Other |  | FF | [7 empty] | Yes | Unit will have VOM adder
Widows Creek | 7 | Stand Alone | Coal | TVA | 473 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Widows Creek | 8 | Stand Alone | Coal | TVA | 465 | 0.077 | 34.4 | Wet Lime FGD | SCR | [8 empty] | No | Unit will have VOM adder
Belews Creek | 1 | Stand Alone | Coal | VACAR | 1135 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Belews Creek | 2 | Stand Alone | Coal | VACAR | 1135 | 0.076 | 35.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cliffside | 5 | Stand Alone | Coal | VACAR | 562 | 0.077 | 34.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Cope | ST1 | Stand Alone | Coal | VACAR | 420 | 0.077 | 34.4 | Dry Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Cross | 1 | Stand Alone | Coal | VACAR | 620 | 0.073 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Cross | 2 | Stand Alone | Coal | VACAR | 540 | 0.073 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Cross | 3 | Stand Alone | Coal | VACAR | 580 | 0.073 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Cross | 4 | Stand Alone | Coal | VACAR | 580 | 0.073 | 34.2 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
G G Allen | 3 | Stand Alone | Coal | VACAR | 265 | 0.06 | 28.3 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
G G Allen | 4 | Stand Alone | Coal | VACAR | 280 | 0.06 | 28.3 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
G G Allen | 5 | Stand Alone | Coal | VACAR | 270 | 0.06 | 28.3 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
L V Sutton | 3 | Stand Alone | Coal | VACAR | 403 | 0.077 | 34.4 |  | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Lee | 3 | Stand Alone | Coal | VACAR | 246 | 0.06 | 28.3 |  |  | ESP | [7 empty] | Yes | Unit will have VOM adder
Marshall (NC DUKE) | 1 | Stand Alone | Coal | VACAR | 385 | 0.063 | 32.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Marshall (NC DUKE) | 2 | Stand Alone | Coal | VACAR | 385 | 0.063 | 32.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Marshall (NC DUKE) | 3 | Stand Alone | Coal | VACAR | 670 | 0.063 | 32.4 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Marshall (NC DUKE) | 4 | Stand Alone | Coal | VACAR | 670 | 0.063 | 32.4 | Wet Lime FGD | SNCR | ESP | [7 empty] | No | Unit will have VOM adder
Mayo | 1 | Stand Alone | Coal | VACAR | 742 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | Yes | Unit will have VOM adder
Roxboro | 1 | Stand Alone | Coal | VACAR | 369 | 0.063 | 33.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Roxboro | 2 | Stand Alone | Coal | VACAR | 662 | 0.063 | 33.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Roxboro | 3 | Stand Alone | Coal | VACAR | 695 | 0.063 | 33.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Roxboro | 4 | Stand Alone | Coal | VACAR | 698 | 0.063 | 33.2 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Wateree | 1 | Stand Alone | Coal | VACAR | 350 | 0.064 | 29.9 | Wet Lime FGD | SCR | FF | [7 empty] | Yes | Unit will have VOM adder
Wateree | 2 | Stand Alone | Coal | VACAR | 350 | 0.064 | 29.9 | Wet Lime FGD | SCR | ESP & FF | [7 empty] | Yes | Unit will have VOM adder
Williams (SC SCGC) | WIL1 | Stand Alone | Coal | VACAR | 615 | 0.063 | 33.8 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Winyah | 1 | Stand Alone | Coal | VACAR | 295 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Winyah | 2 | Stand Alone | Coal | VACAR | 295 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Winyah | 3 | Stand Alone | Coal | VACAR | 295 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
Winyah | 4 | Stand Alone | Coal | VACAR | 270 | 0.06 | 28.3 | Wet Lime FGD | SCR | ESP | [7 empty] | No | Unit will have VOM adder
ENT Aggregated Coal |  | Aggregated | Coal | ENT | 578 | 0.069 | 26.8 | [11 empty] | Unit will have VOM adder
ENT Aggregated Coal, Scrubbed |  | Aggregated | Coal | ENT | - | 0.069 | 26.8 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
FRCC Aggregated Coal |  | Aggregated | Coal | FRCC | - | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
FRCC Aggregated Coal, Scrubbed |  | Aggregated | Coal | FRCC | 136 | 0.066 | 27.3 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
IESO Aggregated Coal |  | Aggregated | Coal | IESO | 306 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
IESO Aggregated Coal, Scrubbed |  | Aggregated | Coal | IESO | - | 0.066 | 27.3 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MAPP_CA Aggregated Coal |  | Aggregated | Coal | MAPP_CA | 635 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
MAPP_CA Aggregated Coal, Scrubbed |  | Aggregated | Coal | MAPP_CA | - | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MAPP_US Aggregated Coal |  | Aggregated | Coal | MAPP_US | 236 | 0.078 | 25.5 | [11 empty] | Unit will have VOM adder
MAPP_US Aggregated Coal, Scrubbed |  | Aggregated | Coal | MAPP_US | 52 | 0.078 | 25.5 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MISO_IN Aggregated Coal |  | Aggregated | Coal | MISO_IN | 1692 | 0.069 | 26.8 | [11 empty] | Unit will have VOM adder
MISO_IN Aggregated Coal, Scrubbed |  | Aggregated | Coal | MISO_IN | 1150 | 0.069 | 26.8 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MISO_MI Aggregated Coal |  | Aggregated | Coal | MISO_MI | 2537 | 0.069 | 26.9 | [11 empty] | Unit will have VOM adder
MISO_MI Aggregated Coal, Scrubbed |  | Aggregated | Coal | MISO_MI | 120 | 0.069 | 26.9 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MISO_MO-IL Aggregated Coal |  | Aggregated | Coal | MISO_MO-IL | 2007 | 0.069 | 26.9 | [11 empty] | Unit will have VOM adder
MISO_MO-IL Aggregated Coal, Scrubbed |  | Aggregated | Coal | MISO_MO-IL | 542 | 0.069 | 26.9 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MISO_W Aggregated Coal |  | Aggregated | Coal | MISO_W | 2910 | 0.073 | 26.2 | [11 empty] | Unit will have VOM adder
MISO_W Aggregated Coal, Scrubbed |  | Aggregated | Coal | MISO_W | 161 | 0.073 | 26.2 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
MISO_WUMS Aggregated Coal |  | Aggregated | Coal | MISO_WUMS | 1857 | 0.074 | 26.1 | [11 empty] | Unit will have VOM adder
MISO_WUMS Aggregated Coal, Scrubbed |  | Aggregated | Coal | MISO_WUMS | - | 0.074 | 26.1 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
NE Aggregated Coal |  | Aggregated | Coal | NE | 961 | 0.07 | 26.8 | [11 empty] | Unit will have VOM adder
NE Aggregated Coal, Scrubbed |  | Aggregated | Coal | NE | - | 0.07 | 26.8 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
NEISO Aggregated Coal |  | Aggregated | Coal | NEISO | 655 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
NEISO Aggregated Coal, Scrubbed |  | Aggregated | Coal | NEISO | 113 | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
NonRTO_Midwest Aggregated Coal |  | Aggregated | Coal | NonRTO_Midwest | 813 | 0.068 | 26.9 | [11 empty] | Unit will have VOM adder
NonRTO_Midwest Aggregated Coal, Scrubbed |  | Aggregated | Coal | NonRTO_Midwest | 1246 | 0.068 | 26.9 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
NYISO_A-F Aggregated Coal |  | Aggregated | Coal | NYISO_A-F | 888 | 0.069 | 26.8 | [11 empty] | Unit will have VOM adder
NYISO_A-F Aggregated Coal, Scrubbed |  | Aggregated | Coal | NYISO_A-F | 680 | 0.069 | 26.8 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
NYISO_G-I Aggregated Coal |  | Aggregated | Coal | NYISO_G-I | 136 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
NYISO_G-I Aggregated Coal, Scrubbed |  | Aggregated | Coal | NYISO_G-I | - | 0.066 | 27.3 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
PJM_E Aggregated Coal |  | Aggregated | Coal | PJM_E | 981 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
PJM_E Aggregated Coal, Scrubbed |  | Aggregated | Coal | PJM_E | 151 | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
PJM_ROM Aggregated Coal |  | Aggregated | Coal | PJM_ROM | 3829 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
PJM_ROM Aggregated Coal, Scrubbed |  | Aggregated | Coal | PJM_ROM | - | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
PJM_ROR Aggregated Coal |  | Aggregated | Coal | PJM_ROR | 9680 | 0.07 | 26.8 | [11 empty] | Unit will have VOM adder
PJM_ROR Aggregated Coal, Scrubbed |  | Aggregated | Coal | PJM_ROR | 740 | 0.07 | 26.8 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
SOCO Aggregated Coal |  | Aggregated | Coal | SOCO | 2417 | 0.068 | 27 | [11 empty] | Unit will have VOM adder
SOCO Aggregated Coal, Scrubbed |  | Aggregated | Coal | SOCO | 1118 | 0.068 | 27 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
SPP_N Aggregated Coal |  | Aggregated | Coal | SPP_N | 1716 | 0.071 | 26.6 | [11 empty] | Unit will have VOM adder
SPP_N Aggregated Coal, Scrubbed |  | Aggregated | Coal | SPP_N | - | 0.071 | 26.6 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
SPP_S Aggregated Coal |  | Aggregated | Coal | SPP_S | 558 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
SPP_S Aggregated Coal, Scrubbed |  | Aggregated | Coal | SPP_S | 178 | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
TVA Aggregated Coal |  | Aggregated | Coal | TVA | 6043 | 0.066 | 27.3 | [11 empty] | Unit will have VOM adder
TVA Aggregated Coal, Scrubbed |  | Aggregated | Coal | TVA | - | 0.066 | 27.3 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
VACAR Aggregated Coal |  | Aggregated | Coal | VACAR | 4648 | 0.07 | 26.7 | [11 empty] | Unit will have VOM adder
VACAR Aggregated Coal, Scrubbed |  | Aggregated | Coal | VACAR | 706 | 0.07 | 26.7 | Wet Lime FGD | [10 empty] | Unit will have VOM adder
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit7_ForcedNewBuilds
Appendix A, Exhibit 7 - Forced New Builds
Updated 3/17/11 from CRA
NEEM Region | Online Year | Plant Name | Unit | MW | Technology | Plant State
ENT | 2011 | Plum Point Energy ST | 1 | 720 | Coal | AR
FRCC | 2011 | WCE3-STE | 1 | 498.9 | CC | FL
FRCC | 2013 | CAPE-STE | 1 | 515 | CC | FL
FRCC | 2014 | RIV-STE | 1 | 503 | CC | FL
FRCC | 2020 | GEC ST 3 | 30 | 201 | CC | FL
FRCC | 2011 | GEC CT 1 | 30 | 150 | CT | FL
FRCC | 2011 | GEC CT 2 | 30 | 150 | CT | FL
FRCC | 2011 | WCE3-CT1 | 1 | 240 | CT | FL
FRCC | 2011 | WCE3-CT2 | 1 | 240 | CT | FL
FRCC | 2011 | WCE3-CT3 | 1 | 240 | CT | FL
FRCC | 2013 | CAPE-CT1 | 1 | 231 | CT | FL
FRCC | 2013 | CAPE-CT2 | 1 | 242 | CT | FL
FRCC | 2013 | CAPE-CT3 | 1 | 231 | CT | FL
FRCC | 2014 | RIV-CT1 | 1 | 231 | CT | FL
FRCC | 2014 | RIV-CT2 | 1 | 242 | CT | FL
FRCC | 2014 | RIV-CT3 | 1 | 231 | CT | FL
FRCC | 2015 | SWN P1&2 | 1 | 52 | CT | FL
IESO | 2011 | RESOP Biomass | 0 | 4.49 | BM | ON
IESO | 2011 | RESOP Biomass | 0 | 3.95 | BM | ON
IESO | 2011 | RESOP Biomass | 0 | 3.2 | BM | ON
IESO | 2012 | Becker (Hornepayne) | 0 | 15 | BM | ON
IESO | 2012 | RESOP Biomass | 0 | 10 | BM | ON
IESO | 2012 | RESOP Biomass | 0 | 10 | BM | ON
IESO | 2013 | FIT Clearydale Farms | 0 | 0.498 | BM | ON
IESO | 2013 | FIT DeBruin Farms Biogas | 0 | 0.36 | BM | ON
IESO | 2013 | FIT Ferme Geranik Biogas | 0 | 0.499 | BM | ON
IESO | 2013 | FIT Grimsby Bioreactor Project | 0 | 1 | BM | ON
IESO | 2013 | FIT Haliburton Forest Biopower 1 | 0 | 0.775 | BM | ON
IESO | 2013 | FIT Index Energy Mills Road Corporation | 0 | 17.812 | BM | ON
IESO | 2013 | FIT Kawartha Biogas Inc. | 0 | 9.8 | BM | ON
IESO | 2013 | FIT Powerbase / Gillette Farms Inc | 0 | 0.498 | BM | ON
IESO | 2013 | FIT Woolwich Bio-En Inc. | 0 | 2.852 | BM | ON
IESO | 2013 | RESOP Biomass | 0 | 0.6 | BM | ON
IESO | 2014 | ST MARYS | 0 | 30 | BM | ON
IESO | 2015 | Atikokan Biomass | 0 | 215 | BM | ON
IESO | 2012 | GRNFLDS_CTG116.500 | 1 | 140 | CC | ON
IESO | 2012 | GRNFLDS_STG213.800 | 1 | 140 | CC | ON
IESO | 2014 | Thunder Bay Gas Conversion 1 | 0 | 150 | CC | ON
IESO | 2015 | Thunder Bay Gas Conversion 2 | 0 | 150 | CC | ON
IESO | 2011 | Halton Hills Generating Station CC | CC | 683 | CC | ON
IESO | 2012 | YORK_EC_LV1 16.500 | 1 | 184 | CT | ON
IESO | 2012 | YORK_EC_LV2 16.500 | 1 | 184 | CT | ON
IESO | 2011 | FIT_BIG_EDDY13.800 | 1 | 5.3 | HY | ON
IESO | 2011 | FIT_WAHP_GEN13.800 | 1 | 6.5 | HY | ON
IESO | 2011 | HOUND CHUTE | 0 | 9.5 | HY | ON
IESO | 2011 | ISLAND FALLS (Yellow Falls) | 0 | 20 | HY | ON
IESO | 2011 | LOWER STURGEON | 0 | 14 | HY | ON
IESO | 2011 | RESOP Water | 0 | 1.17 | HY | ON
IESO | 2011 | WAWAITIN | 0 | 15 | HY | ON
IESO | 2012 | FIT_BOUNDARY13.800 | 1 | 3.75 | HY | ON
IESO | 2012 | FIT_HALF_MIL13.800 | 1 | 4.8 | HY | ON
IESO | 2012 | FIT_IVANHOE 13.800 | 1 | 5.1 | HY | ON
IESO | 2012 | FIT_LAPINIGA13.800 | 1 | 8.2 | HY | ON
IESO | 2012 | FIT_MIDDLETW13.800 | 1 | 5 | HY | ON
IESO | 2012 | FIT_OUTLET 13.800 | 1 | 2.5 | HY | ON
IESO | 2012 | FIT_WAPO_GEN13.800 | 1 | 6.5 | HY | ON
IESO | 2014 | FIT_NEES_GEN13.800 | 1 | 6.5 | HY | ON
IESO | 2014 | FIT_PEES_GEN13.800 | 1 | 6.5 | HY | ON
IESO | 2015 | FIT Allen and Struthers 2130769 | 0 | 2.8 | HY | ON
IESO | 2015 | FIT At Soo Crossing 2154061 | 0 | 4.3 | HY | ON
IESO | 2015 | FIT Big Beaver Falls Hydroelectric Project | 0 | 5.5 | HY | ON
IESO | 2015 | FIT Birch Creek Hydro | 0 | 1 | HY | ON
IESO | 2015 | FIT Bracebridge Falls Generating Station | 0 | 2 | HY | ON
IESO | 2015 | FIT Camp Three Rapids Hydroelectric Project | 0 | 5.5 | HY | ON
IESO | 2015 | FIT Cascade Fall 1723378 | 0 | 2.1 | HY | ON
IESO | 2015 | FIT Charlton Dam GS Expansion | 0 | 0.85 | HY | ON
IESO | 2015 | FIT Driftwood Power | 0 | 0.4 | HY | ON
IESO | 2015 | FIT Elora Hydro Electric Generating Station | 0 | 1 | HY | ON
IESO | 2015 | FIT Four Slide Falls Ltd 1713400 | 0 | 7.3 | HY | ON
IESO | 2015 | FIT High Falls Hydropower Development | 0 | 6.4 | HY | ON
IESO | 2015 | FIT Ivanhoe River, The Chute - 2124750 | 0 | 3.6 | HY | ON
IESO | 2015 | FIT Larder Lake & Raven Falls 2118966 | 0 | 1.25 | HY | ON
IESO | 2015 | FIT Latchford Dam | 0 | 0.838 | HY | ON
IESO | 2015 | FIT Latchford Dam 2 | 0 | 0.419 | HY | ON
IESO | 2015 | FIT Lizard Creek Small Hydro Project | 0 | 1.04 | HY | ON
IESO | 2015 | FIT Marter Twp, Blanche River - 2154070 | 0 | 2.1 | HY | ON
IESO | 2015 | FIT McCarthy Chute 1713399 Ltd. | 0 | 2 | HY | ON
IESO | 2015 | FIT McGraw Falls 2089284 | 0 | 2.4 | HY | ON
IESO | 2015 | FIT McPherson Fall 2154065 | 0 | 2 | HY | ON
IESO | 2015 | FIT North Bala Small Hydro Project | 0 | 5 | HY | ON
IESO | 2015 | FIT Okikendawt Hydroelectric Project | 0 | 10 | HY | ON
IESO | 2015 | FIT Old Woman Falls Hydroelectric Project | 0 | 5.5 | HY | ON
IESO | 2015 | FIT Pecors Power Small Hydro Project | 0 | 2 | HY | ON
IESO | 2015 | FIT Wabageshik Rapid at Outlet Lake 1723377 | 0 | 3.4 | HY | ON
IESO | 2015 | FIT Wanatango Falls 2124716 | 0 | 4.67 | HY | ON
IESO | 2015 | FIT Wasdell Falls Waterpower Project | 0 | 1.9 | HY | ON
IESO | 2015 | FIT Wendigo Waterpower Project | 0 | 3 | HY | ON
IESO | 2015 | FIT White Otter Falls Hydroelectric Project | 0 | 5.5 | HY | ON
IESO | 2015 | FIT Wilson Falls Generating Station | 0 | 2.3 | HY | ON
IESO | 2015 | FIT_GITCHIG113.800 | 1 | 10 | HY | ON
IESO | 2015 | FIT_GITCHIG213.800 | 1 | 8.9 | HY | ON
IESO | 2015 | FIT_NAME_G1 13.800 | 1 | 10 | HY | ON
IESO | 2015 | FIT_TROU_GEN13.800 | 1 | 4 | HY | ON
IESO | 2016 | Harmon | 0 | 78 | HY | ON
IESO | 2016 | Kipling | 0 | 78 | HY | ON
IESO | 2016 | Little Long | 0 | 67 | HY | ON
IESO | 2016 | Smoky Falls | 0 | 215 | HY | ON
IESO | 2013 | FIT Bensfort Road LFG Generation Project | 0 | 2 | LFG | ON
IESO | 2013 | FIT Lafleche Landfill Gas Utilization | 0 | 4.5 | LFG | ON
IESO | 2013 | FIT Merrick Landfill Project | 0 | 1.6 | LFG | ON
IESO | 2013 | FIT WM Ottawa Landfill Gas to Energy | 0 | 6.4 | LFG | ON
IESO | 2011 | RESOP Solar | 0 | 20 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 10 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 10 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 3.33 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 2.95 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 0.66 | PV | ON
IESO | 2011 | RESOP Solar | 0 | 0.02 | PV | ON
IESO | 2012 | FIT_LISKEAR113.800 | 1 | 10 | PV | ON
IESO | 2012 | FIT_LISKEAR313.800 | 1 | 10 | PV | ON
IESO | 2012 | FIT_NP_MART_13.800 | 1 | 10 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 130 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 70 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 59.76 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 39.12 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 20 | PV | ON
IESO | 2012 | RESOP Solar | 0 | 20 | PV | ON
IESO | 2013 | FIT 2176047 | 0 | 10 | PV | ON
IESO | 2013 | FIT 2176050 | 0 | 9 | PV | ON
IESO | 2013 | FIT Alderville 3 | 0 | 5 | PV | ON
IESO | 2013 | FIT Alfred | 0 | 10 | PV | ON
IESO | 2013 | FIT Belleville TS Demorestville | 0 | 10 | PV | ON
IESO | 2013 | FIT Black Bay Solar Project Phase 2 | 0 | 0.75 | PV | ON
IESO | 2013 | FIT Burritts Rapids | 0 | 7 | PV | ON
IESO | 2013 | FIT Consolidated Maintenance facility Solar Roof | 0 | 0.5 | PV | ON
IESO | 2013 | FIT Dave Rampel Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT EffiSolar Beckwith Solar Farm (10MW) | 0 | 10 | PV | ON
IESO | 2013 | FIT EffiSolar Brockville Solar Farm (10MW) | 0 | 10 | PV | ON
IESO | 2013 | FIT EffiSolar Cornwall Solar Farm A (10MW) | 0 | 10 | PV | ON
IESO | 2013 | FIT Glenarm | 0 | 10 | PV | ON
IESO | 2013 | FIT HPG Site A | 0 | 2 | PV | ON
IESO | 2013 | FIT Kap Solar Park | 0 | 6 | PV | ON
IESO | 2013 | FIT Kingston Gardiner Hwy2 North | 0 | 10 | PV | ON
IESO | 2013 | FIT Kingston Gardiner Hwy2 South | 0 | 10 | PV | ON
IESO | 2013 | FIT Kingston Gardiner TS Odessa | 0 | 10 | PV | ON
IESO | 2013 | FIT Kingston Gardiner TS Unity Road | 0 | 10 | PV | ON
IESO | 2013 | FIT Longueil TS Malbouef | 0 | 10 | PV | ON
IESO | 2013 | FIT Mattawishkwia Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT Mississippi Mills Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT Morley Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT Napanee TS Taylor Kidd | 0 | 10 | PV | ON
IESO | 2013 | FIT Norfolk Bloomsburg TS | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Burks Falls West | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Belleville North | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Belleville South | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Burks Falls East | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Crosby | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Glendale | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar McCann L.P. | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar North Burgess | 0 | 10 | PV | ON
IESO | 2013 | FIT Northland Power Solar Rideau Lakes | 0 | 10 | PV | ON
IESO | 2013 | FIT Penn Energy - Edwardsburgh_Morrisburg-1 | 0 | 9.333 | PV | ON
IESO | 2013 | FIT Penn Energy - Hamilton_Port Hope-4 | 0 | 10 | PV | ON
IESO | 2013 | FIT Penn Energy - S. Glengarry_St. Lawrence-1 | 0 | 9.333 | PV | ON
IESO | 2013 | FIT Ramore Solar Park | 0 | 8 | PV | ON
IESO | 2013 | FIT RE Adelaide 1c | 0 | 1 | PV | ON
IESO | 2013 | FIT RE Adelaide 1d | 0 | 0.5 | PV | ON
IESO | 2013 | FIT RE Breen 2 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Highbury 1 | 0 | 5 | PV | ON
IESO | 2013 | FIT RE Ingersoll 1 | 0 | 8 | PV | ON
IESO | 2013 | FIT RE Ingersoll 1a | 0 | 1 | PV | ON
IESO | 2013 | FIT RE Ingersoll 1b | 0 | 0.5 | PV | ON
IESO | 2013 | FIT RE Midhurst 2 | 0 | 3.5 | PV | ON
IESO | 2013 | FIT RE Midhurst 3 | 0 | 3.5 | PV | ON
IESO | 2013 | FIT RE Midhurst 4 | 0 | 6.5 | PV | ON
IESO | 2013 | FIT RE Midhurst 6 | 0 | 9 | PV | ON
IESO | 2013 | FIT RE Orillia 1 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Orillia 2 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Orillia 3 | 0 | 6.5 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 1 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 2 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 3 | 0 | 8 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 4 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 5 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Smiths Falls 6 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Waubaushene 3 | 0 | 10 | PV | ON
IESO | 2013 | FIT RE Waubaushene 4 | 0 | 8 | PV | ON
IESO | 2013 | FIT RE Waubaushene 5 | 0 | 3.5 | PV | ON
IESO | 2013 | FIT Simcoe Solar Energy Centre I | 0 | 10 | PV | ON
IESO | 2013 | FIT Simcoe Solar Energy Centre III | 0 | 10 | PV | ON
IESO | 2013 | FIT SunE Rutley | 0 | 10 | PV | ON
IESO | 2013 | FIT SUNNY SHORES SOLAR FARM | 0 | 10 | PV | ON
IESO | 2013 | FIT Val Caron | 0 | 10 | PV | ON
IESO | 2013 | FIT Vanzwolf Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT Wainwright Solar Park | 0 | 10 | PV | ON
IESO | 2013 | FIT Welland Ridge Road | 0 | 10 | PV | ON
IESO | 2013 | FIT William Rutley Solar Park | 0 | 10 | PV | ON
IESO | 2013 | RESOP Solar | 0 | 30 | PV | ON
IESO | 2015 | FIT_LISKEAR413.800 | 1 | 10 | PV | ON
IESO | 2015 | FIT_NP_ABITI13.800 | 1 | 10 | PV | ON
IESO | 2015 | FIT_NP_EMPIR13.800 | 1 | 10 | PV | ON
IESO | 2015 | FIT_NP_LONG_13.800 | 1 | 10 | PV | ON
IESO | 2011 | FIT_CONESTOG13.800 | 1 | 69 | WT | ON
IESO | 2011 | RALEIGH-WTG20.5750 | 1 | 18 | WT | ON
IESO | 2011 | RESOP Wind | 0 | 106 | WT | ON
IESO | 2011 | RESOP Wind | 0 | 48 | WT | ON
IESO | 2011 | RESOP Wind | 0 | 9 | WT | ON
IESO | 2011 | RESOP Wind | 0 | 6.5 | WT | ON
IESO | 2012 | FIT_BL_2A 13.800 | 1 | 20 | WT | ON
IESO | 2012 | FIT_BL_2B 13.800 | 1 | 20 | WT | ON
IESO | 2012 | FIT_BL_PH1 13.800 | 1 | 20 | WT | ON
IESO | 2012 | FIT_COMBER23220.00 | 1 | 82.8 | WT | ON
IESO | 2012 | FIT_COMBER24220.00 | 1 | 82.8 | WT | ON
IESO | 2012 | FIT_FARM_OWN13.800 | 1 | 100 | WT | ON
IESO | 2012 | FIT_GOUL_BAY13.800 | 1 | 25 | WT | ON
IESO | 2012 | FIT_MCLEANS113.800 | 1 | 50 | WT | ON
IESO | 2012 | FIT_MCLEANS213.800 | 1 | 10 | WT | ON
IESO | 2012 | FIT_PAR_G1 13.800 | 1 | 48.6 | WT | ON
IESO | 2012 | FIT_PRT_DOV 13.800 | 1 | 105 | WT | ON
IESO | 2012 | FIT_SUMHV_G113.800 | 1 | 125 | WT | ON
IESO | 2012 | FIT_WHE_PNE 13.800 | 1 | 60 | WT | ON
IESO | 2012 | FIT_WOLF_IS 13.800 | 1 | 300 | WT | ON
IESO | 2012 | GREENWCHWTG10.6900 | 1 | 25.3 | WT | ON
IESO | 2012 | GREENWCHWTG20.6900 | 1 | 23 | WT | ON
IESO | 2012 | RALEIGH-WTG10.5750 | 1 | 18 | WT | ON
IESO | 2012 | RESOP Wind | 0 | 20 | WT | ON
IESO | 2012 | RESOP Wind | 0 | 10 | WT | ON
IESO | 2012 | TALBOT_WTG1 0.5750 | 1 | 25.3 | WT | ON
IESO | 2012 | TALBOT_WTG2 0.5750 | 1 | 23 | WT | ON
IESO | 2012 | TALBOT_WTG3 0.5750 | 1 | 25.3 | WT | ON
IESO | 2012 | TALBOT_WTG4 0.5750 | 1 | 25.3 | WT | ON
IESO | 2013 | FIT Ballyduff Wind Farm | 0 | 11.5 | WT | ON
IESO | 2013 | FIT Belwood Wind Farm | 0 | 9.2 | WT | ON
IESO | 2013 | FIT Big Thunder Beta Windpark | 0 | 16.5 | WT | ON
IESO | 2013 | FIT Clarington Wind Farm | 0 | 10 | WT | ON
IESO | 2013 | FIT CLEAN BREEZE WIND PARK | 0 | 12.5 | WT | ON
IESO | 2013 | FIT CLEAN BREEZE WIND PARK GRAFTON | 0 | 10 | WT | ON
IESO | 2013 | FIT Conestogo Wind Energy Centre | 0 | 23 | WT | ON
IESO | 2013 | FIT Conestogo Wind Energy Centre 2 | 0 | 19.5 | WT | ON
IESO | 2013 | FIT Ernestown Wind Park | 0 | 10 | WT | ON
IESO | 2013 | FIT Fairview Wind Farm | 0 | 18.4 | WT | ON
IESO | 2013 | FIT Grand Valley Wind Farms (Phase 2) | 0 | 10.8 | WT | ON
IESO | 2013 | FIT GREY HIGHLANDS CLEAN ENERGY | 0 | 20 | WT | ON
IESO | 2013 | FIT GREY HIGHLANDS ZERO EMISSION PEOPLE | 0 | 10 | WT | ON
IESO | 2013 | FIT HAF Energy | 0 | 10 | WT | ON
IESO | 2013 | FIT Little Brit Power | 0 | 1.5 | WT | ON
IESO | 2013 | FIT Merlin Wind Farm | 0 | 10 | WT | ON
IESO | 2013 | FIT Mother Earth Renewable Energy Project - Phase I | 0 | 4 | WT | ON
IESO | 2013 | FIT Ostrander Point Wind Energy Park | 0 | 24 | WT | ON
IESO | 2013 | FIT Plateau I & II Wind | 0 | 18 | WT | ON
IESO | 2013 | FIT Plateau III Wind | 0 | 9 | WT | ON
IESO | 2013 | FIT Pukwis Community Wind Park | 0 | 20 | WT | ON
IESO | 2013 | FIT SETTLERS LANDING WIND PARK | 0 | 10 | WT | ON
IESO | 2013 | FIT skyway 125 | 0 | 10 | WT | ON
IESO | 2013 | FIT SKYWAY 126 WIND ENERGY | 0 | 10 | WT | ON
IESO | 2013 | FIT SNOWY RIDGE WIND PARK | 0 | 10 | WT | ON
IESO | 2013 | FIT South Branch Wind Farm | 0 | 30 | WT | ON
IESO | 2013 | FIT Trout Creek | 0 | 10 | WT | ON
IESO | 2013 | FIT Wainfleet Wind Farm | 0 | 10 | WT | ON
IESO | 2013 | FIT WHISPERING WOODS WIND FARM | 0 | 10 | WT | ON
IESO | 2013 | FIT Whittington Wind Farm | 0 | 6.9 | WT | ON
IESO | 2013 | FIT WIND FARM COLLIE HILL | 0 | 5.6 | WT | ON
IESO | 2013 | FIT ZEP WIND FARM GANARASKA | 0 | 20 | WT | ON
IESO | 2013 | FIT Zurich | 0 | 0.8 | WT | ON
IESO | 2013 | GREENWCHWTG30.6900 | 1 | 25.3 | WT | ON
IESO | 2013 | KRUGER-WTG1 0.6900 | 1 | 25.3 | WT | ON
IESO | 2013 | KRUGER-WTG2 0.6900 | 1 | 25.3 | WT | ON
IESO | 2013 | KRUGER-WTG3 0.6900 | 1 | 32.2 | WT | ON
IESO | 2013 | KRUGER-WTG4 0.6900 | 1 | 18.4 | WT | ON
IESO | 2013 | RALEIGH-WTG30.5750 | 1 | 21 | WT | ON
IESO | 2014 | GREENWCHWTG40.6900 | 1 | 25.3 | WT | ON
IESO | 2014 | RALEIGH-WTG40.5750 | 1 | 21 | WT | ON
MAPP_CA | 2012 | KELSEY1G | 1 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY2G | 2 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY3G | 3 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY4G | 4 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY5G | 5 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY6G | 6 | 45 | HY | Manitoba
MAPP_CA | 2012 | KELSEY7G | 7 | 45 | HY | Manitoba
MAPP_CA | 2012 | WUSK 1G | 1 | 74.3 | HY | Manitoba
MAPP_CA | 2012 | WUSK 2G | 2 | 74.3 | HY | Manitoba
MAPP_CA | 2012 | WUSK 3G | 3 | 74.3 | HY | Manitoba
MAPP_CA | 2013 | PINFLS1G | 1 | 16.7 | HY | Manitoba
MAPP_CA | 2013 | PINFLS2G | 2 | 16.7 | HY | Manitoba
MAPP_CA | 2013 | PINFLS3G | 3 | 18.4 | HY | Manitoba
MAPP_CA | 2013 | PINFLS4G | 4 | 18.4 | HY | Manitoba
MAPP_CA | 2013 | PINFLS5G | 5 | 16.5 | HY | Manitoba
MAPP_CA | 2013 | PINFLS6G | 6 | 16.8 | HY | Manitoba
MAPP_CA | 2011 | STJOS1 W | 1 | 151.2 | WT | Manitoba
MAPP_CA | 2011 | STJOS2 W | 1 | 151.2 | WT | Manitoba
MAPP_US | 2010 | Larimore | 0 | 3.5 | CT | ND
MAPP_US | 2010 | Mobile | 0 | 0.8 | CT | ND
MAPP_US | 2010 | Park River | 0 | 1 | CT | ND
MAPP_US | 2010 | Valley City | 0 | 3 | CT | ND
MAPP_US | 2010 | Minot - Prairie Winds | 1 | 115.5 | WT | ND
MAPP_US | 2010 | Valley City St. Petersberg proj | 0 | 0.9 | WT | ND
MAPP_US | 2011 | Baldwin | 1 | 102.4 | WT | ND
MAPP_US | 2012 | DEERCREE | 1 | 300 | CT | SD
MAPP_US | 2010 | WESSINGT | 1 | 51 | WT | SD
MAPP_US | 2011 | SDPRAIRW | 1 | 151.5 | WT | SD
MISO_IN | 2012 | Edwardsport | 1 | 618 | IGCC | IN
MISO_MI | 2015 | 19GRNEC 345.00 | N1 | 500 | WT | MI
MISO_MI | 2015 | 19GRNECP 345.00 | N1 | 500 | WT | MI
MISO_MI | 2015 | MI-C STA 345345.00 | N1 | 500 | WT | MI
MISO_MI | 2015 | MI-D STA 345345.00 | N1 | 500 | WT | MI
MISO_MO-IL | 2012 | 1PR STATE G126.000 | 1 | 895 | Coal | IL
MISO_MO-IL | 2012 | 1PR STATE G226.000 | 2 | 895 | Coal | IL
MISO_MO-IL | 2014 | 5ADAIR 161.00 | N1 | 300 | WT | MO
MISO_W | 2015 | LEHIGH 3 345.00 | N1 | 300 | WT | IA
MISO_W | 2015 | WEBSTER3 345.00 | N1 | 300 | WT | IA
MISO_W | Not Given | ATCHSN2W 0.6900 | W2 | 250 | WT | IA
MISO_W | Not Given | RLHILLSW 0.5750 | W1 | 250 | WT | IA
MISO_W | 2012 | MERRICT 1G 0.5750 | W | 50 | WT | MN
MISO_W | 2012 | MERRICT 2G 0.5750 | W | 50 | WT | MN
MISO_W | 2012 | MERRICT 3G 0.5750 | W | 50 | WT | MN
MISO_W | 2015 | CHANRMB7 115.00 | N1 | 500 | WT | MN
MISO_W | 2015 | LAKEFLD3 345.00 | N1 | 500 | WT | MN
MISO_W | 2006 | Oliver Co 1 | 1 | 50.6 | WT | ND
MISO_W | 2007 | Oliver Co 2 | 1 | 48 | WT | ND
MISO_W | 2004 | Edgeley/Kulm | 0 | 21 | WT | ND
MISO_W | 2010 | Rugby | 0 | 149.1 | WT | ND
MISO_W | 2011 | Bison I | 1 | 81.8 | WT | ND
MISO_W | 2015 | BRKNGCO3 345.00 | N1 | 200 | WT | SD
MISO_WUMS | 2011 | Oak Creek Power Plant ST | 2 | 512.541 | Coal | WI
MISO_WUMS | 2011 | ATC_J084POI 69.000 | N1 | 100 | WT | WI
MISO_WUMS | 2011 | GLR HL WTG1 0.6900 | W | 99 | WT | WI
MISO_WUMS | 2011 | GLR HL WTG2 0.6900 | W | 150 | WT | WI
MISO_WUMS | 2011 | J079_80 138.00 | N1 | 24 | WT | WI
MISO_WUMS | 2012 | ECOMET WTG1 12.000 | W | 49.5 | WT | WI
MISO_WUMS | 2012 | ECOMET WTG2 12.000 | W | 51 | WT | WI
MISO_WUMS | 2012 | ECOMONT WTG 12.000 | W | 50 | WT | WI
MISO_WUMS | 2012 | STONYBRK WTG0.6000 | W | 98.7 | WT | WI
MISO_WUMS | 2013 | LAKBRZ G 0.6900 | W | 98 | WT | WI
MISO_WUMS | 2013 | LDGE WD WTG 0.6900 | W | 150 | WT | WI
MISO_WUMS | 2013 | QLT B W1 0.6000 | W | 25.2 | WT | WI
MISO_WUMS | 2013 | QLT B W2 0.6000 | W | 25.2 | WT | WI
MISO_WUMS | 2013 | QLT B W3 0.6000 | W | 25.2 | WT | WI
MISO_WUMS | 2013 | QLT B W4 0.6000 | W | 23.1 | WT | WI
NE | 2011 | EGYCTR2G 22.000 | 2 | 232.1 | Coal | NE
NE | 2010 | CROFTON HILLS | 1 | 42 | WT | NE
NE | 2011 | BROKEN1X 34.500 | 1 | 80 | WT | NE
NE | 2011 | PETSBG1X 34.500 | 1 | 80 | WT | NE
NEISO | 2014 | PLAINFIELD | 1 | 43 | BM | CT
NEISO | 2014 | PLAINFIELD | 1 | 43 | BM | CT
NEISO | 2011 | KLEEN_C1 | C1 | 158 | CC | CT
NEISO | 2011 | KLEEN_C2 | C2 | 158 | CC | CT
NEISO | 2011 | KLEEN_S1 | S1 | 318 | CC | CT
NEISO | 2012 | ANSONIA GEN | C1 | 54.5 | CC | CT
NEISO | 2012 | MERIDEN GT1 | C1 | 182 | CC | CT
NEISO | 2012 | MERIDEN GT2 | C2 | 182 | CC | CT
NEISO | 2012 | MERIDEN ST | S1 | 170 | CC | CT
NEISO | 2014 | QP207-1_CT1 | C1 | 168.4 | CC | CT
NEISO | 2014 | QP207-1_CT2 | C2 | 168.4 | CC | CT
NEISO | 2014 | QP207-1_ST | S1 | 188.6 | CC | CT
NEISO | 2011 | MIDDLETWN_11 | 11 | 112 | CT | CT
NEISO | 2011 | MIDDLETWN_12 | 12 | 50 | CT | CT
NEISO | 2011 | MIDDLETWN_13 | 13 | 50 | CT | CT
NEISO | 2011 | MIDDLETWN_14 | 14 | 50 | CT | CT
NEISO | 2011 | MIDDLETWN_15 | 15 | 50 | CT | CT
NEISO | 2012 | QP273-1 | 1 | 40.3 | BM | MA
NEISO | 2013 | RUSSELL BIO | 1 | 60 | BM | MA
NEISO | 2014 | QP174-1_CT | C3 | 190.6 | CC | MA
NEISO | 2014 | QP174-1_ST | S3 | 111 | CC | MA
NEISO | 2014 | MATEP_CC | C3 | 12.5 | CT | MA
NEISO | 2011 | Northfield Mountain Unit 3 | 3 | 295 | HY | MA
NEISO | 2012 | Northfield Mountain Unit 2 | 2 | 295 | HY | MA
NEISO | 2013 | Northfield Mountain Unit 4 | 4 | 295 | HY | MA
NEISO | 2014 | Northfield Mountain Unit 1 | 1 | 295 | HY | MA
NEISO | Not Given | CAPE W CLR-1 | 1 | 126 | WT | MA
NEISO | Not Given | CAPE W CLR-2 | 2 | 108 | WT | MA
NEISO | Not Given | CAPE W CLR-3 | 3 | 126 | WT | MA
NEISO | Not Given | CAPE W CLR-4 | 4 | 108 | WT | MA
NEISO | 2010 | QP316-1_GT | 5 | 9.5 | CT | ME
NEISO | 2011 | QP197 STRNG1 | 1 | 25.3 | WT | ME
NEISO | 2011 | QP197 STRNG2 | 2 | 25.3 | WT | ME
NEISO | 2012 | QP221-1_CLR2 | 2 | 21.6 | WT | ME
NEISO | 2012 | QP251-1 | 1 | 65.9 | BM | NH
NEISO | 2011 | Comerford Unit 2 | 2 | 48.2 | HY | NH
NEISO | 2012 | Comerford Unit 3 | 3 | 48.3 | HY | NH
NEISO | 2013 | Comerford Unit 4 | 4 | 48.2 | HY | NH
NEISO | 2011 | GRANITE DIX | 7 | 21 | WT | NH
NEISO | 2011 | GRANITE FISH | 12 | 36 | WT | NH
NEISO | 2011 | GRANITE OWLS | 14 | 42 | WT | NH
NEISO | 2012 | RIDGEWOOD LD | C1 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | C2 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | C3 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | C4 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | C5 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | C6 | 6.1 | LFG | RI
NEISO | 2012 | RIDGEWOOD LD | S1 | 12.66 | LFG | RI
NEISO | 2010 | SHEFLD CLR-N | 1 | 30 | WT | VT
NEISO | 2012 | QP276-1 EAST | 1 | 14 | WT | VT
NEISO | 2012 | QP276-1 WEST | 1 | 16 | WT | VT
NYISO_A-F | 2011 | Empire Generating CC | CC | 639 | CC | NY
NYISO_A-F | 2011 | Q231SEN19-224.1600 | 1 | 6.4 | LFG | NY
NYISO_A-F | 2011 | ECOGEN_SWT1 0.6900 | W | 9.2 | WT | NY
NYISO_A-F | 2011 | ECOGEN_SWT2 0.6900 | W | 23 | WT | NY
NYISO_A-F | 2011 | ECOGEN_SWT3 0.6900 | W | 23 | WT | NY
NYISO_A-F | 2011 | ECOGEN_SWT4 0.6900 | W | 23 | WT | NY
NYISO_A-F | 2011 | FRFLD_G1 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | FRFLD_G2 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | FRFLD_G3 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2011 | HOWD_C93_G1 0.6900 | W | 7.5 | WT | NY
NYISO_A-F | 2011 | HOWD_C93_G2 0.6900 | W | 27.5 | WT | NY
NYISO_A-F | 2011 | HOWD_C93_G3 0.6900 | W | 27.5 | WT | NY
NYISO_A-F | 2011 | Q180A_CLIB_G0.6900 | W | 10 | WT | NY
NYISO_A-F | 2011 | Q234_CLIB_G10.6900 | W | 7.5 | WT | NY
NYISO_A-F | 2011 | Q234_CLIB_G20.6900 | W | 7.5 | WT | NY
NYISO_A-F | 2011 | Q263STONY_1G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q263STONY_2G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q263STONY_3G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q263STONY_4G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q263STONY_5G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q263STONY_6G0.6900 | W | 22.5 | WT | NY
NYISO_A-F | 2011 | Q271STLINE1G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q271STLINE2G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q271STLINE3G0.6900 | W | 24 | WT | NY
NYISO_A-F | 2011 | Q271STLINE4G0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2011 | Q271STLINE5G0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2012 | BALLHL1G 0.5750 | W | 12 | WT | NY
NYISO_A-F | 2012 | BALLHL2G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | BALLHL3G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | BALLHL4G 0.5750 | W | 12 | WT | NY
NYISO_A-F | 2012 | BALLHL5G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | BALLHL6G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | BALLHL7G 0.5750 | W | 12 | WT | NY
NYISO_A-F | 2012 | BALLHL8G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | BALLHL9G 0.5750 | W | 10.5 | WT | NY
NYISO_A-F | 2012 | JRCHO_1G 0.6900 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | JRCHO_2G 0.6900 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | JRCHO_3G 0.6900 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | JRCHO_4G 0.6900 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | JRDN_G87_G1 0.6900 | W | 8 | WT | NY
NYISO_A-F | 2012 | JRDN_G87_G2 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | JRDN_G87_G3 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | JRDN_G87_G4 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | MORESVL_1G 1.0000 | W | 21 | WT | NY
NYISO_A-F | 2012 | MORESVL_2G 1.0000 | W | 21 | WT | NY
NYISO_A-F | 2012 | MORESVL_5G 1.0000 | W | 21 | WT | NY
NYISO_A-F | 2012 | MRBLRV1G_S880.6000 | W | 25.2 | WT | NY
NYISO_A-F | 2012 | MRBLRV2G_S880.6000 | W | 21 | WT | NY
NYISO_A-F | 2012 | MRBLRV3G_S880.6000 | W | 44.1 | WT | NY
NYISO_A-F | 2012 | MRBLRV4G_S880.6000 | W | 44.1 | WT | NY
NYISO_A-F | 2012 | MRBLRV5G_S880.6000 | W | 42 | WT | NY
NYISO_A-F | 2012 | MRBLRV6G_S880.6000 | W | 39.9 | WT | NY
NYISO_A-F | 2012 | Q168_PRY_1G 0.6900 | W | 28 | WT | NY
NYISO_A-F | 2012 | Q168_PRY_2G 0.6900 | W | 28 | WT | NY
NYISO_A-F | 2012 | Q168_PRY_3G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q168_PRY_4G 0.6900 | W | 28 | WT | NY
NYISO_A-F | 2012 | Q168_PRY_5G 0.6900 | W | 28 | WT | NY
NYISO_A-F | 2012 | Q169_V90_1G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q169_V90_2G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q169_V90_3G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q169_V90_4G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q197_G87_1G 0.6900 | W | 20 | WT | NY
NYISO_A-F | 2012 | Q197_G87_2G 0.6900 | W | 20 | WT | NY
NYISO_A-F | 2012 | Q197_G87_3G 0.6900 | W | 20 | WT | NY
NYISO_A-F | 2012 | Q197_G87_4G 0.6900 | W | 18 | WT | NY
NYISO_A-F | 2012 | Q198_V90_1G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q198_V90_2G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q198_V90_3G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q198_V90_4G 1.0000 | W | 19.8 | WT | NY
NYISO_A-F | 2012 | Q237ALGANY1G0.6600 | W | 17.5 | WT | NY
NYISO_A-F | 2012 | Q237ALGANY2G0.6600 | W | 30 | WT | NY
NYISO_A-F | 2012 | Q237ALGANY3G0.6600 | W | 30 | WT | NY
NYISO_A-F | 2012 | Q241CHTWND_G0.5750 | W | 19.5 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_1G 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_2G 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_3G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_4G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_5G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_6G 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_7G 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_8G 0.6900 | W | 26 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH_9G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q246DUTCH10G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q254RIPW_1G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q254RIPW_2G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q254RIPW_3G 0.6900 | W | 24 | WT | NY
NYISO_A-F | 2012 | Q254RIPW_4G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2012 | Q254RIPW_5G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2013 | Q207_GE_01G 0.6900 | 1 | 24 | WT | NY
NYISO_A-F | 2013 | Q207_GE_02G 0.6900 | 1 | 24 | WT | NY
NYISO_A-F | 2013 | Q207_GE_03G 0.6900 | 1 | 24 | WT | NY
NYISO_A-F | 2013 | Q207_GE_04G 0.6900 | 1 | 22.5 | WT | NY
NYISO_A-F | 2013 | Q207_GE_05G 0.6900 | 1 | 12 | WT | NY
NYISO_A-F | 2013 | Q207_GE_06G 0.6900 | 1 | 22.5 | WT | NY
NYISO_A-F | 2013 | Q207_GE_07G 0.6900 | 1 | 12 | WT | NY
NYISO_A-F | 2013 | Q207_GE_08G 0.6900 | 1 | 24 | WT | NY
NYISO_A-F | 2013 | Q207_GE_09G 0.6900 | 1 | 9 | WT | NY
NYISO_A-F | 2013 | Q207_GE_10G 0.6900 | 1 | 24 | WT | NY
NYISO_A-F | 2013 | Q207_GE_11G 0.6900 | 1 | 12 | WT | NY
NYISO_A-F | 2013 | STLAW_AW_G1 12.000 | W | 12 | WT | NY
NYISO_A-F | 2013 | STLAW_AW_G2 12.000 | W | 39 | WT | NY
NYISO_A-F | 2013 | STLAW_AW_G3 12.000 | W | 39 | WT | NY
NYISO_A-F | 2013 | STLAW_AW_G4 12.000 | W | 39 | WT | NY
NYISO_A-F | 2013 | WHILL_AW_1 12.000 | W | 12 | WT | NY
NYISO_A-F | 2013 | WHILL_AW_2 12.000 | W | 12 | WT | NY
NYISO_A-F | 2013 | WHILL_AW_3 12.000 | W | 13.5 | WT | NY
NYISO_A-F | 2013 | WHORSE G 0.5750 | 1 | 19.5 | WT | NY
NYISO_A-F | 2014 | MUNSVIL_GE1 0.5750 | W | 6 | WT | NY
NYISO_A-F | 2014 | MUNSVIL_GE2 0.5750 | W | 16.5 | WT | NY
NYISO_A-F | 2014 | MUNSVIL_GE3 0.5750 | W | 18 | WT | NY
NYISO_A-F | 2014 | Q157_ORIN_1G0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2014 | Q157_ORIN_2G0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2014 | Q157_ORIN_3G0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2014 | Q157_ORIN_4G0.5750 | W | 24 | WT | NY
NYISO_A-F | 2015 | HRTVL_1G 0.6900 | W | 18.4 | WT | NY
NYISO_A-F | 2015 | HRTVL_2G 0.6900 | W | 13.8 | WT | NY
NYISO_A-F | 2015 | HRTVL_3G 0.6900 | W | 18.4 | WT | NY
NYISO_A-F | 2016 | CNSTO_1G 0.5750 | W | 24 | WT | NY
NYISO_A-F | 2016 | CNSTO_2G 0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2016 | CNSTO_3G 0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2016 | CNSTO_4G 0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2016 | CNSTO_5G 0.5750 | W | 25.5 | WT | NY
NYISO_A-F | 2016 | CNSTO_6G 0.5750 | W | 24 | WT | NY
NYISO_A-F | 2016 | HOUNS10G 0.6900 | W | 28.8 | WT | NY
NYISO_A-F | 2016 | HOUNSF1G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF2G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF3G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF4G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF5G 0.6900 | W | 28.8 | WT | NY
NYISO_A-F | 2016 | HOUNSF6G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF7G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF8G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | HOUNSF9G 0.6900 | W | 26.4 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_1G12.000 | W | 18 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_2G12.000 | W | 18 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_3G12.000 | W | 18 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_4G12.000 | W | 18 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_5G12.000 | W | 18 | WT | NY
NYISO_A-F | 2016 | Q239WDOOR_6G12.000 | W | 9 | WT | NY
NYISO_J-K | 2011 | BAY_G1&2 13.800 | 1 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G1&2 13.800 | 2 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G3&4 13.800 | 3 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G3&4 13.800 | 4 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G5&6 13.800 | 5 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G5&6 13.800 | 6 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G7&8 13.800 | 7 | 64 | CC | NY
NYISO_J-K | 2011 | BAY_G7&8 13.800 | 8 | 64 | CC | NY
NYISO_J-K | 2011 | Q308_GT1 18.000 | 1 | 193.1 | CC | NY
NYISO_J-K | 2011 | Q308_GT2 18.000 | 1 | 193.1 | CC | NY
NYISO_J-K | 2011 | Q308_ST 18.000 | 1 | 277.2 | CC | NY
NYISO_J-K | 2012 | Q330 G 13.800 | 1 | 32 | PV | NY
PJM_E | 2010 | O23 | 1 | 300 | CC | DE
PJM_E | 2010 | T52 | 1 | 20 | CC | DE
PJM_E | 2010 | T53 | 1 | 7.3 | CT | DE
PJM_E | 2010 | T56 | 1 | 8.4 | CT | DE
PJM_E | 2010 | T67 | 1 | 5.3 | CT | DE
PJM_E | 2010 | T68 | 1 | 5.2 | CT | DE
PJM_E | 2015 | R36 | 1 | 450 | WT | DE
PJM_E | 2014 | Q41 | 1 | 30 | BM | NJ
PJM_E | 2010 | S60 | 1 | 63 | CC | NJ
PJM_E | 2010 | S61 | 1 | 20 | CC | NJ
PJM_E | 2010 | T77 | 1 | 64 | CC | NJ
PJM_E | 2010 | T54 | 1 | 6.6 | CC | NJ
PJM_E | 2010 | T54 | 1 | 6.6 | CC | NJ
PJM_E | 2010 | T55 | 1 | 15.3 | CC | NJ
PJM_E | 2010 | T55 | 1 | 12.4 | CC | NJ
PJM_E | 2010 | T59 | 1 | 12.9 | CC | NJ
PJM_E | 2010 | T59 | 1 | 12.9 | CC | NJ
PJM_E | 2010 | T76 | 1 | 27.3 | CC | NJ
PJM_E | 2010 | T76 | 1 | 27.3 | CC | NJ
PJM_E | 2011 | S107 | 1 | 580 | CC | NJ
PJM_E | 2011 | T45 | 1 | 205 | CC | NJ
PJM_E | 2012 | Q11 | 1 | 100 | CC | NJ
PJM_E | 2012 | Q90 | 1 | 650 | CC | NJ
PJM_E | 2012 | S121 | 1 | 63 | CC | NJ
PJM_E | 2012 | T107 | 1 | 624.5 | CC | NJ
PJM_E | 2012 | T41 | 1 | 178 | CC | NJ
PJM_E | 2012 | T41 | 1 | 44.5 | CC | NJ
PJM_E | 2012 | T42 | 1 | 88 | CC | NJ
PJM_E | 2012 | T43 | 1 | 178 | CC | NJ
PJM_E | 2013 | R11 | 1 | 440 | CC | NJ
PJM_E | 2010 | T135 | 1 | 15 | Coal | NJ
PJM_E | 2011 | U1-066 | 1 | 12 | HY | NJ
PJM_E | 2010 | O20 | 1 | 9.1 | LFG | NJ
PJM_E | 2011 | U3-032 | 1 | 20 | PV | NJ
PJM_E | 2011 | U4-036 | 1 | 5.45 | PV | NJ
PJM_E | 2013 | T84 | 1 | 350 | WT | NJ
PJM_E | 2014 | U1-056 | 1 | 350 | WT | NJ
PJM_E | 2010 | U1-090 | 1 | 12 | Coal | OH
PJM_E | 2010 | T118 | 1 | 10 | CC | PA
PJM_E | 2010 | T129 | 1 | 20 | CC | PA
PJM_E | 2012 | P04 | 1 | 555 | CC | PA
PJM_E | 2012 | U1-010 | 1 | 10 | CC | PA
PJM_E | 2013 | U2-074 | 1 | 300 | CC | PA
PJM_ROM | 2011 | S17 | 1 | 112.5 | CC | MD
PJM_ROM | 2011 | T133 | 1 | 225 | CC | MD
PJM_ROM | 2012 | T134 | 1 | 325 | CC | MD
PJM_ROM | 2013 | R17 | 1 | 275 | CC | MD
PJM_ROM | 2011 | S64 | 1 | 18 | BM | PA
PJM_ROM | 2011 | S103 | 1 | 57 | CC | PA
PJM_ROM | 2011 | U4-040 | 1 | 2 | CC | PA
PJM_ROM | 2012 | T117 | 1 | 126 | CC | PA
PJM_ROM | 2011 | Delta Power Plant CC | CC1 | 556 | CC | PA
PJM_ROM | 2010 | Q46 | 1 | 10 | Coal | PA
PJM_ROM | 2010 | T109 | 1 | 20 | Coal | PA
PJM_ROM | 2010 | U2-067 | 1 | 2.5 | Coal | PA
PJM_ROM | 2011 | U4-041 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-042 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-043 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-044 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-045 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-046 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-047 | 1 | 2 | CT | PA
PJM_ROM | 2011 | U4-048 | 1 | 2 | CT | PA
PJM_ROM | 2010 | Q63 | 1 | 16 | HY | PA
PJM_ROM | 2014 | Q20 | 1 | 140 | HY | PA
PJM_ROM | 2010 | T85 | 1 | 6 | LFG | PA
PJM_ROM | 2010 | T86 | 1 | 1.5 | LFG | PA
PJM_ROM | 2011 | S29B | 1 | 5.7 | LFG | PA
PJM_ROM | 2011 | S29B | 1 | 5.7 | LFG | PA
PJM_ROM | 2010 | O48, R40 | 1 | 37.8 | WT | PA
PJM_ROM | 2010 | R32 | 1 | 75 | WT | PA
PJM_ROM | 2011 | K02 | 1 | 70 | WT | PA
PJM_ROM | 2011 | Q34 | 1 | 100 | WT | PA
PJM_ROM | 2011 | Q36 | 1 | 50 | WT | PA
PJM_ROM | 2011 | Q53 | 1 | 38 | WT | PA
PJM_ROM | 2012 | O19 | 1 | 33 | WT | PA
PJM_ROM | 2012 | R43 | 1 | 20 | WT | PA
PJM_ROM | 2014 | U2-069 | 1 | 56 | WT | PA
PJM_ROR | 2012 | R35 | 1 | 50 | BM | IL
PJM_ROR | 2010 | O43 | 1 | 42 | CC | IL
PJM_ROR | 2010 | U1-054 | 1 | 46 | CC | IL
PJM_ROR | 2010 | U4-030 | 1 | 6 | CC | IL
PJM_ROR | 2010 | R18 | 1 | 6.4 | LFG | IL
PJM_ROR | 2010 | L12_CE23 | 1 | 4 | WT | IL
PJM_ROR | 2010 | N21 | 1 | 6 | WT | IL
PJM_ROR | 2010 | N22 | 1 | 11 | WT | IL
PJM_ROR | 2010 | N23 | 1 | 11 | WT | IL
PJM_ROR | 2010 | N24 | 1 | 11 | WT | IL
PJM_ROR | 2010 | N25 | 1 | 11 | WT | IL
PJM_ROR | 2010 | O33 | 1 | 20 | WT | IL
PJM_ROR | 2010 | O09 | 1 | 212 | WT | IL
PJM_ROR | 2010 | O24 | 1 | 100.8 | WT | IL
PJM_ROR | 2010 | O29 | 1 | 225 | WT | IL
PJM_ROR | 2010 | P11 | 1 | 100 | WT | IL
PJM_ROR | 2010 | P14 | 1 | 80 | WT | IL
PJM_ROR | 2010 | P20 | 1 | 210 | WT | IL
PJM_ROR | 2010 | P24 | 1 | 20 | WT | IL
PJM_ROR | 2010 | P25 | 1 | 20 | WT | IL
PJM_ROR | 2010 | P26 | 1 | 20 | WT | IL
PJM_ROR | 2010 | P37 | 1 | 212 | WT | IL
PJM_ROR | 2010 | P39 | 1 | 60 | WT | IL
PJM_ROR | 2010 | Q39 | 1 | 147 | WT | IL
PJM_ROR | 2010 | LEEDK;1U | 1 | 240 | WT | IL
PJM_ROR | 2010 | O27 | 1 | 300 | WT | IL
PJM_ROR | 2010 | P10 | 1 | 340.5 | WT | IL
PJM_ROR | 2010 | P36 | 1 | 240 | WT | IL
PJM_ROR | 2011 | O73 | 1 | 100 | WT | IL
PJM_ROR | 2011 | P40 | 1 | 20 | WT | IL
PJM_ROR | 2012 | FREEPT_G | 1 | 80 | WT | IL
PJM_ROR | 2012 | K02_CE18 | 1 | 80 | WT | IL
PJM_ROR | 2012 | O49 | 1 | 200 | WT | IL
PJM_ROR | 2012 | O68 | 1 | 100 | WT | IL
PJM_ROR | 2010 | R97 | 1 | 20 | Coal | IN
PJM_ROR | 2010 | R03 | 1 | 130 | WT | IN
PJM_ROR | 2011 | S72 | 1 | 300 | WT | IN
PJM_ROR | 2011 | S73 | 1 | 200 | WT | IN
PJM_ROR | 2012 | R60 | 1 | 350 | WT | IN
PJM_ROR | 2013 | Q03 | 1 | 250 | WT | IN
PJM_ROR | 2013 | S71 | 1 | 120 | WT | IN
PJM_ROR | 2010 | S38 | 1 | 8 | Coal | MD
PJM_ROR | 2010 | S14 | 1 | 70 | WT | MD
PJM_ROR | 2011 | K28 | 1 | 100 | WT | MD
PJM_ROR | 2011 | U2-030 | 1 | 60 | WT | MD
PJM_ROR | 2011 | U2-061 | 1 | 50 | WT | MD
PJM_ROR | 2010 | T111 | 1 | 8 | LFG | MI
PJM_ROR | 2011 | P43 | 1 | 63 | BM | NC
PJM_ROR | 2012 | U1-031 | 1 | 80 | BM | NC
PJM_ROR | 2011 | U1-66 | 1 | 9 | CT | NJ
PJM_ROR | 2010 | L01_AEP137 | 1 | 165 | BM | OH
PJM_ROR | 2010 | P30 | 1 | 20 | BM | OH
PJM_ROR | 2015 | S101 | 1 | 580 | CC | OH
PJM_ROR | 2010 | S35 | 1 | 20 | Coal | OH
PJM_ROR | 2010 | T164 | 1 | 15 | Coal | OH
PJM_ROR | 2010 | T165 | 1 | 20 | Coal | OH
PJM_ROR | 2010 | T166 | 1 | 20 | Coal | OH
PJM_ROR | 2010 | N42 | 1 | 600 | Coal | OH
PJM_ROR | 2010 | U4-034 | 1 | 5 | Coal | OH
PJM_ROR | 2010 | U4-035 | 1 | 5 | Coal | OH
PJM_ROR | 2010 | T154 | 1 | 10 | LFG | OH
PJM_ROR | 2010 | R52 | 1 | 200 | WT | OH
PJM_ROR | 2010 | R52a | 1 | 100 | WT | OH
PJM_ROR | 2010 | S45 | 1 | 100 | WT | OH
PJM_ROR | 2011 | T130 | 1 | 300 | WT | OH
PJM_ROR | 2011 | T131 | 1 | 150 | WT | OH
PJM_ROR | 2011 | T142 | 1 | 300 | WT | OH
PJM_ROR | 2011 | U1-059 | 1 | 50 | WT | OH
PJM_ROR | 2012 | R49 | 1 | 150 | WT | OH
PJM_ROR | 2012 | U2-041 | 1 | 300 | WT | OH
PJM_ROR | 2013 | 02DAV-BE 345.00 | 1 | 375 | WT | OH
PJM_ROR | 2014 | R48 | 1 | 48.3 | WT | OH
PJM_ROR | 2014 | T48 | 1 | 50 | WT | OH
PJM_ROR | 2010 | P34 | 1 | 7 | BM | PA
PJM_ROR | 2011 | T174 | 1 | 930 | CC | PA
PJM_ROR | 2011 | T156 | 1 | 20 | Coal | PA
PJM_ROR | 2010 | T155 | 1 | 6 | HY | PA
PJM_ROR | 2011 | N32 | 1 | 10.1 | WT | PA
PJM_ROR | 2011 | T39 | 1 | 18 | WT | PA
PJM_ROR | 2013 | Q25 | 1 | 80 | WT | PA
PJM_ROR | 2010 | S82 | 1 | 20 | CC | VA
PJM_ROR | 2010 | S83 | 1 | 20 | CC | VA
PJM_ROR | 2010 | S84 | 1 | 20 | CC | VA
PJM_ROR | 2010 | S85 | 1 | 20 | CC | VA
PJM_ROR | 2011 | P38 | 1 | 625 | CC | VA
PJM_ROR | 2011 | R31 | 1 | 18 | CC | VA
PJM_ROR | 2012 | T180 | 1 | 650 | CC | VA
PJM_ROR | 2013 | R80 | 1 | 60 | CC | VA
PJM_ROR | 2013 | S97 | 1 | 20 | CC | VA
PJM_ROR | 2013 | S98 | 1 | 20 | CC | VA
PJM_ROR | 2016 | T167 | 1 | 120 | CC | VA
PJM_ROR | 2011 | R63 | 1 | 19 | Coal | VA
PJM_ROR | 2011 | S79 | 1 | 27 | Coal | VA
PJM_ROR | 2011 | S80 | 1 | 20 | Coal | VA
PJM_ROR | 2012 | Q43 | 1 | 534 | Coal | VA
PJM_ROR | 2012 | Q43 | 1 | 534 | Coal | VA
PJM_ROR | 2012 | S100 | 1 | 80 | Coal | VA
PJM_ROR | 2014 | T06 | 1 | 20 | CT | VA
PJM_ROR | 2010 | P09 | 1 | 91 | HY | VA
PJM_ROR | 2010 | T10 | 1 | 3 | LFG | VA
PJM_ROR | 2011 | U2-031 | 1 | 30 | LFG | VA
PJM_ROR | 2010 | N07 | 1 | 38 | WT | VA
PJM_ROR | 2011 | U2-050 | 1 | 100 | WT | VA
PJM_ROR | 2011 | U2-051 | 1 | 60 | WT | VA
PJM_ROR | 2012 | U2-068 | 1 | 130 | WT | VA
PJM_ROR | 2014 | U4-026 | 1 | 100 | WT | VA
PJM_ROR | 2010 | O32 | 1 | 20 | Coal | WV
PJM_ROR | 2010 | O32 | 1 | 20 | Coal | WV
PJM_ROR | 2011 | Q79 | 1 | 100 | Coal | WV
PJM_ROR | 2011 | S74 | 1 | 25 | Coal | WV
PJM_ROR | 2012 | S75 | 1 | 27 | Coal | WV
PJM_ROR | 2013 | S76 | 1 | 25 | Coal | WV
PJM_ROR | 2011 | R76 | 1 | 100 | HY | WV
PJM_ROR | 2013 | S70 | 1 | 36.4 | HY | WV
PJM_ROR | 2010 | Q55 | 1 | 100 | WT | WV
PJM_ROR | 2011 | T157 | 1 | 160 | WT | WV
PJM_ROR | 2012 | J07 | 1 | 124 | WT | WV
PJM_ROR | 2012 | K26 | 1 | 31 | WT | WV
PJM_ROR | 2012 | M23 | 1 | 150 | WT | WV
PJM_ROR | 2012 | N47 | 1 | 85 | WT | WV
PJM_ROR | 2012 | P59 | 1 | 125 | WT | WV
PJM_ROR | 2013 | P52 | 1 | 80 | WT | WV
SOCO | 2019 | MCNTSH6G | 0 | 187 | CC | AL
SOCO | 2012 | 1FITZ BIO 13.800 | 1 | 55 | BM | GA
SOCO | 2011 | 1LIVEOAKS 1A18.000 | 1A | 171 | CC | GA
SOCO | 2011 | 1LIVEOAKS 1B18.000 | 1B | 171 | CC | GA
SOCO | 2011 | 1LIVEOAKS1ST18.000 | 1 | 250 | CC | GA
SOCO | 2011 | 1MCDON 4A 21.000 | 4A | 240 | CC | GA
SOCO | 2011 | 1MCDON 4B 21.000 | 4B | 240 | CC | GA
SOCO | 2011 | 1MCDON 4ST 18.000 | 4 | 379.7 | CC | GA
SOCO | 2011 | 1MCDON 5A 21.000 | 5A | 240 | CC | GA
SOCO | 2011 | 1MCDON 5B 21.000 | 5B | 240 | CC | GA
SOCO | 2011 | 1MCDON 5ST 18.000 | 5 | 373.1 | CC | GA
SOCO | 2011 | 1MCDON 6A 21.000 | 6A | 240 | CC | GA
SOCO | 2011 | 1MCDON 6B 21.000 | 6B | 240 | CC | GA
SOCO | 2011 | 1MCDON 6ST 18.000 | 6 | 375.1 | CC | GA
SOCO | 2011 | 1CONASAUGA 1A 18.000 | 1A | 176 | CC | GA
SOCO | 2011 | 1CONASAUGA 1B 18.000 | 1B | 176 | CC | GA
SOCO | 2011 | 1CONASAUGA 1ST 18.000 | 1 | 268 | CC | GA
SOCO | 2012 | 1LOOPERS 2A 18.000 | 2A | 176 | CC | GA
SOCO | 2012 | 1LOOPERS 2B 18.000 | 2B | 176 | CC | GA
SOCO | 2012 | 1LOOPERS 2ST 18.000 | 2 | 295 | CC | GA
SOCO | 2016 | 1VOGTLE3 26.000 | 3 | 1100 | NU | GA
SOCO | 2017 | 1VOGTLE4 26.000 | 4 | 1100 | NU | GA
SOCO | 2015 | 1KEMP CC1 1 18.000 | 1 | 268 | CC | MS
SOCO | 2015 | 1KEMP CC1 1A18.000 | 1A | 166 | CC | MS
SOCO | 2015 | 1KEMP CC1 1B18.000 | 1B | 166 | CC | MS
SPP_N | 2011 | Iatan ST | 2 | 465.035 | Coal | MO
SPP_S | 2012 | TURKCOAL 24.000 | 1 | 713 | Coal | AR
SPP_S | 2011 | SOUTHWEST 2 | 2 | 275 | Coal | MO
SPP_S | 2017 | MORLND4 18.000 | 1 | 300 | CT | OK
SPP_S | 2011 | KEENAN 1 34.500 | 1 | 150 | WT | OK
SPP_S | 2011 | TLGAWND1 34.500 | 1 | 130 | WT | OK
SPP_S | 2012 | OGEWND11 34.500 | 1 | 150 | WT | OK
SPP_S | 2016 | OGEWND21 34.500 | 1 | 150 | WT | OK
SPP_S | 2011 | ANTELOPE_A 113.800 | A1 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_A 113.800 | A2 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_A 113.800 | A3 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_A 113.800 | A4 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_A 113.800 | A5 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_A 113.800 | A6 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B1 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B2 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B3 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B4 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B5 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_B 113.800 | B6 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C1 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C2 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C3 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C4 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C5 | 9.444 | CT | TX
SPP_S | 2011 | ANTELOPE_C 113.800 | C6 | 9.444 | CT | TX
SPP_S | 2012 | JONES 3 | 1 | 243 | CT | TX
TVA | 2011 | Lagoon Creek CC Steam Turbine | 1 | 220 | CC | TN
TVA | 2010 | Lagoon Creek CC Turbine 1 | 1 | 160 | CC | TN
TVA | 2010 | Lagoon Creek CC Turbine 2 | 1 | 160 | CC | TN
TVA | 2012 | John Sevier CC Steam Turbine | 4 | 383 | CC | TN
TVA | 2012 | John Sevier CC Turbine 1 | 1 | 165 | CC | TN
TVA | 2012 | John Sevier CC Turbine 2 | 2 | 165 | CC | TN
TVA | 2012 | John Sevier CC Turbine 3 | 3 | 165 | CC | TN
TVA | 2013 | Watts Bar Nuclear 2 | 2 | 1203.89 | NU | TN
VACAR | 2011 | 1RICHCC2 | A | 643 | CC | NC
VACAR | 2011 | BUCKG1 18.000 | 1 | 179 | CC | NC
VACAR | 2011 | BUCKG2 18.000 | 2 | 179 | CC | NC
VACAR | 2011 | BUCKS1 18.000 | 3 | 263 | CC | NC
VACAR | 2012 | DNRVRG1 18.000 | 1 | 179 | CC | NC
VACAR | 2012 | DNRVRG2 18.000 | 2 | 179 | CC | NC
VACAR | 2012 | DNRVRS1 18.000 | 3 | 263 | CC | NC
VACAR | 2012 | CLFSDGEN 27.000 | 6 | 825 | Coal | SC
VACAR | 2012 | CLEVELAND1 18.000 | 1 | 179.3 | CT | SC
VACAR | 2012 | CLEVELAND2 18.000 | 2 | 179.3 | CT | SC
VACAR | 2012 | CLEVELAND3 18.000 | 3 | 179.3 | CT | SC
VACAR | 2012 | CLEVELAND4 18.000 | 4 | 179.3 | CT | SC
VACAR | 2016 | VC Summer #2 | 2 | 1165 | NU | SC
VACAR | 2019 | VC Summer #3 | 3 | 1165 | NU | SC
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit8_ForcedRetirements
Appendix A, Exhibit 8 - Forced Retirements
Updated 3/17/11 from CRA
Plant Name | Unit | MW | Technology | Retirement Year | Plant State | NEEM Region | NEEM MW
Cape Canaveral | 1 | 402 | STOG | 2011 | Florida | FRCC | 402
Cape Canaveral | 2 | 402 | STOG | 2011 | Florida | FRCC | 402
Crystal River | 1 | 440.5 | Coal | 2020 | Florida | FRCC | 375
Crystal River | 2 | 523.8 | Coal | 2020 | Florida | FRCC | 494
Atikokan GS | 1 | 211 | Coal | 2013 | Ontario | IESO | 211
Lambton GS | 1 | 520 | Coal | 2010 | Ontario | IESO | 485
Lambton GS | 2 | 520 | Coal | 2010 | Ontario | IESO | 485
Lambton GS | 3 | 489 | Coal | 2014 | Ontario | IESO | 489
Lambton GS | 4 | 502 | Coal | 2014 | Ontario | IESO | 502
Nanticoke | 3 | 510 | Coal | 2010 | Ontario | IESO | 490
Nanticoke | 4 | 505 | Coal | 2010 | Ontario | IESO | 490
Nanticoke | 1 | 490 | Coal | 2011 | Ontario | IESO | 490
Nanticoke | 2 | 490 | Coal | 2011 | Ontario | IESO | 490
Nanticoke | 5 | 490 | Coal | 2014 | Ontario | IESO | 490
Nanticoke | 6 | 490 | Coal | 2014 | Ontario | IESO | 490
Nanticoke | 7 | 508 | Coal | 2014 | Ontario | IESO | 508
Nanticoke | 8 | 490 | Coal | 2014 | Ontario | IESO | 490
Thunder Bay | 2 | 150 | Coal | 2014 | Ontario | IESO | 150
Thunder Bay | 3 | 150 | Coal | 2014 | Ontario | IESO | 150
Webeque First Nation | GEN1 | 0.65 | PeakO | 2012 | Ontario | IESO | 0.65
Brandon #5 | 5 | 105.9 | Coal | 2018 | Manitoba | MAPP_CA | 105.9
Edwardsport | 7 | 40.2 | Coal | 2011 | Indiana | MISO_IN | 40.2
Edwardsport | 8 | 69 | Coal | 2011 | Indiana | MISO_IN | 69
Blount Street | 3 | 34.5 | STOG | 2013 | Wisconsin | MISO_WUMS | 34.5
Blount Street | 4 | 20 | STOG | 2013 | Wisconsin | MISO_WUMS | 20
Blount Street | 5 | 23 | Coal | 2013 | Wisconsin | MISO_WUMS | 23
Rothschild (WI) | TG2 | 5 | STOG | 2014 | Wisconsin | MISO_WUMS | 5
Empire | OE11 | 1.2 | GEO | 2012 | Nevada | NWPP | 1.2
Empire | OE12 | 1.2 | GEO | 2012 | Nevada | NWPP | 1.2
Empire | OE13 | 1.2 | GEO | 2012 | Nevada | NWPP | 1.2
Empire | OE14 | 1.2 | GEO | 2012 | Nevada | NWPP | 1.2
Indian River Generating Station (DE) | 1 | 81.6 | Coal | 2011 | Delaware | PJM_E | 81.6
Indian River Generating Station (DE) | 3 | 176.8 | Coal | 2013 | Delaware | PJM_E | 176.8
Indian River Generating Station (DE) | 2 | 89 | Coal | 2010 | Delaware | PJM_E | 89
Howard M Down | 9 | 16.5 | STOG | 2011 | New Jersey | PJM_E | 16.5
Hudson Generating Station | 1 | 383 | STOG | 2012 | New Jersey | PJM_E | 383
Kearny Generating Station | 9 | 18.5 | PeakG | 2013 | New Jersey | PJM_E | 18.5
Kearny Generating Station | 10 | 122 | PeakG | 2012 | New Jersey | PJM_E | 122
Kearny Generating Station | 11 | 128 | PeakG | 2012 | New Jersey | PJM_E | 128
Cromby Generating Station | 1 | 187.5 | Coal | 2011 | Pennsylvania | PJM_E | 187.5
Cromby Generating Station | 2 | 230 | STOG | 2011 | Pennsylvania | PJM_E | 230
Cromby Generating Station | ICI | 2.7 | PeakO | 2011 | Pennsylvania | PJM_E | 2.7
Eddystone Generating Station | 1 | 353.6 | Coal | 2011 | Pennsylvania | PJM_E | 279
Eddystone Generating Station | 2 | 353.6 | Coal | 2013 | Pennsylvania | PJM_E | 309
Benning | 15 | 290 | STOG | 2012 | District of Columbia | PJM_ROM | 290
Benning | 16 | 290 | STOG | 2012 | District of Columbia | PJM_ROM | 290
Buzzard Point | E1 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E2 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E4 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E5 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E6 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E7 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | E8 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W10 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W11 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W12 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W13 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W14 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W15 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W16 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Buzzard Point | W9 | 18 | PeakO | 2012 | District of Columbia | PJM_ROM | 18
Will County | 1 | 187.5 | Coal | 2010 | Illinois | PJM_ROR | 187.5
Will County | 2 | 183.7 | Coal | 2010 | Illinois | PJM_ROR | 183.7
Richard H Gorsuch | 1 | 50 | Coal | 2010 | Ohio | PJM_ROR | 50
Richard H Gorsuch | 2 | 50 | Coal | 2010 | Ohio | PJM_ROR | 50
Richard H Gorsuch | 3 | 50 | Coal | 2010 | Ohio | PJM_ROR | 50
Richard H Gorsuch | 4 | 50 | Coal | 2010 | Ohio | PJM_ROR | 50
Hunlock Power Station | 3 | 43 | Coal | 2010 | Pennsylvania | PJM_ROR | 43
WPP 1 Petersburg | 1 | 3 | CT | 2013 | Virginia | PJM_ROR | 3
Chesapeake | 7 | 16 | CT | 2012 | Virginia | PJM_ROR | 16
Altavista Power Station | 1 | 63 | Coal | 2010 | Virginia | PJM_ROR | 63
North Branch (WV) | 1 | 80 | Coal | 2010 | West Virginia | PJM_ROR | 80
Phil Sporn | 5 | 495.5 | Coal | 2011 | West Virginia | PJM_ROR | 440
Arapahoe | 4 | 109 | Coal | 2013 | Colorado | RMPA | 109
Jack McDonough | 1 | 251 | Coal | 2013 | Georgia | SOCO | 251
Jack McDonough | 2 | 252 | Coal | 2013 | Georgia | SOCO | 252
Buck Steam Station (NC) | 3 | 80 | Coal | 2012 | North Carolina | VACAR | 80
Buck Steam Station (NC) | 4 | 40 | Coal | 2012 | North Carolina | VACAR | 40
Cape Fear | 5 | 140.6 | Coal | 2014 | North Carolina | VACAR | 140.6
Cape Fear | 6 | 187.9 | Coal | 2014 | North Carolina | VACAR | 187.9
Cliffside | 1 | 40 | Coal | 2011 | North Carolina | VACAR | 40
Cliffside | 2 | 40 | Coal | 2011 | North Carolina | VACAR | 40
Cliffside | 3 | 65 | Coal | 2011 | North Carolina | VACAR | 65
Cliffside | 4 | 65 | Coal | 2011 | North Carolina | VACAR | 65
Dan River (NC) | 1 | 70 | Coal | 2012 | North Carolina | VACAR | 70
Dan River (NC) | 2 | 70 | Coal | 2012 | North Carolina | VACAR | 70
Dan River (NC) | 3 | 142 | Coal | 2012 | North Carolina | VACAR | 142
L V Sutton | 1 | 112.5 | Coal | 2014 | North Carolina | VACAR | 112.5
L V Sutton | 2 | 112.5 | Coal | 2014 | North Carolina | VACAR | 112.5
L V Sutton | 3 | 446.6 | Coal | 2014 | North Carolina | VACAR | 403
Lee | 1 | 75 | Coal | 2013 | North Carolina | VACAR | 75
Lee | 2 | 75 | Coal | 2013 | North Carolina | VACAR | 75
Lee | 3 | 252.4 | Coal | 2013 | North Carolina | VACAR | 246
Riverbend (NC) | 4 | 94 | Coal | 2015 | North Carolina | VACAR | 94
Riverbend (NC) | 5 | 94 | Coal | 2015 | North Carolina | VACAR | 94
Riverbend (NC) | 6 | 133 | Coal | 2015 | North Carolina | VACAR | 133
Riverbend (NC) | 7 | 133 | Coal | 2015 | North Carolina | VACAR | 133
W H Weatherspoon | 1 | 46 | Coal | 2014 | North Carolina | VACAR | 46
W H Weatherspoon | 2 | 46 | Coal | 2014 | North Carolina | VACAR | 46
W H Weatherspoon | 3 | 73.5 | Coal | 2014 | North Carolina | VACAR | 73.5
W S Lee | 1 | 100 | Coal | 2015 | South Carolina | VACAR | 100
W S Lee | 2 | 100 | Coal | 2015 | South Carolina | VACAR | 100
W S Lee | 3 | 170 | Coal | 2015 | South Carolina | VACAR | 170

## Exhibit9_CapitalCostDetail
Appendix A, Exhibit 9 - Capital Cost Detail
| Technology |  | AEO: Base Overnight Costs in 2011 (2010$/kW) | Learning by 2025 | Base Overnight Capital Costs in 2025 ($2010/kW) | Gas Pipeline Cost | Electrical transmission | Rail Spur | Nuclear Decommissioning Cost | All-in Capital Cost in 2011 w/o IDC ($2010/kW) | All-in Capital Cost in 2025 w/o IDC ($2010/kW) | Sources
Nuclear | Nuclear |  | 5339 | 10% | 4805.1 | 0 | 21.92 | 0 | 253.9714 |  |  | [1]
PC Bituminous | Advanced Coal |  | 2844 | 5% | 2701.8 | 0 | 21.92 | 18.9873 | 0 |  |  | [2]
CC F-Frame | CC F-Frame |  | 978 | 5% | 929.1 | 9.98 | 21.92 | 0 | 0 |  |  | [3]
CC H-Frame | CC H-Frame |  | 1003 | 5% | 952.85 | 9.98 | 21.92 | 0 | 0 |  |  | [4]
CT F -Frame | CT F-Frame |  | 665 | 5% | 631.75 | 24.41 | 21.92 | 0 | 0 |  |  | [5]
IGCC Bituminous | IGCC |  | 3221 | 5% | 3059.95 | 0 | 21.92 | 18.9873 | 0 |  |  | [6]
IGCC Bituminous w/ Sequestration | IGCC w/seq |  | 5348 | 10.97% | 4761.55 | 0 | 21.92 | 18.9873 | 0 |  |  | [7]
Wind Cost Class 1 & 2 | Wind (options B&A) |  | 2438 | 10% |  | 0 | 21.92 | 0 | 0 |  |  | [8]
Wind Offshore | Wind Offshore |  | 5975 | 20% | 4780 | 0 | 21.92 | 0 | 0 |  |  | [9]
PV | Photovoltaic |  | 4755 | 20% | 3804 | 0 | 21.92 | 0 | 0 |  |  | [10]
Solar Thermal | Solar Thermal |  | 4692 | 20% | 3753.6 | 0 | 21.92 | 0 | 0 |  |  | [11]
Landfill Gas | Landfill Gas |  | 2503.386 | 5% | 2378.2167 | 0 | 21.92 | 0 | 0 |  |  | [12]
Biomass | Biomass |  | 3860 | 20% | 3088 | 0 | 21.92 | 18.9873 | 0 |  |  | [13]
Geothermal | Geothermal |  | 4141 | 10% | 3726.9 | 0 | 21.92 | 0 | 0 |  |  | [14]
Wind Options A&B based on New Gen Subteam Recommendations (see summary document)
| [1] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
22% Owner's costs also included, Table 12-1. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
Nuclear Decommissioning Cost: CRA analysis.
| [2] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 3-2. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [3] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 5-1. Owner's Cost: CRA analysis. Gas pipeline source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
| [4] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 6-1. Gas pipeline source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Electric transmission source: PJM's
CONE Combined Cycle Revenue Requirements Update, Aug 26, 2008, Table 2, page 3.
| [5] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 9-1. Gas pipeline source: PJM's "CONE Revenue Requirements 2008 Update", Table 5, page 14. PJM's "CONE Revenue Requirements 2008 Update", Table 5, p14.
| [6] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 10-2. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [7] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Learning for IGCC with CCS equals the weighted average of the 5% learning for IGCC
and the 20% learning for CCS from AEO 2010. Contingency and Optimism factors included in AEO 2011 ER overnight costs; 20% Owner's costs also included, Table 11-1. Electric transmission source:
PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur source: CRA assumption.
| [8] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
6% Owner's costs also included, Table 21-1. Electric transmission source: NREL's Wind Deployment System (WinDS) Model - average interconnection cost for the least expensive 300 GW in the US.
| [9] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
25% Owner's costs also included, Table 22-1. Electric transmission source: assumed to be located near load center.
| [10] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
12% Owner's costs also included, Table 24-2. Electric transmission source: Assumed to be the same as wind.
| [11] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
15% Owner's costs also included, Table 23-1. Electric transmission source: Assumed to be the same as wind.
| [12] | AEO 2010 Assumptions, Tables 8.2 & 8.3. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Electrical transmission cost assumed to be the same as nuclear, coal, CC's, etc.
| [13] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 14-1. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [14] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 17-1. Electric transmission source: Assumed to be the same as wind.
All-in Capital Cost w/o IDC ($2010/kW)
| Technology |  | 2011 | 2015 | 2020 | 2025 | 2030 |  |  |  | slope
Nuclear
Advanced Coal
CC H-Frame
CT
IGCC
IGCC w/seq
Wind
Wind Offshore
Photovoltaic
Solar Thermal
Landfill Gas
Biomass
Geothermal
Note: 2010 costs are assumed to equal 2011 costs. 2015 and 2020 costs are interpolated on a straightline basis between 2010 and 2025. 2030 costs are assumed to equal 2025 costs.
CCs are assumed to use F-Frame technology until 2015 when the switch is made to H-Frame technology.

## Exhibit10_RegionalMultipliers
Appendix A, Exhibit 10 - Regional Multipliers
(based on AEO 2011 early release)
Representative AEO Region | NEEM Region | Nuclear | Adv Coal | CC F-Frame | CC H-Frame | CT F-Frame | IGCC | IGCC w/Seq | Wind | Wind Offshr | Photo-voltaic | Solar Thermal | Landfill Gas | Bio-mass | Geo-thermal
Phoenix, Arizona | AZ_NM_SNV_Coal | 0.976 | 0.943 | 1.026 | 1.026 | 1.044 | 0.954 | 0.945 | 0.976 | 1 | 0.938 | 0.911 | 0.955 | 1 | 0.97
Little Rock, Arkansas | ENT | 0.975 | 0.941 | 0.925 | 0.933 | 0.966 | 0.952 | 0.943 | 0.975 | 1 | 0.935 | 0.907 | 0.953 | 0.919 | 1
Houston, Texas | ERCOT | 0.961 | 0.897 | 0.912 | 0.915 | 1.012 | 0.915 | 0.907 | 0.952 | 0.918 | 0.899 | 0.858 | 0.927 | 0.884 | 1
Tampa, Florida | FRCC | 0.979 | 0.946 | 0.94 | 0.942 | 0.954 | 0.956 | 0.955 | 0.978 | 1 | 0.955 | 0.936 | 0.967 | 0.943 | 1
Bismarck, ND | MAPP_US and MAPP_CA | 0.967 | 0.913 | 0.946 | 0.948 | 1.013 | 0.928 | 0.922 | 1.021 | 1 | 0.947 | 0.912 | 0.944 | 0.903 | 1
Indianapolis, Indiana | MISO_IN | 1.02 | 1.035 | 1.009 | 1.009 | 1.017 | 1.033 | 1.012 | 1.003 | 0.99 | 0.988 | 0.981 | 0.991 | 1.015 | 1
Detroit, Michigan | MISO_MI | 1.016 | 1.04 | 1.053 | 1.052 | 0.97 | 1.035 | 1.035 | 1.027 | 1.028 | 1.034 | 1.048 | 1.027 | 1.039 | 1
St. Louis, Missouri | MISO_MO-IL | 1.028 | 1.077 | 1.056 | 1.054 | 1.01 | 1.069 | 1.055 | 1.036 | 1 | 1.044 | 1.057 | 1.03 | 1.047 | 1
St. Pual, Minnesota | MISO_W | 1.019 | 1.041 | 1.045 | 1.044 | 0.994 | 1.036 | 1.034 | 1.075 | 1.048 | 1.06 | 1.072 | 1.023 | 1.043 | 1
Green Bay, Wisconsin | MISO_WUMS | 1.01 | 1.006 | 0.987 | 0.987 | 0.948 | 1.008 | 0.989 | 0.99 | 0.973 | 0.966 | 0.951 | 0.977 | 0.99 | 1
Omaha, Nebraska | NE | 0.985 | 0.961 | 0.985 | 0.986 | 1.343 | 0.969 | 0.962 | 1.035 | 1 | 0.983 | 0.965 | 0.97 | 0.949 | 1
Average of 6-state region (see below) | NEISO | 1.053 | 1.111 | 1.156 | 1.153 | 1.083 | 1.096 | 1.061 | 1.05 | 1.031 | 1.032 | 1.035 | 1.016 | 1.074 | 1
Louisville, Kentucky | NonRTO_Midwest | 0.976 | 0.939 | 0.946 | 0.948 | 0.954 | 0.951 | 0.942 | 0.971 | 1 | 0.934 | 0.906 | 0.952 | 0.924 | 1
Sacramento, California | NP15 | 1.065 | 1.157 | 1.205 | 1.199 | 1.013 | 1.137 | 1.111 | 1.105 | 1 | 1.105 | 1.133 | 1.057 | 1.119 | 1.054
Salt Lake City, Utah | NWPP_Coal | 0.985 | 0.967 | 0.96 | 0.962 | 1.047 | 0.976 | 0.954 | 1.037 | 1 | 0.962 | 0.931 | 0.951 | 1 | 0.971
Syracuse, New York | NYISO_A-F | 1.066 | 1.12 | 1.163 | 1.159 | 1.056 | 1.108 | 1.055 | 1.008 | 0.988 | 0.986 | 0.976 | 0.996 | 1.075 | 1
Syracuse, New York | NYISO_G-I | 1.066 | 1.12 | 1.163 | 1.159 | 1.056 | 1.108 | 1.055 | 1.008 | 0.988 | 0.986 | 0.976 | 0.996 | 1.075 | 1
New York City, New York | NYISO_J-K | 1.134 | 1.348 | 1.684 | 1.664 | 0.966 | 1.295 | 1.314 | 1.246 | 1.294 | 1.366 | 1.501 | 1.263 | 1.383 | 1
Syracuse, New York | OH (IESO) | 1.12 | - | - | 1.2 | 1.37 | - | - | 1.11 | 0.75 | 0.95 | - | 1.2 | 1.04 | -
Philadelphia, Pennsylvania | PJM_E | 1.049 | 1.129 | 1.261 | 1.253 | 1.037 | 1.11 | 1.113 | 1.061 | 1 | 1.116 | 1.161 | 1.085 | 1.131 | 1
Baltimore, Maryland | PJM_ROM | 1.034 | 1.053 | 1.204 | 1.199 | 1.056 | 1.05 | 1.011 | 1.017 | 0.979 | 0.974 | 0.956 | 0.983 | 1.016 | 1
Cincinnati, Ohio | PJM_ROR | 1.008 | 1.005 | 0.983 | 0.984 | 0.998 | 1.008 | 0.985 | 0.981 | 1 | 0.954 | 0.934 | 0.969 | 0.98 | 1
Denver, Colorado | RMPA | 0.974 | 0.934 | 1.021 | 1.021 | 1.206 | 0.946 | 0.937 | 1.022 | 1 | 0.956 | 0.927 | 0.953 | 0.918 | 0.973
Atlanta, Georgia | SOCO | 0.965 | 0.911 | 0.934 | 0.937 | 0.985 | 0.927 | 0.919 | 0.961 | 0.93 | 0.913 | 0.877 | 0.937 | 0.895 | 1
Los Angeles, California | SP15 | 1.095 | 1.224 | 1.29 | 1.282 | 1.056 | 1.198 | 1.137 | 1.124 | 1.077 | 1.096 | 1.114 | 1.052 | 1.134 | 0.935
Wichita, Kansas | SPP_N | 0.972 | 0.927 | 0.95 | 0.957 | 0.97 | 0.94 | 0.931 | 1.019 | 1 | 0.949 | 0.917 | 0.946 | 0.909 | 1
Wichita, Kansas | SPP_S | 0.972 | 0.927 | 0.95 | 0.957 | 0.97 | 0.94 | 0.931 | 1.019 | 1 | 0.949 | 0.917 | 0.946 | 0.909 | 1
Knoxville, Tennessee | TVA | 0.963 | 0.903 | 0.915 | 0.918 | 0.985 | 0.921 | 0.909 | 0.954 | 1 | 0.898 | 0.856 | 0.927 | 0.883 | 1
Charlotte, North Carolina | VACAR | 0.959 | 0.896 | 0.895 | 0.909 | 1.012 | 0.915 | 0.899 | 0.951 | 0.907 | 0.884 | 0.836 | 0.917 | 0.866 | 1
Source: EIA Updated Capital Cost Estimates for Electricity Generation Plants, Nov 2010
http://www.eia.gov/oiaf/beck_plantcosts/pdf/updatedplantcosts.pdf
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Original CRA data
Boston, Massachusetts | NEISO | 1.183 | 1.387 | 1.4 | 1.389 | 1.126 | 1.338 | 1.262 | 1.111 | 1.132 | 1.164 | 1.222 | 1.118 | 1.335 | 1
State-specific location percent variation from same source as above
|  | Nuclear | Adv Coal | CC F-Frame | CC H-Frame | CT F-Frame | IGCC | IGCC w/Seq | Wind | Wind Offshr | Photo-voltaic | Solar Thermal | Landfill Gas | Bio-mass | Geo-thermal
City | State | 2236MW | 1300MW | 540MW | 400MW | 210MW | 1200MW | 520MW | 100MW | 400MW | 100MW | 100MW | 50MW | 50MW | 50MW
Hartford | Connecticut | 0.147 | 0.294 | 0.279 | 0.272 | 0.037 | 0.26 | 0.177 | 0.066 | 0.057 | 0.071 | 0.092 | 0.052 | 0.229 | 0
Portland | Maine | 0.004 | -0.006 | -0.034 | -0.027 | 0 | 0 | -0.028 | 0.064 | -0.026 | -0.032 | -0.059 | -0.041 | -0.04 | 0
Boston | Massachusetts | 0.183 | 0.387 | 0.4 | 0.389 | 0.126 | 0.338 | 0.262 | 0.111 | 0.132 | 0.164 | 0.222 | 0.118 | 0.335 | 0
Concord | New Hampshire | -0.008 | -0.018 | 0.073 | 0.072 | 0.054 | -0.013 | -0.022 | 0.053 | 0 | -0.003 | -0.017 | -0.02 | -0.036 | 0
Providence | Rhode Island | 0.016 | 0.043 | 0.22 | 0.214 | 0.122 | 0.039 | 0.034 | 0.021 | 0.025 | 0.031 | 0.042 | 0.028 | 0.034 | 0
Burlington | Vermont | -0.023 | -0.033 | -0.001 | 0 | 0.161 | -0.046 | -0.058 | 0.034 | 0 | -0.042 | -0.072 | -0.044 | -0.081 | 0
Average |  | 0.053 | 0.111 | 0.156 | 0.153 | 0.083 | 0.096 | 0.061 | 0.05 | 0.031 | 0.032 | 0.035 | 0.016 | 0.074 | 0
Average for Onshore wind is calculated as the average location percent variations of cities in Maine, New Hampshire, and Vermont as most onshore wind would be in these states for NEISO

## Exhibit11_WindCF & Potential
Appendix A, Exhibit 11 - NEEM Capacity Factors (New and Existing) and Resource Potentials
Based on NREL data for Onshore Potential Capacities and CRA data for capacity factors (and associated wind shapes in Exhibit 4) and CRA data for all Offshore
NEEM Region | NREL Onshore Potential Class 3, MW | Class 3 Avg Capacity Factor (x% of CRA) | NREL Onshore Potential (Class 4+), MW | Avg Class 4+ Capacity Factor (CRA) | CRA Offshore Potential (shallow offshore only, Class 4+), MW | Avg Capacity Factor
AZ_NM_SNV | 224904 | 26% | 107026 | 0.306 | - | NA
ENT | 2326 | 29.6% | 77 | 0.336 | - | NA
ERCOT | 286850 | 29.4% | 97173 | 0.333 | - | NA
FRCC | - | #DIV/0! | - | 0 | - | NA
MAPP_US | 279490 | 33.9% | 602545 | 0.398 | - | NA
MAPP_CA | - | #N/A | 300000 | 0.285 | NA | NA
MISO_IN | 102337 | 29.4% | 16 | 0.331 | 765 | 35%
MISO_MI | 56833 | 27% | 632 | 0.305 | 4360 | 35.7%
MISO_MO_IL | 105738 | 31.1% | 5867 | 0.35 | - | NA
MISO_W | 775035 | 31.7% | 1199936 | 0.377 | - | 0%
MISO_WUMS | 16528 | 28.4% | 284 | 0.326 | 2054 | 33.8%
NE | 417805 | 35.7% | 464227 | 0.405 | - | NA
NEISO_CT | 4.68 | 21.9% | 1.46 | 0.264 | 176 | 35%
NEISO_MA | 1562.7 | 25.4% | 488.28 | 0.307 | 7944 | 45.6%
NEISO_ME | 7963.22 | 28.2% | 2488.18 | 0.341 | 174 | 39.9%
NEISO_NH | 2372.12 | 27.5% | 741.19 | 0.332 | 20 | 36.5%
NEISO_RI | 84.22 | 18.6% | 26.31 | 0.224 | 223 | 42.7%
NEISO_VT | 4917.36 | 28.4% | 1536.47 | 0.342 | - | NA
NEISO (Note A) | 16904 | 27.9% | 5282 | 0.336
NonRTO_Midwest | 57 | 22.4% | 23 | 0.262 | - | 0%
NP15 | 10824 | 25.2% | 3440 | 0.297 | 135 | 40%
NWPP | 653248 | 22.7% | 591099 | 0.264 | 193 | 40%
NYISO_A-F | 12648 | 28.2% | 837 | 0.331 | 486 | 0.38
NYISO_G-I | 300 | 27.9% | 63 | 0.339 | 245 | NA
NYISO_J-K | 164 | 27.8% | 169 | 0.316 | 2368 | 0.407
IESO | - | #N/A | 300000 | 0.285 | 6414 | 38%
PJM_E | 3147 | 20.1% | 467 | 0.226 | 9588 | 41.4%
PJM_ROM | 5812 | 24.3% | 1228 | 0.285 | 16918 | 39.6%
PJM_ROR | 50402 | 26.7% | 3204 | 0.318 | 20230 | 38.1%
RMPA | 417139 | 28.8% | 539849 | 0.343 | - | NA
SOCO | 52 | 0% | 8 | 0 | - | NA
SP15 | 31170 | 24.6% | 14849 | 0.297 | - | NA
SPP_N | 292779 | 33% | 597665 | 0.392 | - | NA
SPP_S | 420353 | 34.4% | 496536 | 0.392 | - | NA
TVA | 105 | 23.9% | 34 | 0.291 | - | NA
VACAR | 2797 | 24.8% | 693 | 0.297 | 39250 | 39.4%
Note A: EWITS weighted capacity factor value from CRA is 32.1% for Class 4+ and 26.6% for Class 3 (ratioed value from Class 4+)
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit12_NewResourceLimits
Appendix A, Exhibit 12 - New Resource Limits
Cumulative New Build GW Limit Potential by NEEM Region | [5 empty] | Note: Forced New Builds are included in this constraint
| Pulverized Coal | Nuclear | On-Shore Wind Class 3 | On-Shore Wind Class 4+ | Off-Shore Wind | Biomass | Photo-voltaic | Landfill Gas | Geoth- ermal | Solar Thermal | IGCC-CCS
AZ_NM_SNV | ∞ | ∞ | 224.9 | 107.03 | - | 6.54 | 10 | 0.0455 | 1.45 | 10 | ∞
ENT | ∞ | ∞ | 2.33 | 0.08 | - | 10.0749 | 5 | 0.13425 | 0 | 0 | ∞
ERCOT | ∞ | ∞ | 286.85 | 97.17 | - | 4.065 | 10 | 0.354 | 0 | 0 | ∞
FRCC | ∞ | ∞ | - | - | - | 2.0019 | 10 | 0.198 | 0 | 0 | ∞
MAPP_US | ∞ | ∞ | 279.49 | 602.54 | - | 5.4 | 1 | 0 | 0 | 0 | ∞
MISO_IN | ∞ | ∞ | 102.34 | 0.02 | 0.8 | 6.1 | 1.3 | 0.1 | 0 | 0 | ∞
MISO_MI | ∞ | ∞ | 56.83 | 0.63 | 4.4 | 6.1445 | 1.25 | 0.1282 | 0 | 0 | ∞
MISO_MO_IL | ∞ | ∞ | 105.74 | 5.87 | - | 8.8789 | 7 | 0.4355 | 0 | 0 | ∞
MISO_W | ∞ | ∞ | 775.03 | 1199.94 | - | 5.4 | 1 | 0 | 0 | 0 | ∞
MISO_WUMS | ∞ | ∞ | 16.53 | 0.28 | 2.1 | 3.2008 | 2 | 0.1675 | 0 | 0 | ∞
NE | ∞ | ∞ | 417.81 | 464.23 | - | 10.8177 | 2 | 0.071667 | 0 | 0 | ∞
NEISO | 0 | ∞ | 16.9 | 5.28 | 8.5 | 1.7 | 12 | 0.71 | 0 | 0 | 4
NonRTO_Midwest | ∞ | ∞ | 0.06 | 0.02 | - | 6.1445 | 1.25 | 0.1282 | 0 | 0 | ∞
NP15 | 0 | 0 | 10.82 | 3.44 | 0.1 | 0.84324 | 10 | 0.565 | 0.64 | 0.1 | ∞
NWPP | ∞ | ∞ | 653.25 | 591.1 | 0.2 | 9.05 | 5 | 0.26 | 0.52 | 0.003 | ∞
NYISO_A-F | 0 | ∞ | 12.65 | 0.84 | 0.5 | 1.0007 | 4 | 0.446 | 0 | 0 | ∞
NYISO_G-I | 0 | 0 | 0.3 | 0.06 | 0.2 | 0.81872 | 2 | 0.223 | 0 | 0 | ∞
NYISO_J-K | 0 | 0 | 0.16 | 0.17 | 2.4 | 0 | 4 | 0.446 | 0 | 0 | 0
PJM_E | 0 | ∞ | 3.15 | 0.47 | 9.6 | 0.33231 | 2 | 0.142 | 0 | 0 | ∞
PJM_ROM | ∞ | ∞ | 5.81 | 1.23 | 16.9 | 2.3578 | 4 | 0.284 | 0 | 0 | ∞
PJM_ROR | ∞ | ∞ | 50.4 | 3.2 | 20.2 | 10.5563 | 6.9167 | 0.36815 | 0 | 0 | ∞
RMPA | ∞ | ∞ | 417.14 | 539.85 | - | 3.7268 | 5 | 0.05 | 2.57 | 9.3548 | ∞
SOCO | ∞ | ∞ | 0.05 | 0.01 | - | 6.5552 | 2 | 0.13425 | 0 | 0 | ∞
SP15 | 0 | 0 | 31.17 | 14.85 | - | 0.67459 | 10 | 0.565 | 1.49 | 10 | ∞
SPP_N | ∞ | ∞ | 292.78 | 597.66 | - | 6.4056 | 2 | 0.095 | 0 | 0 | ∞
SPP_S | ∞ | ∞ | 420.35 | 496.54 | - | 4.5073 | 2 | 0.095 | 0 | 0 | ∞
TVA | ∞ | ∞ | 0.11 | 0.03 | - | 7.3943 | 2 | 0.13425 | 0 | 0 | ∞
VACAR | ∞ | ∞ | 2.8 | 0.69 | 39.3 | 6.9863 | 1.3333 | 0.0895 | 0 | 0 | ∞
ALB | 0 | ∞ | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BC | 0 | ∞ | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OH | 0 | ∞ | 0 | 300 | 6.414 | 0 | 0.1 | 0 | 0 | 0 | 0
MAPP_CA | 0 | ∞ | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | ∞ | ∞ | 4202.65 | 5338.51 | 111.54 | 137.7 | 126.1 | 6.5 | 6.67 | 29.4578 | ∞
New Pulverized Coal assumed not to be built in California, New York, New England, PJM East, and Canada
New Nuclear assumed not to be built in California or near New York City
CCS is a proposed CRA assumption. |  | PV and solar thermal are proposed CRA assumptions.
On- and Off-shore wind resource potential based on Win DS base case
Biomass based on CRA judgment, informed by USDA/DOE 2005 "Billion Ton Study".
Landfill gas based on CRA judgment, informed by EPA NEEDS report (2006).
Geothermal based on Lovekin & Pletka, GRC Transactions, vol. 33, 2009 (note: could be used for capital costs in lieu of AEO 2011)
Yellow values are updates from CRA 2/3/11
Onshore Winds have had a Class 3 category added and Class 4+ values changed based on NREL data, see Exhibit 11
Cumulative GW of New Build Allowed in Total U.S. and Canada through This Year
Note: If %, represents % of total in table above; Forced Builds are included in constraint; if no figure listed the table above applies
| 2010 | 2015 | 2020 |  | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Pulverized Coal | 0 | F | F+10
Nuclear | 0 | F1 | *F2 |  | *F2+15 | *F2+50 | *F2+100 | *F2+150 | *F2+200 | *F2+250
On-Shore Wind | 0 | F | F+175
Off-Shore Wind | 0 | F | F+20
Biomass | 0 | F | 25% |  | 50% | 75% | 100%
Photovoltaic | 0 | F | 10
Landfill Gas | 0 | F | 33% |  | 67% | 100%
Geo Thermal | 0 | F | 33%
Solar Thermal | 0 | F | 33%
IGCC-CCS | 0 | F | F+2 |  | F+12 | F+32
IGCC | 0 | F | F+60
CCS Retrofits | 0 | F | F+5 |  | F+25 | F+65
F: Forced builds only | * F2 = F1 + (2016-2020 nuclear builds)
Represents practical constraints on building over time, such as permitting/siting, construction lead times. CRA assumptions.
2020 limits in place for all technologies, most other types unlimited (other than in table above) by 2025
Transfer limits, reserve margins, hurdle rates, and intermittent resource limits will limit construction inside any particular NEEM region
Nuclear likely to be highly economic in certain scenarios, thus on-going limitations in place to represent licensing issues.
IGCC-CCS not available until 2020 (for economic builds); CCS Retrofits available in the same year.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note on F17: Changed from "-" to 8.5 based on sum of state amounts from CRA. Not sure how "-" was inserted. --StanORNL February 28, 2011 8:08:08 PM EST

## Exhibit13_RetrofitCosts
Appendix A, Exhibit 13 - Retrofit Costs Source Information
Only change is for BAU sensitivity 9 - no new non-CO2 EPA Regs--CRA revise and document retirement/retrofit logic as appropriate. Tables 8-10 probably stay the same, just the logic in applying them gets revised.
Retrofit Type | Emissions Type | Capital Cost | Fixed O&M | Variable O&M
FGD | SO2 | Sargent & Lundy. "IPM Model - Revisions to Cost and Performance for APC Technologies. Wet FGD Cost Development Methodology." August 2010. [Table 1] | Sargent & Lundy. "IPM Model - Revisions to Cost and Performance for APC Technologies. Wet FGD Cost Development Methodology." August 2010. [Table 1] | Sargent & Lundy. "IPM Model - Revisions to Cost and Performance for APC Technologies. Wet FGD Cost Development Methodology." August 2010. [Table 1]
SCR | NOx | Cichanowicz, J Edward. "Current Capital Cost and Cost-Effectiveness of Power Plant Emissions Control Technologies." January 2010. [Figure 6-1] | Cichanowicz, J Edward. "Current Capital Cost and Cost-Effectiveness of Power Plant Emissions Control Technologies." January 2010. [Table 6-1] | Cichanowicz, J Edward. "Current Capital Cost and Cost-Effectiveness of Power Plant Emissions Control Technologies." January 2010. [Table 6-1]
SNCR | NOx | EPA IPM 2006 Documentation | EPA IPM 2006 Documentation | EPA IPM 2006 Documentation
ACI | Hg | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Figures B-6 and B-8] | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Figure B-7] | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Pages 65-66]; CRA discussion with Cichanowicz.
RPJ | Hg | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Figures B-6 and B-8] | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Figure B-7] | Cichanowicz, J Edward. "Testimony of J E Cichanowicz to the Illinois Pollution Control Board. A Review of the Status of Mercury Control Technology." July 28, 2006. [Pages 65-66]; CRA discussion with Cichanowicz.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit14_ForcedRetrofits
Appendix A, Exhibit 14 - Forced Retrofits
OK, but suggest CRA drop non-EI regions (if any), redo if NEEM region change affects, and verify that table is up to date and complete with all of Ventyx and CRA info. | No changes for BAU Sensitivities 1-9. (Ex Gen)
NEEM Region | Installation Year Modeled | Plant Name | Unit | Control Type (NOx, SO2, PM, HG, CO, VOC, Multi, CO2) | Control Equipment | Install Date | Retrofit Modeled
MISO_MO_IL | 2011 | Sioux | 1 | SO2 | Wet Lime FGD | 2010-09-30 | FGD
MISO_MO_IL | 2011 | Sioux | 2 | SO2 | Wet Lime FGD | 2010-09-30 | FGD
MISO_W | 2011 | Lansing | 4 | NOx | Selective Catalytic Reduction | 2010-09-30 | SCR
MAPP_US | 2011 | Leland Olds 1 & 2 | 1 | SO2 | Wet Limestone | 2011-03-31 | FGD
MAPP_US | 2011 | Leland Olds 1 & 2 | 2 | SO2 | Wet Limestone | 2010-10-31 | FGD
MISO_W | 2011 | Sutherland (IA) | 3 | NOx | Selective Non-catalytic Reduction | 2010-10-31 | SNCR
MI | 2012 | J H Campbell | 2 | NOx | Selective Catalytic Reduction | 2011-09-30 | SCR
NEISO | 2012 | Merrimack | 1 | SO2 | Wet Limestone | 2011-12-31 | FGD
NEISO | 2012 | Merrimack | 2 | SO2 | Wet Limestone | 2011-12-31 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 1 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 2 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 3 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 4 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 5 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Clifty Creek | 6 | SO2 | Wet Limestone | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Kyger Creek | 1 | SO2 | Flue Gas Desulfurization | 2011-03-31 | FGD
NonRTO_Midwest | 2011 | Kyger Creek | 2 | SO2 | Flue Gas Desulfurization | 2011-03-31 | FGD
NonRTO_Midwest | 2011 | Kyger Creek | 3 | SO2 | Flue Gas Desulfurization | 2011-03-31 | FGD
NonRTO_Midwest | 2011 | Kyger Creek | 4 | SO2 | Flue Gas Desulfurization | 2011-06-30 | FGD
NonRTO_Midwest | 2011 | Kyger Creek | 5 | SO2 | Flue Gas Desulfurization | 2011-06-30 | FGD
PJM_ROR | 2011 | Chesterfield | 3 | SO2 | Flue Gas Desulfurization | 2011-06-30 | FGD
PJM_ROR | 2011 | Chesterfield | 4 | SO2 | Flue Gas Desulfurization | 2011-06-30 | FGD
PJM_ROR | 2011 | Chesterfield | 5 | SO2 | Flue Gas Desulfurization | 2011-06-30 | FGD
PJM_E | 2011 | Hudson Generating Station | 2 | NOx | Selective Catalytic Reduction | 2010-12-31 | SCR
PJM_E | 2011 | Hudson Generating Station | 2 | SO2 | Dry Lime FGD | 2010-12-31 | FGD
PJM_Midwest | 2011 | Cardinal | 3 | SO2 | Wet Limestone | 2011-03-31 | FGD
PJM_Midwest | 2011 | W H Sammis | 1 | NOx | Selective Non-catalytic Reduction | 2010-12-31 | SNCR
PJM_Midwest | 2011 | W H Sammis | 3 | NOx | Selective Non-catalytic Reduction | 2010-12-31 | SNCR
PJM_Midwest | 2011 | W H Sammis | 4 | NOx | Selective Non-catalytic Reduction | 2010-12-31 | SNCR
MISO_MO_IL | 2011 | Baldwin Energy Complex | 3 | SO2 | Dry Lime FGD | 2010-12-31 | FGD
MISO_MO_IL | 2013 | Havana | 6 | SO2 | Dry Lime FGD | 2012-12-01 | FGD
SOCO | 2012 | R D Morrow | 1 | SO2 | Wet Limestone | 2011-08-30 | FGD
SOCO | 2012 | R D Morrow | 2 | SO2 | Wet Limestone | 2011-08-30 | FGD
SOCO | 2014 | Scherer | 1 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2014 | Scherer | 1 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2014 | Scherer | 2 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2014 | Scherer | 2 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2014 | Scherer | 3 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2014 | Scherer | 3 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2014 | Scherer | 4 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2014 | Scherer | 4 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2011 | Miller | 1 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2011 | Miller | 1 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2010 | Miller | 2 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2010 | Miller | 2 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2009 | Miller | 3 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2009 | Miller | 3 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2010 | Miller | 4 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
SOCO | 2010 | Miller | 4 | SO2 | Flue Gas Desulfurization | 2013-12-31 | FGD
SOCO | 2012 | Crist | 6 | NOx | Selective Catalytic Reduction | 2013-12-31 | SCR
VACAR | 2011 | Cliffside | 5 | SO2 | Wet Limestone | 2010-10-31 | FGD
MISO_WUMS | 2012 | South Oak Creek | 7 | NOx | Selective Catalytic Reduction | 2012-06-01 | SCR
MISO_WUMS | 2012 | South Oak Creek | 7 | SO2 | Wet Limestone | 2012-06-01 | FGD
MISO_WUMS | 2012 | South Oak Creek | 8 | NOx | Selective Catalytic Reduction | 2012-06-01 | SCR
MISO_WUMS | 2012 | South Oak Creek | 8 | SO2 | Wet Limestone | 2012-06-01 | FGD
MISO_WUMS | 2013 | Edgewater (WI) | 5 | NOx | Selective Catalytic Reduction | 2012-10-31 | SCR
MISO_WUMS | 2013 | South Oak Creek | 5 | NOx | Selective Catalytic Reduction | 2012-12-01 | SCR
MISO_WUMS | 2013 | South Oak Creek | 5 | SO2 | Wet Limestone | 2012-12-01 | FGD
MISO_WUMS | 2013 | South Oak Creek | 6 | NOx | Selective Catalytic Reduction | 2012-12-01 | SCR
MISO_WUMS | 2013 | South Oak Creek | 6 | SO2 | Wet Limestone | 2012-12-01 | FGD

## Exhibit15_NuclearUprates
Appendix A, Exhibit 15
Forced Retrofits - Nuclear Uprates
Plant Name | Uprate MW | Uprate Date
Prairie Island 1 | 9 | 2011%
Prairie Island 2 | 9 | 2011%
LaSalle 1 | 19 | 2011%
LaSalle 2 | 19 | 2011%
Browns Ferry 1 | 165 | 2014%
Browns Ferry 2 | 165 | 2014%
Browns Ferry 3 | 165 | 2014%
Monticello (MN) 1 | 76 | 2012%
Point Beach 1 | 121 | 2011%
Point Beach 2 | 114 | 2011%
Nine Mile Point Nuclear Station (NY) 2 | 168 | 2012%
Limerick 1 | 19 | 2011%
Limerick 2 | 19 | 2011%
Grand Gulf Nuclear Station 1 | 170 | 2012%
Turkey Point 3 | 115 | 2012
Turkey Point 4 | 115 | 2012%
Farley 1 | 35 | 2011%
Farley 2 | 35 | 2012%
The input assumptions contained herein reflect a joint assumptions development process between EIPC,
EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling. As such,
these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit16A_HHNaturalGasPrices
Appendix A, Exhibit 16 - Natural Gas Prices, Base Case
AEO 2011 Reference Case (early release)
Shift in Price from
Year | Henry Hub Spot Price (2010$/MMBtu) |  | AEO2011 HH (2009$/MMBtu) | AEO2011 in 2010$/MMBtu | AEO 2010 Reference HH (2008$/MMBtu) | AEO2010 in 2010$/MMBtu | AEO2011 | AEO2010 | Composite Price in 2010$/MMBtu | AEO2010 Hi Gas Scenario in 2008 $/mmbtu | Ratio of 2010 Hi Gas to Reference | Hi Gas Henry Hub Price (2010$/mmBtu)
2011 | 4.52 |  | 4.4807 |  | 5.6827 |  | 100% | 0% |  | 6.27
2012 | 4.6066 |  | 4.5665 |  | 6.1725 |  |  |  |  | 7.15
2013 | 4.743 |  | 4.7018 |  | 6.129 |  |  |  |  | 7.27
2014 | 4.8077 |  | 4.7659 |  | 6.0861 |  |  |  |  | 7.41
2015 | 4.8478 |  | 4.8057 |  | 6.2707 |  |  |  |  | 7.59
2016 | 4.877 |  | 4.8346 |  | 6.377 |  |  |  |  | 7.67
2017 | 4.9247 |  | 4.882 |  | 6.385 |  |  |  |  | 7.64
2018 | 5.0029 |  | 4.9594 |  | 6.434 |  |  |  |  | 7.68
2019 | 5.0807 |  | 5.0365 |  | 6.5062 |  |  |  |  | 7.85
2020 | 5.2234 |  | 5.178 |  | 6.64 |  |  |  |  | 7.8
2021 | 5.3794 |  | 5.3327 |  | 6.7401 |  |  |  |  | 7.61
2022 | 5.533 |  | 5.4849 |  | 6.9289 |  |  |  |  | 7.84
2023 | 5.7164 |  | 5.6668 |  | 6.9571 |  |  |  |  | 8.15
2024 | 5.8971 |  | 5.8459 |  | 6.9144 |  |  |  |  | 8.43
2025 | 6.0656 |  | 6.0129 |  | 6.9918 |  |  | 100% |  | 8.71
2026 | 6.2063 |  | 6.1524 |  | 7.152 |  |  | 100% |  | 8.92
2027 | 6.335 |  | 6.2799 |  | 7.292 |  |  | 100% |  | 9.14
2028 | 6.4203 |  | 6.3645 |  | 7.5303 |  |  | 100% |  | 9.5
2029 | 6.4822 |  | 6.4259 |  | 7.7743 |  |  | 100% |  | 9.78
2030 | 6.5596 |  | 6.5026 |  | 8.0498 |  |  | 100% |  | 10
2031 | 6.6804 |  | 6.6224 |  | 8.389 |  |  | 100% |  | 9.93
2032 | 6.818 |  | 6.7588 |  | 8.4968 |  |  | 100% |  | 10.18
2033 | 6.9363 |  | 6.876 |  | 8.5296 |  |  | 100% |  | 10.52
2034 | 7.0702 |  | 7.0088 |  | 8.7486 |  |  | 100% |  | 10.78
2035 | 7.2541 |  | 7.1911 |  | 8.8799 |  |  | 100% |  | 10.88
Between 2035 and 2050, CRA proposes to increase gas prices at the |  |  | EIA Case ID |  | EIA Case ID
same rate of increase for the 2030-2035 period. |  |  | d120810c |  | d111809a
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
|  | From AEO2011 Refernce |  | 2008 | 2009 | 2010
|  |  | GDP Chain-type Price Index (2005=1.000) | 1.086 | 1.0962 | 1.1058

## Exhibit16B_NEEMRegionGasPrices
Appendix A, Exhibit 16B - Natural Gas Prices, Base Case | [8 empty] | 1.0088 | convert 2009$ to 2010$
AEO 2011 Reference Case (early release)
Posted 2/9/11 |  |  |  |  | Between 2035 and 2050, CRA proposes to increase gas prices at the
| 2010$/MMBtu |  |  |  | same rate of increase for the 2030-2035 period.
| Region | Season | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| ALB | Summer | 4.17 | 4.02 | 3.97 | 3.84 | 3.96 | 4.26 | 4.43 | 4.59 | 4.7 | 4.83 | 4.97 | 5.15 | 5.34 | 5.48 | 5.6 | 5.7 | 5.81 | 5.94 | 6.05 | 6.15 | 6.25 | 6.37 | 6.52 | 6.72 | 6.93
| ALB | Winter | 4.5 | 4.35 | 4.39 | 4.26 | 4.4 | 4.74 | 4.92 | 5.1 | 5.22 | 5.37 | 5.53 | 5.72 | 5.93 | 6.08 | 6.22 | 6.34 | 6.45 | 6.6 | 6.73 | 6.84 | 6.95 | 7.08 | 7.25 | 7.47 | 7.7
| ALB | Shoulder | 4.34 | 4.15 | 4.11 | 3.98 | 4.1 | 4.42 | 4.6 | 4.75 | 4.87 | 5.01 | 5.15 | 5.34 | 5.54 | 5.67 | 5.8 | 5.91 | 6.03 | 6.15 | 6.27 | 6.38 | 6.48 | 6.61 | 6.76 | 6.97 | 7.18
| AZ_NM_SNV_Gas | Summer | 4.56 | 4.31 | 4.27 | 4.22 | 4.26 | 4.38 | 4.5 | 4.65 | 4.8 | 4.92 | 5.08 | 5.27 | 5.41 | 5.53 | 5.63 | 5.76 | 5.89 | 6.02 | 6.13 | 6.22 | 6.31 | 6.43 | 6.55 | 6.71 | 6.87
| AZ_NM_SNV_Gas | Winter | 4.72 | 4.69 | 4.72 | 4.72 | 4.77 | 4.89 | 5.03 | 5.2 | 5.36 | 5.51 | 5.68 | 5.89 | 6.04 | 6.18 | 6.29 | 6.44 | 6.59 | 6.74 | 6.85 | 6.95 | 7.06 | 7.18 | 7.32 | 7.5 | 7.69
| AZ_NM_SNV_Gas | Shoulder | 4.54 | 4.43 | 4.43 | 4.39 | 4.43 | 4.56 | 4.68 | 4.85 | 5 | 5.13 | 5.28 | 5.48 | 5.63 | 5.76 | 5.86 | 6 | 6.14 | 6.27 | 6.38 | 6.48 | 6.57 | 6.69 | 6.82 | 6.98 | 7.15
| BC | Summer | 4.12 | 3.92 | 3.87 | 3.75 | 3.86 | 4.15 | 4.32 | 4.47 | 4.58 | 4.71 | 4.84 | 5.02 | 5.2 | 5.34 | 5.45 | 5.56 | 5.67 | 5.78 | 5.9 | 6 | 6.09 | 6.2 | 6.35 | 6.55 | 6.75
| BC | Winter | 4.6 | 4.48 | 4.5 | 4.38 | 4.51 | 4.86 | 5.06 | 5.23 | 5.36 | 5.51 | 5.67 | 5.87 | 6.09 | 6.24 | 6.39 | 6.51 | 6.63 | 6.77 | 6.9 | 7.02 | 7.13 | 7.27 | 7.45 | 7.67 | 7.9
| BC | Shoulder | 4.3 | 4.15 | 4.12 | 3.99 | 4.12 | 4.43 | 4.61 | 4.77 | 4.89 | 5.03 | 5.17 | 5.35 | 5.55 | 5.7 | 5.82 | 5.93 | 6.04 | 6.17 | 6.29 | 6.4 | 6.51 | 6.63 | 6.78 | 6.99 | 7.21
| ENT | Summer | 4.57 | 4.41 | 4.44 | 4.38 | 4.46 | 4.55 | 4.6 | 4.67 | 4.73 | 4.83 | 4.97 | 5.08 | 5.24 | 5.39 | 5.53 | 5.65 | 5.77 | 5.84 | 5.87 | 5.92 | 6.04 | 6.18 | 6.27 | 6.41 | 6.6
| ENT | Winter | 4.79 | 4.79 | 4.87 | 4.83 | 4.91 | 5 | 5.07 | 5.15 | 5.21 | 5.33 | 5.47 | 5.61 | 5.77 | 5.95 | 6.09 | 6.23 | 6.36 | 6.43 | 6.47 | 6.52 | 6.65 | 6.81 | 6.92 | 7.07 | 7.28
| ENT | Shoulder | 4.65 | 4.54 | 4.59 | 4.53 | 4.61 | 4.7 | 4.75 | 4.83 | 4.89 | 5 | 5.13 | 5.26 | 5.42 | 5.58 | 5.72 | 5.85 | 5.97 | 6.03 | 6.07 | 6.13 | 6.25 | 6.39 | 6.48 | 6.63 | 6.83
| ERCOT | Summer | 4.59 | 4.41 | 4.42 | 4.36 | 4.43 | 4.52 | 4.58 | 4.65 | 4.71 | 4.82 | 4.96 | 5.08 | 5.23 | 5.39 | 5.52 | 5.64 | 5.76 | 5.83 | 5.86 | 5.91 | 6.02 | 6.17 | 6.26 | 6.4 | 6.59
| ERCOT | Winter | 4.69 | 4.73 | 4.81 | 4.75 | 4.85 | 4.95 | 5.01 | 5.09 | 5.16 | 5.28 | 5.42 | 5.56 | 5.73 | 5.9 | 6.04 | 6.17 | 6.3 | 6.37 | 6.41 | 6.47 | 6.59 | 6.75 | 6.85 | 7 | 7.21
| ERCOT | Shoulder | 4.62 | 4.5 | 4.55 | 4.48 | 4.57 | 4.66 | 4.72 | 4.8 | 4.85 | 4.97 | 5.1 | 5.23 | 5.39 | 5.55 | 5.69 | 5.81 | 5.93 | 6 | 6.03 | 6.09 | 6.21 | 6.34 | 6.44 | 6.59 | 6.79
| FRCC | Summer | 5.78 | 5.56 | 5.49 | 5.43 | 5.48 | 5.54 | 5.6 | 5.65 | 5.69 | 5.81 | 5.91 | 6.07 | 6.25 | 6.44 | 6.61 | 6.73 | 6.85 | 6.92 | 6.96 | 7.02 | 7.12 | 7.25 | 7.37 | 7.5 | 7.72
| FRCC | Winter | 5.78 | 5.82 | 5.81 | 5.77 | 5.84 | 5.9 | 5.96 | 6.01 | 6.06 | 6.18 | 6.3 | 6.46 | 6.66 | 6.86 | 7.04 | 7.17 | 7.29 | 7.36 | 7.41 | 7.48 | 7.59 | 7.73 | 7.85 | 7.99 | 8.23
| FRCC | Shoulder | 5.75 | 5.62 | 5.56 | 5.52 | 5.57 | 5.63 | 5.69 | 5.74 | 5.78 | 5.9 | 6.01 | 6.17 | 6.35 | 6.54 | 6.71 | 6.84 | 6.96 | 7.03 | 7.07 | 7.13 | 7.24 | 7.37 | 7.49 | 7.63 | 7.85
| HQ | Summer | 3.78 | 4.13 | 4.43 | 4.55 | 4.43 | 4.28 | 4.29 | 4.32 | 4.33 | 4.35 | 4.38 | 4.44 | 4.56 | 4.63 | 4.74 | 4.8 | 4.87 | 4.96 | 5.05 | 5.16 | 5.26 | 5.34 | 5.42 | 5.49 | 5.48
| HQ | Winter | 6.47 | 5.74 | 5.89 | 6.04 | 5.87 | 5.67 | 5.68 | 5.71 | 5.72 | 5.74 | 5.77 | 5.86 | 6 | 6.09 | 6.24 | 6.3 | 6.38 | 6.51 | 6.62 | 6.76 | 6.88 | 7 | 7.1 | 7.18 | 7.16
| HQ | Shoulder | 4.16 | 4.55 | 4.83 | 4.96 | 4.83 | 4.66 | 4.67 | 4.7 | 4.71 | 4.72 | 4.76 | 4.82 | 4.95 | 5.02 | 5.14 | 5.2 | 5.27 | 5.37 | 5.46 | 5.58 | 5.68 | 5.77 | 5.87 | 5.93 | 5.92
| MAPP_CA | Summer | 4.23 | 4.06 | 3.99 | 3.93 | 4.02 | 4.13 | 4.24 | 4.36 | 4.48 | 4.61 | 4.72 | 4.84 | 4.99 | 5.14 | 5.32 | 5.43 | 5.54 | 5.65 | 5.74 | 5.83 | 5.92 | 6.03 | 6.16 | 6.33 | 6.53
| MAPP_CA | Winter | 4.58 | 4.44 | 4.46 | 4.41 | 4.51 | 4.64 | 4.78 | 4.91 | 5.04 | 5.18 | 5.33 | 5.45 | 5.62 | 5.79 | 6 | 6.13 | 6.26 | 6.37 | 6.48 | 6.59 | 6.69 | 6.82 | 6.95 | 7.15 | 7.38
| MAPP_CA | Shoulder | 4.4 | 4.2 | 4.16 | 4.1 | 4.19 | 4.3 | 4.43 | 4.55 | 4.67 | 4.8 | 4.94 | 5.06 | 5.21 | 5.36 | 5.56 | 5.68 | 5.8 | 5.9 | 6 | 6.1 | 6.19 | 6.31 | 6.44 | 6.62 | 6.82
| MAPP_US | Summer | 4.23 | 4.06 | 3.99 | 3.93 | 4.02 | 4.13 | 4.24 | 4.36 | 4.48 | 4.61 | 4.72 | 4.84 | 4.99 | 5.14 | 5.32 | 5.43 | 5.54 | 5.65 | 5.74 | 5.83 | 5.92 | 6.03 | 6.16 | 6.33 | 6.53
| MAPP_US | Winter | 4.58 | 4.44 | 4.46 | 4.41 | 4.51 | 4.64 | 4.78 | 4.91 | 5.04 | 5.18 | 5.33 | 5.45 | 5.62 | 5.79 | 6 | 6.13 | 6.26 | 6.37 | 6.48 | 6.59 | 6.69 | 6.82 | 6.95 | 7.15 | 7.38
| MAPP_US | Shoulder | 4.4 | 4.2 | 4.16 | 4.1 | 4.19 | 4.3 | 4.43 | 4.55 | 4.67 | 4.8 | 4.94 | 5.06 | 5.21 | 5.36 | 5.56 | 5.68 | 5.8 | 5.9 | 6 | 6.1 | 6.19 | 6.31 | 6.44 | 6.62 | 6.82
| MISO_IN | Summer | 4.33 | 4.11 | 4.17 | 4.12 | 4.23 | 4.22 | 4.3 | 4.4 | 4.35 | 4.44 | 4.55 | 4.67 | 4.83 | 4.97 | 5.11 | 5.22 | 5.34 | 5.43 | 5.49 | 5.57 | 5.66 | 5.78 | 5.91 | 6.06 | 6.22
| MISO_IN | Winter | 4.62 | 4.51 | 4.59 | 4.56 | 4.68 | 4.66 | 4.76 | 4.87 | 4.81 | 4.91 | 5.04 | 5.17 | 5.34 | 5.5 | 5.65 | 5.79 | 5.91 | 6.02 | 6.08 | 6.17 | 6.27 | 6.41 | 6.54 | 6.71 | 6.89
| MISO_IN | Shoulder | 4.42 | 4.25 | 4.31 | 4.27 | 4.39 | 4.37 | 4.46 | 4.56 | 4.51 | 4.6 | 4.72 | 4.84 | 5.01 | 5.15 | 5.29 | 5.42 | 5.54 | 5.63 | 5.7 | 5.77 | 5.87 | 6 | 6.13 | 6.29 | 6.44
| MISO_MI | Summer | 4.19 | 3.99 | 3.94 | 3.89 | 3.98 | 4.07 | 4.18 | 4.27 | 4.34 | 4.45 | 4.55 | 4.67 | 4.82 | 4.96 | 5.1 | 5.21 | 5.32 | 5.43 | 5.5 | 5.58 | 5.67 | 5.8 | 5.93 | 6.09 | 6.25
| MISO_MI | Winter | 4.3 | 4.23 | 4.24 | 4.21 | 4.31 | 4.42 | 4.53 | 4.62 | 4.7 | 4.81 | 4.93 | 5.06 | 5.23 | 5.37 | 5.52 | 5.64 | 5.77 | 5.88 | 5.95 | 6.04 | 6.14 | 6.27 | 6.43 | 6.59 | 6.77
| MISO_MI | Shoulder | 4.23 | 4.05 | 4.03 | 3.98 | 4.07 | 4.17 | 4.28 | 4.38 | 4.44 | 4.56 | 4.67 | 4.79 | 4.95 | 5.09 | 5.22 | 5.34 | 5.46 | 5.56 | 5.63 | 5.71 | 5.82 | 5.94 | 6.08 | 6.24 | 6.4
| MISO_MO_IL | Summer | 4.28 | 4.09 | 4.04 | 3.98 | 4.06 | 4.23 | 4.31 | 4.37 | 4.45 | 4.47 | 4.61 | 4.67 | 4.83 | 4.96 | 5.16 | 5.27 | 5.39 | 5.53 | 5.64 | 5.71 | 5.8 | 5.93 | 6.05 | 6.21 | 6.38
| MISO_MO_IL | Winter | 4.62 | 4.49 | 4.46 | 4.42 | 4.51 | 4.69 | 4.78 | 4.85 | 4.95 | 4.98 | 5.12 | 5.2 | 5.37 | 5.52 | 5.74 | 5.85 | 5.98 | 6.15 | 6.26 | 6.35 | 6.46 | 6.59 | 6.73 | 6.9 | 7.1
| MISO_MO_IL | Shoulder | 4.39 | 4.23 | 4.18 | 4.13 | 4.22 | 4.38 | 4.47 | 4.54 | 4.62 | 4.65 | 4.78 | 4.86 | 5.02 | 5.15 | 5.36 | 5.48 | 5.59 | 5.75 | 5.85 | 5.93 | 6.03 | 6.16 | 6.29 | 6.45 | 6.64
| MISO_W | Summer | 4.23 | 4.05 | 4 | 3.94 | 4.02 | 4.14 | 4.25 | 4.37 | 4.49 | 4.62 | 4.74 | 4.85 | 5 | 5.15 | 5.33 | 5.45 | 5.56 | 5.66 | 5.76 | 5.85 | 5.94 | 6.05 | 6.18 | 6.34 | 6.54
| MISO_W | Winter | 4.59 | 4.45 | 4.45 | 4.41 | 4.5 | 4.63 | 4.76 | 4.9 | 5.03 | 5.17 | 5.31 | 5.44 | 5.61 | 5.78 | 5.98 | 6.11 | 6.24 | 6.36 | 6.47 | 6.56 | 6.67 | 6.79 | 6.94 | 7.13 | 7.35
| MISO_W | Shoulder | 4.38 | 4.2 | 4.16 | 4.1 | 4.19 | 4.31 | 4.43 | 4.56 | 4.67 | 4.8 | 4.94 | 5.06 | 5.21 | 5.37 | 5.56 | 5.68 | 5.79 | 5.91 | 6 | 6.1 | 6.2 | 6.31 | 6.44 | 6.62 | 6.83
| MISO_WUMS | Summer | 4.12 | 3.92 | 3.9 | 3.85 | 3.93 | 4.03 | 4.14 | 4.22 | 4.29 | 4.4 | 4.5 | 4.62 | 4.77 | 4.9 | 5.04 | 5.15 | 5.27 | 5.37 | 5.44 | 5.52 | 5.61 | 5.73 | 5.87 | 6.02 | 6.18
| MISO_WUMS | Winter | 4.4 | 4.3 | 4.29 | 4.26 | 4.35 | 4.46 | 4.58 | 4.68 | 4.75 | 4.87 | 4.99 | 5.12 | 5.28 | 5.44 | 5.58 | 5.71 | 5.83 | 5.95 | 6.02 | 6.11 | 6.22 | 6.35 | 6.5 | 6.67 | 6.85
| MISO_WUMS | Shoulder | 4.21 | 4.06 | 4.03 | 3.99 | 4.08 | 4.18 | 4.29 | 4.38 | 4.45 | 4.56 | 4.67 | 4.79 | 4.95 | 5.09 | 5.23 | 5.34 | 5.46 | 5.57 | 5.64 | 5.72 | 5.81 | 5.94 | 6.08 | 6.25 | 6.41
| NE | Summer | 4.23 | 4.05 | 4 | 3.94 | 4.03 | 4.14 | 4.26 | 4.38 | 4.5 | 4.62 | 4.75 | 4.86 | 5.01 | 5.16 | 5.35 | 5.46 | 5.57 | 5.68 | 5.77 | 5.86 | 5.96 | 6.07 | 6.19 | 6.37 | 6.57
| NE | Winter | 4.6 | 4.45 | 4.44 | 4.4 | 4.49 | 4.62 | 4.75 | 4.88 | 5.01 | 5.15 | 5.3 | 5.42 | 5.59 | 5.75 | 5.96 | 6.1 | 6.22 | 6.33 | 6.44 | 6.54 | 6.65 | 6.76 | 6.91 | 7.1 | 7.32
| NE | Shoulder | 4.36 | 4.2 | 4.16 | 4.1 | 4.19 | 4.31 | 4.43 | 4.56 | 4.68 | 4.81 | 4.94 | 5.06 | 5.21 | 5.37 | 5.57 | 5.68 | 5.8 | 5.91 | 6.01 | 6.1 | 6.2 | 6.31 | 6.45 | 6.62 | 6.83
| NEISO | Summer | 3.76 | 4.11 | 4.42 | 4.53 | 4.4 | 4.25 | 4.25 | 4.28 | 4.29 | 4.3 | 4.33 | 4.39 | 4.5 | 4.56 | 4.68 | 4.72 | 4.79 | 4.88 | 4.96 | 5.07 | 5.16 | 5.25 | 5.33 | 5.39 | 5.38
| NEISO | Winter | 6.54 | 5.8 | 5.94 | 6.11 | 5.95 | 5.74 | 5.75 | 5.8 | 5.81 | 5.84 | 5.87 | 5.96 | 6.12 | 6.21 | 6.36 | 6.44 | 6.52 | 6.65 | 6.77 | 6.91 | 7.04 | 7.16 | 7.27 | 7.35 | 7.34
| NEISO | Shoulder | 4.08 | 4.5 | 4.78 | 4.91 | 4.77 | 4.61 | 4.62 | 4.65 | 4.66 | 4.68 | 4.7 | 4.77 | 4.89 | 4.97 | 5.09 | 5.14 | 5.21 | 5.31 | 5.41 | 5.52 | 5.62 | 5.72 | 5.8 | 5.87 | 5.86
| NonRTO_midwest | Summer | 4.79 | 4.67 | 4.69 | 4.65 | 4.72 | 4.8 | 4.83 | 4.89 | 4.93 | 5.02 | 5.16 | 5.27 | 5.43 | 5.59 | 5.73 | 5.86 | 5.97 | 6.03 | 6.06 | 6.11 | 6.22 | 6.34 | 6.45 | 6.59 | 6.79
| NonRTO_midwest | Winter | 5.12 | 5.09 | 5.17 | 5.15 | 5.22 | 5.3 | 5.36 | 5.41 | 5.45 | 5.55 | 5.71 | 5.83 | 6 | 6.18 | 6.34 | 6.47 | 6.6 | 6.66 | 6.7 | 6.75 | 6.87 | 7.02 | 7.14 | 7.29 | 7.51
| NonRTO_midwest | Shoulder | 4.88 | 4.81 | 4.86 | 4.83 | 4.89 | 4.97 | 5.02 | 5.08 | 5.11 | 5.2 | 5.35 | 5.46 | 5.63 | 5.79 | 5.94 | 6.07 | 6.19 | 6.25 | 6.28 | 6.34 | 6.44 | 6.58 | 6.69 | 6.82 | 7.03
| NP15 | Summer | 4.87 | 4.65 | 4.61 | 4.52 | 4.55 | 4.62 | 4.79 | 4.97 | 5.15 | 5.26 | 5.44 | 5.63 | 5.76 | 5.91 | 6.05 | 6.19 | 6.31 | 6.44 | 6.54 | 6.63 | 6.71 | 6.83 | 6.96 | 7.12 | 7.33
| NP15 | Winter | 5 | 4.97 | 4.99 | 4.93 | 4.96 | 5.03 | 5.22 | 5.42 | 5.61 | 5.73 | 5.93 | 6.13 | 6.28 | 6.45 | 6.6 | 6.75 | 6.88 | 7.01 | 7.13 | 7.22 | 7.32 | 7.44 | 7.59 | 7.77 | 7.99
| NP15 | Shoulder | 4.92 | 4.74 | 4.72 | 4.65 | 4.67 | 4.74 | 4.92 | 5.11 | 5.28 | 5.4 | 5.58 | 5.77 | 5.91 | 6.07 | 6.22 | 6.36 | 6.48 | 6.61 | 6.71 | 6.8 | 6.9 | 7.01 | 7.15 | 7.32 | 7.53
| NWPP_Gas | Summer | 4.15 | 3.94 | 3.89 | 3.77 | 3.88 | 4.18 | 4.35 | 4.5 | 4.61 | 4.74 | 4.87 | 5.04 | 5.24 | 5.37 | 5.49 | 5.59 | 5.7 | 5.82 | 5.93 | 6.03 | 6.13 | 6.24 | 6.39 | 6.59 | 6.79
| NWPP_Gas | Winter | 4.56 | 4.46 | 4.47 | 4.35 | 4.49 | 4.83 | 5.02 | 5.19 | 5.33 | 5.48 | 5.63 | 5.84 | 6.06 | 6.2 | 6.35 | 6.47 | 6.59 | 6.73 | 6.86 | 6.98 | 7.1 | 7.23 | 7.4 | 7.62 | 7.86
| NWPP_Gas | Shoulder | 4.29 | 4.14 | 4.12 | 3.99 | 4.12 | 4.43 | 4.61 | 4.77 | 4.89 | 5.02 | 5.16 | 5.35 | 5.55 | 5.69 | 5.82 | 5.93 | 6.04 | 6.17 | 6.29 | 6.4 | 6.5 | 6.62 | 6.78 | 6.98 | 7.2
| NYISO_A-F | Summer | 4.86 | 4.87 | 5.16 | 5.37 | 5.3 | 4.96 | 4.9 | 4.87 | 4.83 | 4.8 | 4.81 | 4.86 | 4.98 | 5.06 | 5.23 | 5.3 | 5.39 | 5.5 | 5.58 | 5.71 | 5.82 | 5.93 | 6.01 | 6.08 | 6.09
| NYISO_A-F | Winter | 5.21 | 5.32 | 5.72 | 5.96 | 5.88 | 5.49 | 5.42 | 5.39 | 5.33 | 5.29 | 5.3 | 5.35 | 5.48 | 5.57 | 5.74 | 5.81 | 5.91 | 6.02 | 6.11 | 6.25 | 6.37 | 6.48 | 6.58 | 6.64 | 6.64
| NYISO_A-F | Shoulder | 4.99 | 5.03 | 5.37 | 5.59 | 5.51 | 5.15 | 5.08 | 5.06 | 5.01 | 4.97 | 4.98 | 5.04 | 5.15 | 5.23 | 5.4 | 5.47 | 5.57 | 5.68 | 5.76 | 5.89 | 6.01 | 6.11 | 6.2 | 6.26 | 6.27
| NYISO_G-I | Summer | 4.14 | 4.47 | 4.83 | 5.04 | 4.97 | 4.65 | 4.59 | 4.56 | 4.52 | 4.48 | 4.5 | 4.55 | 4.66 | 4.74 | 4.89 | 4.95 | 5.04 | 5.13 | 5.22 | 5.33 | 5.44 | 5.54 | 5.62 | 5.67 | 5.68
| NYISO_G-I | Winter | 6.5 | 5.96 | 6.24 | 6.5 | 6.4 | 5.98 | 5.91 | 5.88 | 5.83 | 5.78 | 5.79 | 5.85 | 5.98 | 6.08 | 6.28 | 6.36 | 6.47 | 6.59 | 6.69 | 6.84 | 6.97 | 7.09 | 7.2 | 7.28 | 7.28
| NYISO_G-I | Shoulder | 4.46 | 4.85 | 5.21 | 5.43 | 5.36 | 5.01 | 4.95 | 4.92 | 4.87 | 4.84 | 4.84 | 4.89 | 5.01 | 5.09 | 5.26 | 5.33 | 5.42 | 5.52 | 5.6 | 5.74 | 5.84 | 5.95 | 6.03 | 6.1 | 6.1
| NYISO_J-K | Summer | 3.88 | 4.28 | 4.67 | 4.86 | 4.79 | 4.48 | 4.42 | 4.4 | 4.36 | 4.32 | 4.33 | 4.38 | 4.48 | 4.55 | 4.7 | 4.76 | 4.84 | 4.94 | 5.01 | 5.12 | 5.22 | 5.31 | 5.39 | 5.45 | 5.45
| NYISO_J-K | Winter | 7.03 | 6.3 | 6.54 | 6.83 | 6.73 | 6.3 | 6.22 | 6.18 | 6.13 | 6.08 | 6.09 | 6.15 | 6.3 | 6.4 | 6.62 | 6.7 | 6.82 | 6.95 | 7.05 | 7.21 | 7.35 | 7.48 | 7.59 | 7.67 | 7.68
| NYISO_J-K | Shoulder | 4.19 | 4.71 | 5.08 | 5.29 | 5.22 | 4.88 | 4.82 | 4.79 | 4.75 | 4.71 | 4.72 | 4.77 | 4.88 | 4.96 | 5.12 | 5.19 | 5.28 | 5.37 | 5.46 | 5.59 | 5.69 | 5.79 | 5.88 | 5.94 | 5.95
| OH | Summer | 4.85 | 4.86 | 5.16 | 5.37 | 5.3 | 4.96 | 4.9 | 4.89 | 4.85 | 4.81 | 4.83 | 4.88 | 5 | 5.09 | 5.26 | 5.33 | 5.43 | 5.53 | 5.62 | 5.75 | 5.87 | 5.97 | 6.06 | 6.13 | 6.14
| OH | Winter | 5.22 | 5.33 | 5.72 | 5.97 | 5.88 | 5.49 | 5.42 | 5.38 | 5.32 | 5.27 | 5.29 | 5.33 | 5.46 | 5.54 | 5.71 | 5.78 | 5.87 | 5.98 | 6.07 | 6.21 | 6.32 | 6.43 | 6.52 | 6.58 | 6.59
| OH | Shoulder | 4.98 | 5.03 | 5.36 | 5.58 | 5.5 | 5.15 | 5.08 | 5.05 | 5 | 4.96 | 4.97 | 5.02 | 5.14 | 5.23 | 5.39 | 5.46 | 5.56 | 5.66 | 5.75 | 5.88 | 6 | 6.1 | 6.19 | 6.25 | 6.26
| PJM_E | Summer | 4.26 | 4.64 | 4.98 | 5.04 | 5.07 | 4.82 | 4.77 | 4.75 | 4.72 | 4.71 | 4.73 | 4.79 | 4.91 | 5 | 5.15 | 5.23 | 5.32 | 5.43 | 5.5 | 5.61 | 5.72 | 5.81 | 5.9 | 5.96 | 5.97
| PJM_E | Winter | 6.46 | 5.87 | 6.1 | 6.16 | 6.17 | 5.87 | 5.8 | 5.78 | 5.74 | 5.72 | 5.75 | 5.81 | 5.95 | 6.07 | 6.25 | 6.34 | 6.45 | 6.58 | 6.67 | 6.81 | 6.92 | 7.04 | 7.14 | 7.21 | 7.22
| PJM_E | Shoulder | 4.6 | 4.99 | 5.32 | 5.38 | 5.4 | 5.14 | 5.08 | 5.06 | 5.03 | 5.01 | 5.04 | 5.1 | 5.22 | 5.32 | 5.48 | 5.56 | 5.66 | 5.77 | 5.85 | 5.97 | 6.07 | 6.17 | 6.27 | 6.34 | 6.34
| PJM_ROM | Summer | 4.38 | 4.7 | 5.02 | 5.09 | 5.11 | 4.86 | 4.8 | 4.79 | 4.76 | 4.74 | 4.77 | 4.82 | 4.95 | 5.04 | 5.19 | 5.27 | 5.36 | 5.47 | 5.55 | 5.66 | 5.76 | 5.85 | 5.94 | 6.01 | 6.01
| PJM_ROM | Winter | 6.25 | 5.77 | 6.04 | 6.09 | 6.11 | 5.81 | 5.75 | 5.73 | 5.68 | 5.66 | 5.69 | 5.76 | 5.9 | 6.01 | 6.19 | 6.28 | 6.39 | 6.51 | 6.61 | 6.74 | 6.86 | 6.97 | 7.08 | 7.15 | 7.15
| PJM_ROM | Shoulder | 4.67 | 5.01 | 5.33 | 5.4 | 5.42 | 5.16 | 5.1 | 5.08 | 5.04 | 5.02 | 5.05 | 5.11 | 5.23 | 5.33 | 5.5 | 5.58 | 5.67 | 5.78 | 5.87 | 5.98 | 6.09 | 6.2 | 6.28 | 6.35 | 6.36
| PJM_ROR | Summer | 4.21 | 4.08 | 4.14 | 4.09 | 4.2 | 4.19 | 4.28 | 4.37 | 4.32 | 4.41 | 4.52 | 4.64 | 4.8 | 4.94 | 5.07 | 5.19 | 5.31 | 5.4 | 5.46 | 5.53 | 5.62 | 5.75 | 5.87 | 6.03 | 6.18
| PJM_ROR | Winter | 4.83 | 4.57 | 4.64 | 4.6 | 4.72 | 4.71 | 4.81 | 4.92 | 4.86 | 4.96 | 5.08 | 5.22 | 5.4 | 5.55 | 5.7 | 5.84 | 5.96 | 6.07 | 6.14 | 6.22 | 6.32 | 6.46 | 6.6 | 6.77 | 6.95
| PJM_ROR | Shoulder | 4.33 | 4.23 | 4.3 | 4.26 | 4.38 | 4.36 | 4.45 | 4.55 | 4.5 | 4.59 | 4.71 | 4.83 | 5 | 5.14 | 5.28 | 5.4 | 5.52 | 5.62 | 5.68 | 5.76 | 5.86 | 5.98 | 6.11 | 6.27 | 6.43
| RMPA | Summer | 4.5 | 4.34 | 4.31 | 4.25 | 4.31 | 4.42 | 4.53 | 4.67 | 4.79 | 4.93 | 5.07 | 5.25 | 5.4 | 5.53 | 5.63 | 5.77 | 5.92 | 6.06 | 6.16 | 6.25 | 6.34 | 6.45 | 6.56 | 6.73 | 6.92
| RMPA | Winter | 4.84 | 4.78 | 4.82 | 4.77 | 4.83 | 4.96 | 5.08 | 5.24 | 5.39 | 5.54 | 5.69 | 5.89 | 6.06 | 6.21 | 6.33 | 6.49 | 6.65 | 6.81 | 6.92 | 7.02 | 7.12 | 7.25 | 7.38 | 7.56 | 7.78
| RMPA | Shoulder | 4.6 | 4.49 | 4.49 | 4.43 | 4.48 | 4.61 | 4.72 | 4.87 | 5 | 5.14 | 5.28 | 5.47 | 5.63 | 5.77 | 5.87 | 6.02 | 6.18 | 6.32 | 6.42 | 6.52 | 6.61 | 6.73 | 6.85 | 7.02 | 7.22
| SOCO | Summer | 4.98 | 4.77 | 4.84 | 4.82 | 4.86 | 4.92 | 4.93 | 4.98 | 5 | 5.09 | 5.23 | 5.34 | 5.5 | 5.66 | 5.81 | 5.92 | 6.05 | 6.1 | 6.15 | 6.18 | 6.32 | 6.45 | 6.56 | 6.7 | 6.9
| SOCO | Winter | 5.14 | 5.14 | 5.29 | 5.29 | 5.33 | 5.4 | 5.41 | 5.46 | 5.49 | 5.59 | 5.73 | 5.86 | 6.03 | 6.2 | 6.36 | 6.49 | 6.63 | 6.69 | 6.74 | 6.79 | 6.94 | 7.08 | 7.2 | 7.35 | 7.56
| SOCO | Shoulder | 5.04 | 4.89 | 4.99 | 4.97 | 5.01 | 5.08 | 5.09 | 5.14 | 5.16 | 5.25 | 5.4 | 5.51 | 5.67 | 5.84 | 5.98 | 6.12 | 6.23 | 6.3 | 6.34 | 6.38 | 6.52 | 6.66 | 6.77 | 6.91 | 7.11
| SP15 | Summer | 4.84 | 4.62 | 4.58 | 4.5 | 4.53 | 4.59 | 4.76 | 4.96 | 5.13 | 5.24 | 5.42 | 5.6 | 5.73 | 5.89 | 6.02 | 6.16 | 6.28 | 6.41 | 6.51 | 6.6 | 6.68 | 6.79 | 6.93 | 7.09 | 7.3
| SP15 | Winter | 5.05 | 4.99 | 5.02 | 4.96 | 4.98 | 5.06 | 5.24 | 5.44 | 5.63 | 5.76 | 5.96 | 6.16 | 6.31 | 6.47 | 6.63 | 6.78 | 6.91 | 7.05 | 7.16 | 7.26 | 7.36 | 7.48 | 7.62 | 7.8 | 8.03
| SP15 | Shoulder | 4.91 | 4.74 | 4.73 | 4.65 | 4.68 | 4.74 | 4.93 | 5.11 | 5.29 | 5.4 | 5.59 | 5.78 | 5.92 | 6.07 | 6.22 | 6.36 | 6.49 | 6.62 | 6.72 | 6.81 | 6.9 | 7.01 | 7.16 | 7.32 | 7.53
| SPP_N | Summer | 4.44 | 4.23 | 4.15 | 4.08 | 4.16 | 4.3 | 4.44 | 4.56 | 4.64 | 4.77 | 4.89 | 5.05 | 5.22 | 5.36 | 5.5 | 5.61 | 5.72 | 5.82 | 5.92 | 6 | 6.09 | 6.2 | 6.33 | 6.5 | 6.7
| SPP_N | Winter | 4.66 | 4.59 | 4.57 | 4.52 | 4.61 | 4.77 | 4.93 | 5.06 | 5.15 | 5.29 | 5.43 | 5.6 | 5.79 | 5.95 | 6.1 | 6.22 | 6.34 | 6.46 | 6.57 | 6.66 | 6.76 | 6.88 | 7.02 | 7.2 | 7.43
| SPP_N | Shoulder | 4.5 | 4.34 | 4.29 | 4.22 | 4.3 | 4.47 | 4.61 | 4.72 | 4.82 | 4.95 | 5.08 | 5.23 | 5.41 | 5.57 | 5.7 | 5.82 | 5.93 | 6.04 | 6.15 | 6.23 | 6.31 | 6.42 | 6.56 | 6.74 | 6.94
| SPP_S | Summer | 4.54 | 4.38 | 4.39 | 4.32 | 4.4 | 4.49 | 4.55 | 4.62 | 4.68 | 4.8 | 4.93 | 5.06 | 5.21 | 5.36 | 5.49 | 5.61 | 5.73 | 5.8 | 5.83 | 5.88 | 6 | 6.14 | 6.23 | 6.37 | 6.56
| SPP_S | Winter | 4.77 | 4.75 | 4.84 | 4.79 | 4.88 | 4.98 | 5.05 | 5.13 | 5.2 | 5.32 | 5.47 | 5.61 | 5.78 | 5.95 | 6.09 | 6.22 | 6.35 | 6.43 | 6.47 | 6.53 | 6.66 | 6.81 | 6.91 | 7.07 | 7.28
| SPP_S | Shoulder | 4.61 | 4.5 | 4.54 | 4.48 | 4.56 | 4.66 | 4.72 | 4.79 | 4.86 | 4.98 | 5.11 | 5.24 | 5.4 | 5.56 | 5.69 | 5.82 | 5.94 | 6.01 | 6.05 | 6.1 | 6.22 | 6.36 | 6.46 | 6.61 | 6.8
| TVA | Summer | 4.81 | 4.66 | 4.69 | 4.66 | 4.72 | 4.8 | 4.84 | 4.9 | 4.94 | 5.03 | 5.17 | 5.28 | 5.44 | 5.6 | 5.75 | 5.88 | 5.99 | 6.05 | 6.09 | 6.14 | 6.24 | 6.37 | 6.49 | 6.62 | 6.83
| TVA | Winter | 5.06 | 5.09 | 5.17 | 5.15 | 5.22 | 5.3 | 5.35 | 5.41 | 5.44 | 5.54 | 5.69 | 5.81 | 5.98 | 6.16 | 6.32 | 6.45 | 6.58 | 6.64 | 6.67 | 6.73 | 6.84 | 6.98 | 7.1 | 7.24 | 7.46
| TVA | Shoulder | 4.91 | 4.81 | 4.86 | 4.82 | 4.89 | 4.97 | 5.02 | 5.07 | 5.11 | 5.2 | 5.35 | 5.46 | 5.63 | 5.79 | 5.93 | 6.07 | 6.18 | 6.24 | 6.28 | 6.33 | 6.44 | 6.57 | 6.68 | 6.82 | 7.03
| VACAR | Summer | 5.16 | 5.19 | 5.27 | 5.07 | 5.14 | 5.23 | 5.32 | 5.38 | 5.43 | 5.5 | 5.61 | 5.71 | 5.85 | 6.02 | 6.16 | 6.29 | 6.43 | 6.53 | 6.61 | 6.66 | 6.75 | 6.85 | 6.96 | 7.07 | 7.22
| VACAR | Winter | 6.41 | 6 | 6.03 | 5.8 | 5.89 | 5.99 | 6.09 | 6.15 | 6.21 | 6.31 | 6.41 | 6.53 | 6.71 | 6.9 | 7.06 | 7.21 | 7.37 | 7.49 | 7.57 | 7.63 | 7.74 | 7.85 | 7.97 | 8.11 | 8.28
| VACAR | Shoulder | 5.35 | 5.43 | 5.5 | 5.29 | 5.37 | 5.47 | 5.55 | 5.61 | 5.67 | 5.75 | 5.85 | 5.96 | 6.12 | 6.29 | 6.44 | 6.57 | 6.72 | 6.83 | 6.9 | 6.97 | 7.05 | 7.16 | 7.27 | 7.39 | 7.55
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit16C_AEORegionGasPrices
Appendix A, Exhibit 16C - AEO2011 Regional Gas Prices
The data below is the regional natural gas prices for the electricity sector from the AEO2011 preliminary reference scenario dated 12/08/2010 (d120810c)
These have been updated to 2010 $/mmbtu from the AEO2011 reported 2009$/mmbtu using a GDP deflator value between 2009 and 2010 of 1.00876
Natural Gas Prices (2010 dollars per million Btu)
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
ERCT | 8.88 | 3.95 | 4.95 | 4.63 | 4.54 | 4.58 | 4.52 | 4.6 | 4.7 | 4.76 | 4.84 | 4.89 | 5.01 | 5.15 | 5.28 | 5.44 | 5.6 | 5.74 | 5.86 | 5.98 | 6.05 | 6.09 | 6.14 | 6.26 | 6.4 | 6.5 | 6.65 | 6.85
FRCC | 10.35 | 7.7 | 6.68 | 5.77 | 5.66 | 5.62 | 5.57 | 5.62 | 5.68 | 5.74 | 5.79 | 5.84 | 5.95 | 6.07 | 6.23 | 6.41 | 6.61 | 6.78 | 6.9 | 7.03 | 7.09 | 7.14 | 7.2 | 7.31 | 7.44 | 7.56 | 7.7 | 7.92
MROE | 9.18 | 4.58 | 4.66 | 4.24 | 4.09 | 4.06 | 4.02 | 4.11 | 4.21 | 4.32 | 4.41 | 4.49 | 4.59 | 4.71 | 4.83 | 4.99 | 5.13 | 5.27 | 5.38 | 5.5 | 5.61 | 5.68 | 5.77 | 5.86 | 5.99 | 6.13 | 6.29 | 6.46
MROW | 8.76 | 4.65 | 4.79 | 4.39 | 4.22 | 4.19 | 4.13 | 4.22 | 4.34 | 4.47 | 4.59 | 4.71 | 4.85 | 4.98 | 5.1 | 5.26 | 5.41 | 5.61 | 5.73 | 5.84 | 5.95 | 6.05 | 6.15 | 6.25 | 6.36 | 6.5 | 6.67 | 6.88
NEWE | 10.29 | 4.86 | 5.17 | 4.77 | 4.77 | 5.02 | 5.15 | 5.01 | 4.84 | 4.84 | 4.88 | 4.89 | 4.91 | 4.94 | 5.01 | 5.14 | 5.21 | 5.34 | 5.4 | 5.47 | 5.58 | 5.68 | 5.8 | 5.91 | 6 | 6.09 | 6.16 | 6.15
NYCW | 10.65 | 4.99 | 5.19 | 5.01 | 5.06 | 5.4 | 5.62 | 5.54 | 5.18 | 5.12 | 5.09 | 5.04 | 5 | 5.02 | 5.07 | 5.19 | 5.27 | 5.44 | 5.51 | 5.61 | 5.72 | 5.8 | 5.94 | 6.05 | 6.16 | 6.25 | 6.31 | 6.32
NYLI | 10.65 | 4.99 | 5.19 | 5.01 | 5.06 | 5.4 | 5.62 | 5.54 | 5.18 | 5.12 | 5.09 | 5.04 | 5 | 5.02 | 5.07 | 5.19 | 5.27 | 5.44 | 5.51 | 5.61 | 5.72 | 5.8 | 5.94 | 6.05 | 6.16 | 6.25 | 6.31 | 6.32
NYUP | 10.65 | 4.99 | 5.19 | 5.01 | 5.06 | 5.4 | 5.62 | 5.54 | 5.18 | 5.12 | 5.09 | 5.04 | 5 | 5.02 | 5.07 | 5.19 | 5.27 | 5.44 | 5.51 | 5.61 | 5.72 | 5.8 | 5.94 | 6.05 | 6.16 | 6.25 | 6.31 | 6.32
RFCE | 10.67 | 4.99 | 5.28 | 5.08 | 5.14 | 5.44 | 5.5 | 5.52 | 5.25 | 5.19 | 5.18 | 5.14 | 5.12 | 5.15 | 5.21 | 5.34 | 5.43 | 5.6 | 5.68 | 5.78 | 5.9 | 5.98 | 6.1 | 6.21 | 6.31 | 6.41 | 6.47 | 6.48
RFCM | 9.18 | 4.58 | 4.66 | 4.24 | 4.09 | 4.06 | 4.02 | 4.11 | 4.21 | 4.32 | 4.41 | 4.49 | 4.6 | 4.71 | 4.83 | 4.99 | 5.13 | 5.27 | 5.38 | 5.5 | 5.61 | 5.68 | 5.77 | 5.86 | 5.99 | 6.13 | 6.29 | 6.46
RFCW | 9.52 | 4.47 | 4.89 | 4.45 | 4.28 | 4.34 | 4.3 | 4.42 | 4.4 | 4.5 | 4.6 | 4.54 | 4.64 | 4.75 | 4.88 | 5.05 | 5.19 | 5.34 | 5.46 | 5.58 | 5.68 | 5.74 | 5.82 | 5.91 | 6.04 | 6.17 | 6.34 | 6.5
SRDA | 8.98 | 4 | 4.98 | 4.66 | 4.57 | 4.62 | 4.56 | 4.65 | 4.74 | 4.79 | 4.87 | 4.93 | 5.04 | 5.18 | 5.3 | 5.46 | 5.62 | 5.77 | 5.89 | 6.02 | 6.08 | 6.12 | 6.17 | 6.3 | 6.44 | 6.54 | 6.69 | 6.88
SRGW | 8.95 | 4.27 | 4.79 | 4.42 | 4.26 | 4.22 | 4.16 | 4.25 | 4.42 | 4.5 | 4.57 | 4.66 | 4.69 | 4.82 | 4.89 | 5.06 | 5.2 | 5.4 | 5.52 | 5.63 | 5.79 | 5.9 | 5.98 | 6.08 | 6.21 | 6.34 | 6.5 | 6.69
SRSE | 9.93 | 4.37 | 5.5 | 5.05 | 4.92 | 5.03 | 5.02 | 5.06 | 5.12 | 5.13 | 5.18 | 5.2 | 5.3 | 5.44 | 5.55 | 5.72 | 5.88 | 6.03 | 6.16 | 6.29 | 6.35 | 6.39 | 6.43 | 6.58 | 6.71 | 6.83 | 6.97 | 7.17
SRCE | 9.84 | 4.3 | 5.28 | 4.92 | 4.84 | 4.89 | 4.86 | 4.93 | 5.01 | 5.06 | 5.11 | 5.15 | 5.24 | 5.39 | 5.5 | 5.67 | 5.83 | 5.99 | 6.12 | 6.24 | 6.3 | 6.33 | 6.38 | 6.49 | 6.63 | 6.74 | 6.88 | 7.09
SRVC | 10.74 | 4.97 | 6.05 | 5.62 | 5.52 | 5.58 | 5.37 | 5.45 | 5.54 | 5.63 | 5.7 | 5.75 | 5.83 | 5.94 | 6.05 | 6.21 | 6.38 | 6.53 | 6.67 | 6.81 | 6.93 | 7 | 7.06 | 7.16 | 7.26 | 7.37 | 7.5 | 7.66
SPNO | 8.64 | 4.68 | 4.88 | 4.53 | 4.38 | 4.33 | 4.26 | 4.34 | 4.5 | 4.64 | 4.77 | 4.86 | 4.99 | 5.12 | 5.28 | 5.46 | 5.61 | 5.75 | 5.87 | 5.98 | 6.09 | 6.19 | 6.28 | 6.37 | 6.48 | 6.62 | 6.79 | 7
SPSO | 8.86 | 3.99 | 4.94 | 4.63 | 4.54 | 4.58 | 4.51 | 4.6 | 4.69 | 4.76 | 4.84 | 4.9 | 5.02 | 5.15 | 5.29 | 5.45 | 5.61 | 5.74 | 5.87 | 5.99 | 6.06 | 6.1 | 6.15 | 6.27 | 6.42 | 6.51 | 6.66 | 6.86
AZNM | 8.05 | 4.75 | 4.76 | 4.61 | 4.47 | 4.46 | 4.43 | 4.47 | 4.6 | 4.72 | 4.89 | 5.04 | 5.17 | 5.33 | 5.53 | 5.67 | 5.81 | 5.91 | 6.04 | 6.19 | 6.32 | 6.43 | 6.53 | 6.62 | 6.74 | 6.88 | 7.04 | 7.21
CAMX | 7.99 | 4.29 | 5.23 | 4.92 | 4.78 | 4.76 | 4.69 | 4.72 | 4.79 | 4.96 | 5.16 | 5.34 | 5.45 | 5.64 | 5.83 | 5.97 | 6.13 | 6.28 | 6.42 | 6.54 | 6.67 | 6.78 | 6.87 | 6.96 | 7.08 | 7.22 | 7.38 | 7.6
NWPP | 7.52 | 4.63 | 4.23 | 4.32 | 4.16 | 4.14 | 4.02 | 4.14 | 4.46 | 4.64 | 4.8 | 4.92 | 5.06 | 5.2 | 5.39 | 5.59 | 5.73 | 5.86 | 5.97 | 6.08 | 6.21 | 6.33 | 6.44 | 6.54 | 6.66 | 6.82 | 7.03 | 7.25
RMPA | 7.7 | 4.75 | 4.75 | 4.64 | 4.52 | 4.53 | 4.47 | 4.52 | 4.65 | 4.76 | 4.91 | 5.04 | 5.19 | 5.33 | 5.52 | 5.68 | 5.82 | 5.92 | 6.07 | 6.23 | 6.37 | 6.48 | 6.57 | 6.67 | 6.79 | 6.9 | 7.08 | 7.28
US | 9.18 | 4.86 | 5.23 | 4.84 | 4.73 | 4.79 | 4.75 | 4.82 | 4.86 | 4.93 | 5 | 5.07 | 5.16 | 5.28 | 5.41 | 5.57 | 5.72 | 5.87 | 5.99 | 6.11 | 6.2 | 6.27 | 6.35 | 6.46 | 6.58 | 6.7 | 6.83 | 7
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit17_TransferLimits
Table. Transfer Limits between NEEM Regions (all limits in MW) - Transfer limits are unidirectional and should be stated as "FROM" column
C "TO" columns D through R
DESTINATION
|  | AZ_NM_SNV | ENTERGY | ERCOT | FRCC | MAPP_CA | MAPP_US | MISO_IN | MISO_MI | MISO_MO_IL | MISO_W | MISO_WUMS | NE | NEISO | Non_RTO_Midwest
ORIGIN | AZ_NM_SNV
| ENTERGY | [8 empty] | 2260
ERCOT
FRCC
| MAPP_CA | [5 empty] | 372 |  |  |  | 1970
| MAPP_US |  |  |  |  | 165 |  |  |  |  | 2635 |  | 2000
| MISO_IN | [7 empty] | 5000 | 5000 |  |  |  |  | 4800
| MISO_MI | [6 empty] | 2045 |  |  |  | 117
| MISO_MO_IL |  | 2540 |  |  |  |  | 2100 |  |  | 960
| MISO_W |  |  |  |  | 700 | 2300 |  |  | 3800 |  | 1629 | 2800
| MISO_WUMS | [7 empty] | 99 |  | 1137
| NE | [5 empty] | 1600 |  |  |  | 1600
NEISO
| Non_RTO_Midwest | [6 empty] | 4450
| NWPP | [5 empty] | 150
| NYISO__A-F | [12 empty] | 600
| NYISO_GHI | [12 empty] | 600
| NYISO_J_&_K | [12 empty] | 0
| IESO |  |  |  |  | 262 |  |  | 1840 |  | 140
PJM_Eastern_MAAC
PJM_Rest_of_MAAC
| PJM_Rest_of_RTO | [6 empty] | 909 | 1305 | 1111 | 709 | 1467
| RMPA | [5 empty] | 200 | [5 empty] | 310
| SOCO |  | 2400 |  | 3700
| SPP_N |  | 1800 | [6 empty] | 2000 | 750 |  | 330
| SPP_S | 400 | 850 | 800
| TVA |  | 3000 | [6 empty] | 4000 |  |  |  |  | 700
VACAR
Legend
Note: Non-existent links are blank.
DESTINATION
|  | NWPP | NYISO_A-F | NYISO_GHI | NYISO_J_&_K | IESO | PJM_Eastern_MAAC | PJM_Rest_of_MAAC | PJM_Rest_of_RTO | RMPA | SOCO | SPP_N | SPP_S | TVA | VACAR
ORIGIN | AZ_NM_SNV | [11 empty] | 400
| ENTERGY | [9 empty] | 2000 | 1300 | 1300 | 2100
| ERCOT | [11 empty] | 800
| FRCC | [9 empty] | 900
| MAPP_CA |  |  |  |  | 330
| MAPP_US | 200 | [7 empty] | 200
| MISO_IN | [7 empty] | 992
| MISO_MI |  |  |  |  | 1580 |  |  | 1424
| MISO_MO_IL | [7 empty] | 1212 |  |  | 2000 |  | 4000
| MISO_W |  |  |  |  | 90 |  |  | 773 |  |  | 3200
| MISO_WUMS | [7 empty] | 1600
| NE | [8 empty] | 310 |  | 1800
| NEISO |  | 600 | 600 | 430
| Non_RTO_Midwest | [12 empty] | 2400
NWPP
| NYISO__A-F |  |  | 4250 |  | 1600 |  | 1000
| NYISO_GHI |  | 1999 |  | 6130 |  | 1500
| NYISO_J_&_K |  |  | 1999
| IESO |  | 1725
| PJM_Eastern_MAAC |  |  | 500 | 330 |  |  | 8000
| PJM_Rest_of_MAAC |  | 2000 |  |  |  | 8000 |  | 8000
| PJM_Rest_of_RTO | [6 empty] | 8000 | [5 empty] | 2500 | 3000
| RMPA | [10 empty] | 210
| SOCO | [12 empty] | 2600 | 2000
| SPP_N | [8 empty] | 210 |  |  | 4000
| SPP_S | [10 empty] | 0
| TVA | [7 empty] | 2000 |  | 3200 |  |  |  | 900
| VACAR | [7 empty] | 2000 |  | 3000 |  |  | 900
Legend
Note: Non-existent links are blank.

## Exhibit18_WheelCost&TransCost
Appendix A, Exhibit 18 - Wheeling Charges, Trading Friction, and Total Hurdle
Working DRAFT | Updated 3/17/11 from CRA
From | To | Wheeling Cost 2010$/MWh | Trading Friction 2010$/MWh | Total Hurdle 2010$/MWh
ENT | MISO_MO-IL | 3 | 5 | 8
ENT | SOCO | 3 | 5 | 8
ENT | SPP_N | 3 | 5 | 8
ENT | SPP_S | 3 | 5 | 8
ENT | TVA | 3 | 5 | 8
ERCOT | SPP_S | 3 | 5 | 8
FRCC | SOCO | 3 | 5 | 8
MAPP_CA | MAPP_US | 4 | 3 | 7
MAPP_CA | MISO_W | 0 | 0 | 0
MAPP_CA | OH | 5 | 3 | 8
MAPP_US | MAPP_CA | 4 | 3 | 7
MAPP_US | MISO_W | 4 | 3 | 7
MAPP_US | NE | 4 | 3 | 7
MAPP_US | NWPP_Coal | 5 | 3 | 8
MAPP_US | RMPA | 5 | 3 | 8
MISO_IN | MISO_MI | 0 | 0 | 0
MISO_IN | MISO_MO-IL | 0 | 0 | 0
MISO_IN | NonRTO_Midwest | 5 | 3 | 8
MISO_IN | PJM_ROR | 0 | 2 | 2
MISO_MI | MISO_IN | 0 | 0 | 0
MISO_MI | MISO_WUMS | 0 | 0 | 0
MISO_MI | OH | 5 | 3 | 8
MISO_MI | PJM_ROR | 0 | 2 | 2
MISO_MO-IL | ENT | 5 | 3 | 8
MISO_MO-IL | MISO_IN | 0 | 0 | 0
MISO_MO-IL | MISO_W | 0 | 0 | 0
MISO_MO-IL | PJM ROR | 0 | 2 | 2
MISO_MO-IL | SPP_N | 5 | 3 | 8
MISO_MO-IL | TVA | 5 | 3 | 8
MISO_W | MAPP_CA | 0 | 0 | 0
MISO_W | MAPP_US | 4 | 3 | 7
MISO_W | MISO_IN | 0 | 0 | 0
MISO_W | MISO_MO-IL | 0 | 0 | 0
MISO_W | MISO_WUMS | 0 | 0 | 0
MISO_W | NE | 4 | 3 | 7
MISO_W | OH | 5 | 3 | 8
MISO_W | PJM ROR | 0 | 2 | 2
MISO_W | SPP-N | 4 | 3 | 7
MISO_WUMS | MISO_MI | 0 | 0 | 0
MISO_WUMS | MISO_W | 0 | 0 | 0
MISO_WUMS | PJM_ROR | 0 | 2 | 2
NE | MAPP_US | 2 | 3 | 5
NE | MISO_W | 2 | 3 | 5
NE | RMPA | 2 | 3 | 5
NE | SPP_N | 0 | 0 | 0
NEISO | NYISO_A-F | 0 | 3 | 3
NEISO | NYISO_GHI | 0 | 3 | 3
NEISO | NYISO_JK | 0 | 3 | 3
NonRTO_Midwest | MISO_IN | 3 | 5 | 8
NonRTO_Midwest | TVA | 3 | 5 | 8
NWPP_Coal | MAPP_US | 3 | 5 | 8
NYISO_A-F | NEISO | 0 | 3 | 3
NYISO_A-F | NYISO_GHI | 0 | 0 | 0
NYISO_A-F | OH | 4 | 3 | 7
NYISO_A-F | PJM_ROM | 5 | 3 | 8
NYISO_GHI | NEISO | 0 | 3 | 3
NYISO_GHI | NYISO_A-F | 0 | 0 | 0
NYISO_GHI | NYISO_JK | 0 | 0 | 0
NYISO_GHI | PJM_E | 5 | 3 | 8
NYISO_JK | NEISO | 0 | 3 | 3
NYISO_JK | NYISO_GHI | 0 | 0 | 0
NYISO_JK | PJM_E | 5 | 3 | 8
OH | MAPP_CA | 2 | 5 | 7
OH | MISO_MI | 2 | 5 | 7
OH | MISO_W | 2 | 5 | 7
OH | NYISO_A-F | 2 | 5 | 7
PJM_E | NYISO_GHI | 3 | 3 | 6
PJM_E | NYISO_JK | 3 | 3 | 6
PJM_E | PJM_ROM | 0 | 0 | 0
PJM_ROM | NYISO_A-F | 3 | 3 | 6
PJM_ROM | PJM_E | 0 | 0 | 0
PJM_ROM | PJM_ROR | 0 | 0 | 0
PJM_ROR | MISO_IN | 0 | 2 | 2
PJM_ROR | MISO_MI | 0 | 2 | 2
PJM_ROR | MISO_MO-IL | 0 | 2 | 2
PJM_ROR | MISO_W | 0 | 2 | 2
PJM_ROR | MISO_WUMS | 0 | 2 | 2
PJM_ROR | NonRTO_Midwest | 3 | 3 | 6
PJM_ROR | PJM_ROM | 0 | 0 | 0
PJM_ROR | TVA | 3 | 3 | 6
PJM_ROR | VACAR | 3 | 3 | 6
RMPA | MAPP_US | 3 | 5 | 8
RMPA | NE | 3 | 5 | 8
RMPA | SPP_N | 3 | 5 | 8
SOCO | ENT | 5 | 5 | 10
SOCO | FRCC | 5 | 5 | 10
SOCO | TVA | 5 | 5 | 10
SOCO | VACAR | 5 | 5 | 10
SPP_N | ENT | 2 | 3 | 5
SPP_N | MISO_MO-IL | 2 | 3 | 5
SPP_N | MISO_W | 2 | 3 | 5
SPP_N | NE | 0 | 0 | 0
SPP_N | RMPA | 2 | 3 | 5
SPP_N | SPP_S | 0 | 0 | 0
SPP_S | AZ_NM_SNV_Coal | 2 | 3 | 5
SPP_S | ENT | 2 | 3 | 5
SPP_S | ERCOT | 2 | 3 | 5
SPP_S | SPP_N | 0 | 0 | 0
TVA | ENT | 4 | 5 | 9
TVA | MISO-MO-IL | 4 | 5 | 9
TVA | NonRTO_Midwest | 4 | 5 | 9
TVA | PJM_ROR | 4 | 5 | 9
TVA | SOCO | 4 | 5 | 9
TVA | VACAR | 4 | 5 | 9
VACAR | PJM_ROR | 2 | 5 | 7
VACAR | SOCO | 2 | 5 | 7
VACAR | TVA | 2 | 5 | 7
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit19_CanadianHydro-Wind
Exhibit 19: Canadian Hydro and Wind Definitions
Existing (Baseline Infrastructure) Flows | Transfer Capacity | Annual Transfer Capacity | Details |  | Reserve Margin Credit
HQ-NE | 2920 | 0.75 | Lines used to full capacity 18 hours a day and zero capacity 6 hours a day |  | 100% (2920 MW)
HQ-NY | 1500 | 0.44 | Lines used at 1000 MW capacity 16 hours a day and zero capacity 8 hours a day |  | 80% (1200 MW)
HQ-OH | 3000 | 0.09 | Lines used at 400 MW capacity 16 hours a day and zero capacity 8 hours a day |  | 0
NB-NE | 1400 | 0.71 | Lines used to full capacity 16 hours a day and ~20% of capacity 8 hours a day (representing existing and expected wind imports) |  | 100% (1400 MW)
|  | HQ/Maritimes Pseudo Generator Definitions |  |  |  | Manitoba and Ontario Hydro are not pseudo generators
Parameter | Source/Definition | HQ/NE Hydro | HQ- New York Hydro | HQ-OH Hydro | Maritime-NE Hydro | Manitoba | Ontario
First Year Available |  | 2020 | 2020 | 2020 | 2020 | 2020 | 2020
Overnight Capital Cost ($/kW) | AEO 2011 (in 2010 dollars) | 3076 | 3076 | 3076 | 3076 | 3076 | 3800 (2010 Canadian $)
Operating Life | hydro asset life time around 100 Years | 100 | 100 | 100 | 100 | 100 | 100
8760 hr gen shape | Use normalized load shapes | Based on load shape for NEISO | Based on load shape for NY | Based on load shape for OH | Based on load shape for NEISO | Based on load shape for MISO-W | Based on load shape for OH
FOM ($/kW-year) | AEO 2011 (in 2010 dollars) (table 4) | 14.24 | 14.24 | 14.24 | 14.24 | 14.24 | 14.24
VOM ($/MWh) | AEO 2011 (in 2010 dollars) (table 4) | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | 0 (hurdle/wheel cost already accounted for in NEEM regions) | 0 (hurdle/wheel cost already accounted for in NEEM regions)
Emissions (lb/MMBtu) | AEO 2011 | 0 | 0 | 0 | 0 | 0 | 0
Reserve Margin Contribution | Based on Regional Stakeholder Input | 1 | 0.8 | 0 | 1 | 1 | 1
Resource Potential | provided by regional experts | Total possible HQ-NE by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | Total possible HQ-NE by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | Total possible HQ-OH by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | 500 MW - available 2020 | 695 (by 2020) +1495 (by2025) +2460 (by 2025) | 250 MW - available 2020
Refurb cost at end of life | EOL refurb cost of 100 year life asset won’t impact EIPC study | 0 | 0 | 0 | 0 | 0 | 0
Fixed Charge Rate | Use average EIPC FCR values for technologies as FCR spread is small | 0.112 | 0.112 | 0.112 | 0.112 | 0.112 | 0.112
Change in Capital Cost over Time | Use AEO 2010 learning rates for hydro | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Electrical Transmission ($/kW) | CRA from Exhibit 9 (based on coal plant) | 21.92 | 21.92 | 21.92 | 21.92 | 21.92 | 21.92
Regional Multiplier | For lack of data in AEO2011 assumed | 1 | 1 | 1 | 1 | 1 | 1
Parameter | Source/Definition | Martime-NE Wind
First Year Available | 2020 | 2020
Overnight Capital Cost ($/kW) | According to Exhibit 9
Operating Life | use same as other regions | 20
8760 hr gen shape | ME wind shape adjusted to account for 35% capacity factor | see below
FOM ($/kW-year) | 49k per 1.5 MW turbine year | 32.66/kw yr
VOM ($/MWh) |  | $7 - represent hurdle/wheel cost for transmision between regions
Emissions (lb/MMBtu) | AEO 2011 | 0
Reserve Margin Contribution | based on NEISO wind | 0.15
Resource Potential | per spreadsheet | 1500
Refurb cost at end of life | 20 year life as in other areas
Fixed Charge Rate | Use average EIPC FCR values for technologies | 0.118
Change in Capital Cost over Time | According to Exhibit 9
Electrical Transmission ($/kW) | According to Exhibit 9
Regional Multiplier | For lack of data in AEO2011 assumed | 1
Load Block shapes for IESO, NEISO and NYISO from Exhibit 1
| Season | Summer | [9 empty] | Shoulder |  |  |  |  | Winter |  |  |  |  | Table 3
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935 | Peak Demand
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | MW
NEISO | 2011 | 1 | 0.935 | 0.86 | 0.785 | 0.748 | 0.703 | 0.653 | 0.614 | 0.565 | 0.45 | 0.63 | 0.624 | 0.599 | 0.555 | 0.435 | 0.718 | 0.683 | 0.656 | 0.606 | 0.486 | 26043
NYISO_A-F | 2011 | 1 | 0.952 | 0.902 | 0.843 | 0.808 | 0.773 | 0.734 | 0.707 | 0.67 | 0.566 | 0.727 | 0.742 | 0.715 | 0.671 | 0.559 | 0.823 | 0.801 | 0.776 | 0.73 | 0.615 | 11504
IESO | 2011 | 1 | 0.95599 | 0.89414 | 0.85493 | 0.82517 | 0.80008 | 0.76978 | 0.73611 | 0.69934 | 0.60364 | 0.76457 | 0.78562 | 0.76078 | 0.7156 | 0.60337 | 0.88247 | 0.85828 | 0.83043 | 0.7809 | 0.65668
weighted average
| Season | Summer | [9 empty] | Shoulder |  |  |  |  | Winter
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935
| Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20
Maritimes-NEISO Wind Profile | All | 0.28 | 0.18 | 0.2 | 0.21 | 0.23 | 0.26 | 0.21 | 0.22 | 0.28 | 0.3 | 0.44 | 0.4 | 0.33 | 0.36 | 0.39 | 0.6 | 0.5 | 0.47 | 0.45 | 0.48

## Exhibit 20 Demand Response
| BAU% | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.8 | 0.7 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expanded BAU% | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NEEM Region | State to use | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
ENT | AR+LA+MS | 0.01 | 0.01 | 0.009 | 0.009 | 0.009 | 0.009 | 0.016 | 0.023 | 0.03 | 0.036 | 0.043 | 0.05 | 0.057 | 0.064 | 0.071 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078
FRCC | FL | 0.057 | 0.056 | 0.054 | 0.053 | 0.052 | 0.051 | 0.054 | 0.057 | 0.06 | 0.064 | 0.068 | 0.072 | 0.076 | 0.081 | 0.085 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089
MAPP_US | ND | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.014 | 0.018 | 0.023 | 0.027 | 0.031 | 0.036 | 0.04 | 0.044 | 0.049 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
MISO_IN | IN | 0.057 | 0.056 | 0.055 | 0.054 | 0.054 | 0.053 | 0.054 | 0.055 | 0.057 | 0.058 | 0.06 | 0.062 | 0.064 | 0.066 | 0.068 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
MISO_MI | MI | 0.088 | 0.087 | 0.086 | 0.085 | 0.083 | 0.082 | 0.086 | 0.089 | 0.093 | 0.097 | 0.101 | 0.106 | 0.11 | 0.115 | 0.119 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124 | 0.124
MISO_MO-IL | MO | 0.016 | 0.015 | 0.015 | 0.015 | 0.015 | 0.014 | 0.022 | 0.029 | 0.037 | 0.044 | 0.052 | 0.059 | 0.067 | 0.075 | 0.082 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
MISO_W | MN+IA+SD | 0.098 | 0.096 | 0.094 | 0.093 | 0.091 | 0.09 | 0.09 | 0.091 | 0.092 | 0.092 | 0.094 | 0.096 | 0.098 | 0.1 | 0.102 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104
MISO_WUMS | WI | 0.014 | 0.014 | 0.014 | 0.014 | 0.014 | 0.013 | 0.017 | 0.02 | 0.023 | 0.026 | 0.03 | 0.033 | 0.036 | 0.04 | 0.043 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047 | 0.047
NE | NE | 0.107 | 0.105 | 0.103 | 0.101 | 0.1 | 0.098 | 0.1 | 0.103 | 0.105 | 0.107 | 0.111 | 0.114 | 0.118 | 0.122 | 0.126 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129 | 0.129
NEISO | ME+NH+VT+MA+RI+CT | 0.075 | 0.107 | 0.105 | 0.104 | 0.103 | 0.102 | 0.105 | 0.108 | 0.111 | 0.115 | 0.118 | 0.122 | 0.126 | 0.13 | 0.133 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137 | 0.137
NYISO_A-F | NY | 0.081 | 0.081 | 0.08 | 0.079 | 0.078 | 0.078 | 0.078 | 0.079 | 0.08 | 0.081 | 0.083 | 0.084 | 0.086 | 0.087 | 0.089 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091
NYISO_G-I | NY | 0.081 | 0.081 | 0.08 | 0.079 | 0.078 | 0.078 | 0.078 | 0.079 | 0.08 | 0.081 | 0.083 | 0.084 | 0.086 | 0.087 | 0.089 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091
NYISO_J-K | NY | 0.081 | 0.081 | 0.08 | 0.079 | 0.078 | 0.078 | 0.078 | 0.079 | 0.08 | 0.081 | 0.083 | 0.084 | 0.086 | 0.087 | 0.089 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091
NonRTO_Midwest | KY | 0.017 | 0.017 | 0.016 | 0.016 | 0.016 | 0.016 | 0.019 | 0.023 | 0.026 | 0.03 | 0.034 | 0.038 | 0.042 | 0.046 | 0.049 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
PJM_E | NJ+DE | 0.042 | 0.041 | 0.04 | 0.04 | 0.039 | 0.038 | 0.042 | 0.045 | 0.048 | 0.052 | 0.056 | 0.059 | 0.063 | 0.067 | 0.071 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075 | 0.075
PJM_ROM | PA+MD | 0.09 | 0.088 | 0.086 | 0.084 | 0.083 | 0.082 | 0.084 | 0.086 | 0.089 | 0.091 | 0.094 | 0.097 | 0.101 | 0.104 | 0.107 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11
PJM_ROR | VA+WV+OH+IL | 0.034 | 0.033 | 0.033 | 0.032 | 0.031 | 0.031 | 0.036 | 0.042 | 0.047 | 0.053 | 0.059 | 0.065 | 0.071 | 0.077 | 0.083 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089
SOCO | GA+AL | 0.049 | 0.048 | 0.048 | 0.047 | 0.046 | 0.045 | 0.051 | 0.057 | 0.063 | 0.069 | 0.076 | 0.083 | 0.09 | 0.097 | 0.104 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111 | 0.111
SPP_N | KS | 0.027 | 0.027 | 0.026 | 0.026 | 0.026 | 0.025 | 0.029 | 0.034 | 0.038 | 0.042 | 0.046 | 0.051 | 0.055 | 0.06 | 0.064 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069
SPP_S | OK | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.011 | 0.019 | 0.028 | 0.037 | 0.046 | 0.054 | 0.063 | 0.072 | 0.081 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
TVA | TN | 0.053 | 0.052 | 0.051 | 0.05 | 0.049 | 0.048 | 0.05 | 0.053 | 0.056 | 0.059 | 0.062 | 0.066 | 0.069 | 0.073 | 0.076 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
VACAR | SC+NC | 0.048 | 0.048 | 0.047 | 0.046 | 0.045 | 0.044 | 0.049 | 0.053 | 0.058 | 0.062 | 0.068 | 0.073 | 0.078 | 0.084 | 0.089 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094 | 0.094
ERCOT | TX | 0.011 | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.017 | 0.024 | 0.031 | 0.037 | 0.045 | 0.052 | 0.059 | 0.066 | 0.073 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
AZ_NM_SNV_Coal | AZ | 0.012 | 0.011 | 0.011 | 0.011 | 0.011 | 0.011 | 0.015 | 0.019 | 0.023 | 0.027 | 0.031 | 0.035 | 0.039 | 0.044 | 0.048 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052
NP15 | CA | 0.064 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.064 | 0.063 | 0.064 | 0.064 | 0.065 | 0.065 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
NWPP_Coal | WA | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.008 | 0.011 | 0.015 | 0.019 | 0.023 | 0.027 | 0.031 | 0.034 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
RMPA | CO | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.035 | 0.036 | 0.037 | 0.038 | 0.039 | 0.041 | 0.043 | 0.045 | 0.046 | 0.048 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SP15 | CA | 0.064 | 0.071 | 0.069 | 0.068 | 0.067 | 0.066 | 0.065 | 0.064 | 0.064 | 0.063 | 0.064 | 0.064 | 0.065 | 0.065 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
ALB | ND | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.014 | 0.018 | 0.023 | 0.027 | 0.031 | 0.036 | 0.04 | 0.044 | 0.049 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
BC | WA | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.008 | 0.011 | 0.015 | 0.019 | 0.023 | 0.027 | 0.031 | 0.034 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
MAPP_CA | ND | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.014 | 0.018 | 0.023 | 0.027 | 0.031 | 0.036 | 0.04 | 0.044 | 0.049 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053
IESO | NY | 0.081 | 0.081 | 0.08 | 0.079 | 0.078 | 0.078 | 0.078 | 0.079 | 0.08 | 0.081 | 0.083 | 0.084 | 0.086 | 0.087 | 0.089 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091 | 0.091
Old ENT region with MI instead of MS |  | 0.047 | 0.047 | 0.046 | 0.045 | 0.044 | 0.044 | 0.049 | 0.054 | 0.06 | 0.065 | 0.071 | 0.077 | 0.083 | 0.089 | 0.095 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101 | 0.101

## Exhibit21_MRN Inputs
Appendix A, Exhibit 21: Key MRN Parameters (formerly Exhibit 19)
|  | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Energy Prices | Gas Wellhead Price (2009 dollars per million Btu)* | 4.0951 | 4.2562 | 4.5855 | 5.324 | 5.757 | 6.3658 |  |  |  | (a)
| World crude oil price (2009 dollars per barrel) | 74.8593 | 86.9385 | 98.709 | 107.5323 | 112.3452 | 114.0502 |  |  |  | (a)
Resources/Endowments | Gas supply resource index (2010 = 1)* | 1 | 1.0365 | 1.0795 | 1.1086 | 1.1587 | 1.224 |  |  |  | (a)
Macro economic | GDP Index (2010 = 1) | 1 | 1.1601 | 1.3177 | 1.5138 | 1.7196 | 1.9432 |  |  |  | (a) (c)
Alternate transporation fuels defaults | Cost of Ethanol (relative to gasoline) | 1.09 | 1.34 | 1.41 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
| Cost of advanced biodiesel (relative to gasoline) | 0.15 | 0.33 | 0.58 | 1.19 | 1.38 | 1.38 | 1.38 | 1.38 | 1.38
New vehicle technologies defaults | Plug to Wheels Electricity Usage for PHEV40 KWH per Mile | 0.36 | 0.345 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.255 | 0.24
| Plug to Wheels Electricity Usage for BEV100 KWH per Mile | 0.36 | 0.345 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.255 | 0.24
| % of time on electric engine for PHEV40 | 0.5 | 0.55 | 0.6 | 0.62 | 0.64 | 0.655 | 0.67 | 0.685 | 0.7
| Vehicle cost premium for PHEV40 (relative to conventional) | 2 | 1.8 | 1.71 | 1.65 | 1.59 | 1.54 | 1.5 | 1.46 | 1.42 | (b)
| Vehicle cost premium for BEV100 (relative to conventional) | 4.19 | 3.46 | 3.16 | 2.92 | 2.73 | 2.55 | 2.4 | 2.25 | 2.12 | (b)
| miles per gallon of Internal Combustion Engine in PHEV40 | 30 | 34.55 | 39.1 | 41 | 42.9 | 44.35 | 45.8 | 47 | 48.2
New vehicle stock (millions) | Plug-in 10/40 Gasoline Hybrid | 0 | 0.17 | 0.49 | 1.14 | 2.23 | 3.55 | 5.65 | 9 | 14.32 | (a) (d)
| 100/200 Mile Electric Vehicle | 0.02 | 0.13 | 0.32 | 0.64 | 1.07 | 1.51 | 2.12 | 2.99 | 4.2 | (a) (d)
Total VMT for Light-Duty Vehicles (billions of miles) |  | 2733.552 | 2947.1597 | 3199.0596 | 3465.4707 | 3753.7415 | 4043.7061 |  |  |  | (a)
Alternative Fuel VMT (billions of miles) | Plug-in 10/40 Gasoline Hybrid | 0 | 1.9531 | 5.935 | 14.3818 | 28.6389 | 46.2024 |  |  |  | (a)
| 100/200 Mile Electric Vehicle | 0.2882 | 1.4878 | 3.7443 | 7.776 | 13.2829 | 18.9172 |  |  |  | (a)
Emissions factors for transport fuel defaults | Gasoline (CO2e/MJ) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
| Ethanol (CO2e/MJ) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
| Advanced biodiesel (CO2e/MJ) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
Carbon tax | Carbon tax (in $ per metric ton of CO2) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Gas price and gas resource are interdependent. Tightening or loosening the gas resource will be used to obtain high and low gas price sensitivities
(a) Data based on ER AEO2011 through 2035. Growth after 2035 based on growth from 2030 to 2035
(b) CRA may modify these two parameters as needed to approximately match the PHEV/BEV AEO 2011 new vehicle stock projection. These two parameters then will be modified to create higher EV penetration sensitivities.
(c) The GDP parameters can be modified to create high or low economic growth sensitivities
(d) Updated 2/3/11 to include Light Duty trucks within the New Vehicle stock
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit22_RPS Summary
Exhibit 22 RPS Summary. Details on the RPS calculation are in a separate document Appendix C
State | Tier | Load Covered (%) | Penalty or ACP ($/MWh) | Target
|  |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Connecticut | RE | 100 | 55 | 11% | 12% | 13% | 14% | 15.5% | 17% | 18.5% | 20% | 22.5% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23%
Delaware | RE | 100 | 80 | 4.982% | 6.8% | 8.1% | 9.4% | 10.7% | 12% | 13.25% | 14.5% | 15.75% | 17% | 17.75% | 18.5% | 19.25% | 20% | 20.75% | 21.5% | 22.5% | 22.5% | 22.5% | 22.5%
| Solar | 100 | 500 | 0.018% | 0.2% | 0.4% | 0.6% | 0.8% | 1% | 1.25% | 1.5% | 1.75% | 2% | 2.25% | 2.5% | 2.75% | 3% | 3.25% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5%
District of Columbia | RE | 100 | 50 | 3.96% | 4.93% | 6.4% | 7.87% | 9.33% | 11.29% | 13.25% | 15.2% | 17.15% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6%
| Solar | 100 | 500 | 0.04% | 0.07% | 0.1% | 0.13% | 0.17% | 0.21% | 0.25% | 0.3% | 0.35% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4%
Illinois | RE | 88.5 | 19.1 | 5.5% | 6.482% | 7.46% | 8.365% | 9.2% | 10.11% | 11.52% | 12.93% | 14.34% | 15.75% | 17.16% | 18.57% | 19.98% | 21.39% | 22.8% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5%
| Solar | 88.5 | 19.1 | 0% | 0.0175% | 0.04% | 0.135% | 0.3% | 0.645% | 0.735% | 0.825% | 0.915% | 1.005% | 1.095% | 1.185% | 1.275% | 1.365% | 1.455% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Kansas | All RE | 81.5 | 100 | 6% | 6% | 6% | 6% | 6% | 9% | 9% | 9% | 9% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12%
Maine | RE | 98.3 | 60.93 | 34% | 35% | 36% | 37% | 38% | 39% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
Maryland | RE | 98 | 40 | 4.95% | 6.4% | 8% | 10% | 10.1% | 12.2% | 12.55% | 14.9% | 16.2% | 16.5% | 16.85% | 18% | 18% | 18% | 18% | 18% | 18% | 18% | 18% | 18%
| Solar | 98 | 300 | 0.05% | 0.1% | 0.2% | 0.3% | 0.4% | 0.5% | 0.55% | 0.9% | 1.2% | 1.5% | 1.85% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
Massachusetts | RE | 100 | 60.93 | 9.444% | 10.33% | 11.18% | 11.99% | 12.73% | 13.69% | 14.69% | 15.69% | 16.69% | 17.69% | 18.69% | 19.69% | 20.69% | 21.69% | 22.69% | 23.69% | 24.69% | 25.69% | 26.69% | 27.69%
| Solar | 100 | 600 | 0.1564% | 0.2713% | 0.4207% | 0.6149% | 0.8674% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066%
Michigan | RE | 100 | 40 | Target 2012: 4.8%; Target 2013: 5.645%; Target 2014: 6.75%; Target 2015: 10%
Minnesota | Xcel | 47.8 | 100 | 15% | 18% | 18% | 18% | 18% | 25% | 25% | 25% | 25% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Other Utilities RE | 52.2 | 100 | 7% | 12% | 12% | 12% | 12% | 17% | 17% | 17% | 17% | 20% | 20% | 20% | 20% | 20% | 25% | 25% | 25% | 25% | 25% | 25%
Missouri | RE | 70 | 100 | 1.96% | 1.96% | 1.96% | 4.9% | 4.9% | 4.9% | 4.9% | 9.8% | 9.8% | 9.8% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7%
| Solar | 70 | 600 | 0.04% | 0.04% | 0.04% | 0.1% | 0.1% | 0.1% | 0.1% | 0.2% | 0.2% | 0.2% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3%
New Hampshire | RE | 98.2 | 60.93 | 9.5% | 10.5% | 11.5% | 12.5% | 13.5% | 14.5% | 15.5% | 16.5% | 17.5% | 18.5% | 19.5% | 20.5% | 21.5% | 22.5% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5%
| Solar | 98.2 | 160.01 | 0.08% | 0.15% | 0.2% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3%
New Jersey | RE | 98.3 | 50 | 7.992% | 8.82% | 9.643% | 10.48% | 11.31% | 12.15% | 12.98% | 14.82% | 16.68% | 18.53% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38%
| Solar (in GWh) | 98.3 | 693 | 306 | 442 | 596 | 772 | 965 | 1150 | 1357 | 1591 | 1858 | 2164 | 2518 | 2928 | 3433 | 3989 | 4610 | 5316 | 5316 | 5316 | 5316 | 5316
| Offshore Wind (in MW) |  |  | Target 2021: 1100
New York | RE | 100 | 20 | 3.39% | 4.54% | 5.6% | 6.83% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09%
North Carolina | RE | 100 | 40 | 0% | 2.93% | 2.93% | 2.93% | 5.86% | 5.86% | 5.86% | 9.8% | 9.8% | 9.8% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3%
| Solar | 100 | 200 | 0.02% | 0.07% | 0.07% | 0.07% | 0.14% | 0.14% | 0.14% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2%
Ohio | RE | 88.6 | 45 | 0.97% | 1.44% | 1.91% | 2.38% | 3.35% | 4.32% | 5.28% | 6.24% | 7.2% | 8.16% | 9.12% | 10.08% | 11.04% | 12% | 12% | 12% | 12% | 12% | 12% | 12%
| Solar | 88.6 | 400 | 0.03% | 0.06% | 0.09% | 0.12% | 0.15% | 0.18% | 0.22% | 0.26% | 0.3% | 0.34% | 0.38% | 0.42% | 0.46% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Pennsylvania | RE | 97.3 | 45 | 2.98% | 3.467% | 3.949% | 4.416% | 4.856% | 5.25% | 5.707% | 6.16% | 6.61% | 7.057% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5%
| Solar | 97.3 | 654.37 | 0.0203% | 0.0325% | 0.051% | 0.084% | 0.144% | 0.25% | 0.2933% | 0.34% | 0.39% | 0.4433% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Rhode Island | RE | 99.3 | 60.93 | 5.5% | 6.5% | 7.5% | 8.5% | 10% | 11.5% | 13% | 14.5% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16%
Wisconsin | RE | 100 | 40 | 6.125% | 6.125% | 6.125% | 6.125% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12%
Montana | RE | 66.6 | 10 | 10% | 10% | 10% | 10% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
North Dakota | 10% by 2015 | 100 | 10 | 0% | 0% | 0% | 0% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Oklahoma | 15% by 2015 | [6 empty] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
South Dakota | 10% by 2015 |  |  | 0% | 0% | 0% | 0% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Vermont | RE | 90 | 60.93 | 10% | 10% | 15% | 15% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
Virginia | 15% of base year (2007) sales by 2025 |  |  | 1% | 2% | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10% | 11% | 12% | 13% | 14% | 15% | 15% | 15% | 15% | 15% | 15%
Nebraska | 10% by 2020 |  |  | 1% | 2% | 3% | 4% | 5% | 6% | 7% | 8% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Note on A5: Tyler Ruthven: CHP tier removed as it is not RE
Note on B5: Tyler Ruthven: Tier 1 (all RE) and Tier 2 (Bio RE) combined
Note on C5: Tyler Ruthven: RPS covers IOUs (93.4% of load) but as MOUs are required to come up w/similar RPS, Load % increased to 100%
Note on B6: Tyler Ruthven: RE New and RE Existing Tiers combined
Note on C6: Tyler Ruthven: PS covers ~70% of DE Load (prior to expiration of secondary RPS requirement it covered ~57%) but MOUs required to come up w/simialar RPS requirements by 2013 there fore value is listed as 100%
Note on D6: Tyler Ruthven: DE ACP increasings if a utility uses ACP for more than 1 compliance year. Max value is used for modeling purposes
Note on C7: Tyler Ruthven: PS covers ~70% of DE Load (prior to expiration of secondary RPS requirement it covered ~57%) but MOUs required to come up w/simialar RPS requirements by 2013 there fore value is listed as 100%
Note on D7: Tyler Ruthven: DE ACP increasings if a utility uses ACP for more than 1 compliance year. Max value is used for modeling purposes
Note on A8: Tyler Ruthven: Hydro/MSW tier removed as it expires in 2020
Note on A10: Tyler Ruthven: IL IOU and Competitive Supplier RPSs combined
Note on B10: Tyler Ruthven: Wind and all RE Tiers combined.
Note on C10: Tyler Ruthven: IOU and Competitive Suppliers RPS combined
Note on D10: Tyler Ruthven: Non-IOU ACP applied
Note on C11: Tyler Ruthven: IOU and Competitive Suppliers RPS combined
Note on D11: Tyler Ruthven: Non-IOU ACP applied
Note on D12: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $100 ACP value is set
Note on B13: Tyler Ruthven: Existing Tier (30%) and New RE Tier Combined
Note on D13: Tyler Ruthven: ACP for new RE
Note on A14: Tyler Ruthven: Tier 2 removed as it zeroes out in 2018
Note on C14: Tyler Ruthven: RPS currently covers 93.4% of load but this number will increase when current exemptions lapse therefore it is set at 98%
Note on C15: Tyler Ruthven: RPS currently covers 93.4% of load but this number will increase when current exemptions lapse therefore it is set at 98%
Note on D15: Tyler Ruthven: Solar ACP declines over time from $400 in 2010 to $50 in 2023. Listed value is set at $300
Note on A16: Tyler Ruthven: Tier 3 (MSW) removed as it is not renewable
Note on B16: Tyler Ruthven: Includes both Tier 1 (New RE) and Tier 2 (existing RE). Tier 2 target is 3.6% a year
Note on C16: J Tyler Ruthven: Adjusted from 86 to reflect MA belief that MOUs will meet targets
Note on B17: J Tyler Ruthven: MA Solar targets are assumptions based on MA's 400 MW solar target
Note on C17: J Tyler Ruthven: Adjusted from 86 to reflect MA belief that MOUs will meet targets
Note on A18: Tyler Ruthven: Beyond 2015, utilities are required to purchase the same # of RECs as in 2015, not 10% of load
Note on D18: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on B19: Tyler Ruthven: 1/6 of the target must be met by non-wind/solar resources
Note on D19: Tyler Ruthven: Penalty for non-compliance is monetary penalty no greater than the cost of compliance - so non-compliance not expected and ACP set at $100
Note on D20: Tyler Ruthven: Penalty for non-compliance is monetary penalty no greater than the cost of compliance - so non-compliance not expected and ACP set at $100
Note on D21: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $100 ACP value is set
Note on D22: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $600 ACP value is set
Note on B23: Tyler Ruthven: Tier 1 (New RE), Tier 3 (Existing Bio) and Tier 4 (existing hydro) combined
Note on D23: Tyler Ruthven: ACP for New RE Tier
Note on B25: Tyler Ruthven: Tier 1 (non-hydro RE) and Tier 2 (all RE) combined
Note on B27: Tyler Ruthven: Recent law creates an Offshore wind tier to support the building of 1100 MW of offshore wind - these facilities will reduce the overall RPS target by the corresponding amount
Note on B28: Tyler Ruthven: Includes Baseline Resources (accounts for ~20% points from NY and imported Hydro), Customer-sited Tier (~0.5% point mostly from solar and anaerobic digestors) and Main Tier resources. Does not include 1% point voluntary goal nor government purchasing requirements
Note on C28: Tyler Ruthven: NY RPS covers 84.7% of load - LIPA is exempt. However, LIPA is pursuing identical goals to the NY RPS therefore its load is included.
Note on D28: Tyler Ruthven: ACP set at approximate level of previous NYSERDA REC purchases
Note on A29: Tyler Ruthven: IOU and MOU/Coop targets combined
Note on B29: Tyler Ruthven: Includes Tier 1 (RE), Tier 3 (Swine Waste) and Tier 4 (Poultry Waste). IOUs can meet 25% of the targets with EE and MOUs can meet 100% of the target with EE. It is assumed here that none of the targets are met with EE.
Note on C29: Tyler Ruthven: IOU and MOU/Coop targets combined so that 100% of load is covered
Note on D29: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on D30: Tyler Ruthven: No Information on ACP found so proxy value of $200 used
Note on A33: Tyler Ruthven: Tier 2 removed as it is not renewable; % values reduced by .02% according to PA modeling
Note on B35: Tyler Ruthven: New RE and Existing RE tiers combined
Note on D36: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on A38: J Tyler Ruthven: ND has indicated that their Voluntary RPS should be modeled in full
Note on D38: J Tyler Ruthven: ND has supported a token $10 ACP
Note on A39: J Tyler Ruthven: OK has indicated that their utilities will meet their RPS target
Note on A41: J Tyler Ruthven: VT has indicated that their Voluntary RPS should be modeled as mandatory
Note on A42: J Tyler Ruthven: VA has indicated that their Voluntary RPS should be modeled in full

## Exhibit23_EPA_Regulations
EPA Regulations Modeling
| Sources | Modeling
Existing Regulations | NERC Moderate Case and Sierra Club Data | SCR retrofits added for all coal units greater than 200 MW and that do not have SCRs by 2018
Transport Rule | CRA Proposal | Transport Rule not modeled as it is rendered non-binding by the Utility MACT Rule
Utility MACT Rule | CRA Proposal and NERC Moderate Case | All U.S. coal units must have wet scrubbers by 2018; All U.S. coal units must have sorbent injection and fabric filters by 2018
Cooling Water Intake Structures Rule | NERC Moderate Case, CRA and EPA input | All nuclear generating units and all coal generating units larger than 200 MW employing once-through cooling systems will be required to replace their cooling water systems with closed-loop cooling systems by 2020. Compliance costs and capacity penalties will be based on the NERC report (NERC Moderate Case and CRA Modeling); All coal generating units smaller than 200 MW and non-nuclear steam generating units will be required to install an alternative compliance technology valued at 90% of the cost of fine-mesh screens (NERC Report and CRA Modeling)
Coal Combustion Residuals Rule | NERC Moderate Case | $15 per ton (2010 dollars) of ash waste added to operating costs of coal plants by 2018 ----to add $15/ton coal ash for EPA regs, which is estimated to be approximatley $0.63/MWh adder to VOM for coal for most cases, except when residuals not in effect.
NERC Moderate Case taken from:
http://www.nerc.com/files/EPA_Scenario_Final.pdf
| Cooling Water Intake Structure Notes | Data on >200 MW coal generating unit cooling structure taken from Form EIA-860
25% of Nuclear generating units estimated to have closed-loop cooling based on analysis of NRC unit information. Closed-loop cooling systems will be added to all nuclear units at 75% of total cost estimate to account for units that already have closed-loop cooling.
Cost of fine mesh screens estimated at $25/kW for overlay retrofitting plus $0.63/kW-year O&M

## Exhibit24_CarbonModeling
Values raised from $1.86 based on recent decisions within RGGI
| 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
RGGI States $/tCO2 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89
Cost adder only applicable to RGGI states: |  | CT, DE, MA, MD, ME, NH, NJ, NY, RI and VT
Sources
CRA information
RGGI Nov. 12 Stakeholder Meeting RGGI Modeling Review |  | http://www.rggi.org/stakeholder_meeting

## Exhibit25_Renewable Incentives
Production Tax Credit and Investment Tax Credit Policy Sunsets
PTC and ITC are modeled in full with no expiration date
Details | PTC | Tax credit of ~$22/MWh (2010 $) for every MWh produced for a 10 year period after installation | Primarily utilized by wind generation | http://www.dsireusa.org/incentives/incentive.cfm?Incentive_Code=US13F&re=1&ee=1
| ITC | Tax credit equal to 30% the value of the capital cost of an applicable facility given immediately after the facility is installed | Primarily utilized by solar generation | http://www.dsireusa.org/incentives/incentive.cfm?Incentive_Code=US13F&re=1&ee=1

## Exhibit26_ EE Energy Targets
Exhibit 26 Energy Efficiency Resource Standards - Energy Savings from 2010 on based on Existing Programs
Savings are already be included in Energy growth rates in Table 2
Sources of Information: |  | (1) FERC's December 2010 "Renewable Power & Energy Efficiency: Energy Efficiency Resource Standards (EERS) and Goals"
(2) ACEEE's October 2010 "The 2010 State Energy Efficiency Scorecard"
(3) U.S. DOE's July 2010 "State Energy Efficiency Resource Standards Analysis"
Reserve Margin Region | NEEM Region |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
AK | AK |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AZNM_SNV | AZNM_SNV |  | 0.008 | 0.018 | 0.03 | 0.045 | 0.061 | 0.078 | 0.093 | 0.108 | 0.123 | 0.138 | 0.153 | 0.153 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154 | 0.154
ENT | ENT |  | 0 | 0.001 | 0.002 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004
ERCOT | ERCOT |  | 0.004 | 0.008 | 0.012 | 0.016 | 0.02 | 0.024 | 0.028 | 0.032 | 0.036 | 0.04 | 0.044 | 0.048 | 0.052 | 0.056 | 0.06 | 0.064 | 0.068 | 0.072 | 0.076 | 0.08 | 0.084
FRCC | FRCC |  | 0.004 | 0.007 | 0.011 | 0.014 | 0.018 | 0.021 | 0.025 | 0.028 | 0.032 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
HI | HI |  | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21
MISO | MISO_IN |  | 0.003 | 0.008 | 0.015 | 0.024 | 0.035 | 0.048 | 0.062 | 0.079 | 0.097 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117
MISO | MISO_MI |  | 0.005 | 0.013 | 0.023 | 0.033 | 0.043 | 0.053 | 0.063 | 0.073 | 0.083 | 0.093 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103
MISO | MISO_MO-IL |  | 0.004 | 0.011 | 0.02 | 0.032 | 0.046 | 0.063 | 0.08 | 0.096 | 0.113 | 0.13 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147 | 0.147
MISO | MISO_W |  | 0.012 | 0.024 | 0.037 | 0.046 | 0.055 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
MISO | MISO_WUMS |  | 0.01 | 0.021 | 0.035 | 0.051 | 0.069 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089
SPP | NE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEISO | NEISO | from NE States | 0.011 | 0.02 | 0.027 | 0.037 | 0.046 | 0.055 | 0.064 | 0.072 | 0.08 | 0.088 | 0.096 | 0.104 | 0.112 | 0.12 | 0.127 | 0.134 | 0.142 | 0.149 | 0.156 | 0.162 | 0.169
Non-RTO Midwest | Non-RTO Midwest |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA | NP15 |  | 0.01 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
NWPP | NWPP |  | 0.005 | 0.011 | 0.017 | 0.023 | 0.029 | 0.035 | 0.037 | 0.038 | 0.04 | 0.041 | 0.043 | 0.044 | 0.046 | 0.047 | 0.049 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
NYISO | NYISO_AF |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
NYISO | NYISO_GI |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
NYISO | NYISO_JK |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
PJM | PJM EASTERN MAAC |  | 0.008 | 0.024 | 0.045 | 0.065 | 0.086 | 0.106 | 0.124 | 0.141 | 0.159 | 0.176 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194 | 0.194
PJM | PJM REST OF MAAC |  | 0.01 | 0.025 | 0.04 | 0.051 | 0.058 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066
PJM | PJM REST OF RTO |  | 0.003 | 0.008 | 0.013 | 0.019 | 0.028 | 0.037 | 0.047 | 0.058 | 0.071 | 0.084 | 0.098 | 0.112 | 0.125 | 0.136 | 0.147 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158
RMPA | RMPA |  | 0.006 | 0.012 | 0.018 | 0.024 | 0.03 | 0.036 | 0.042 | 0.049 | 0.055 | 0.061 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067 | 0.067
SOCO | SOCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA | SP15 |  | 0.01 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SPP | SPP_N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPP | SPP_S |  | 0 | 0.02 | 0.04 | 0.06 | 0.08 | 0.1 | 0.12 | 0.14 | 0.16 | 0.18 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
TVA | TVA |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VACAR | VACAR |  | 0.002 | 0.003 | 0.005 | 0.006 | 0.008 | 0.009 | 0.011 | 0.014 | 0.016 | 0.021 | 0.026 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031

## Exhibit27_EE Peak Targets
Exhibit 27 Energy Efficiency Resource Standards - Peak Demand Savings from 2010 on based on Existing Programs
Savings are already be included in Peak Demand growth rates in Table 3
Energy Efficiency Resource Standards - Peak Demand Savings from 2010 on
Sources of Information: |  | (1) FERC's December 2010 "Renewable Power & Energy Efficiency: Energy Efficiency Resource Standards (EERS) and Goals"
(2) ACEEE's October 2010 "The 2010 State Energy Efficiency Scorecard"
(3) U.S. DOE's July 2010 "State Energy Efficiency Resource Standards Analysis"
Reserve Margin Region | NEEM Region |  | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
AK | AK |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AZNM_SNV | AZNM_SNV |  | 0.007 | 0.018 | 0.031 | 0.047 | 0.064 | 0.081 | 0.098 | 0.115 | 0.131 | 0.148 | 0.164 | 0.164 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165 | 0.165
ENT | ENT |  | 0 | 0.001 | 0.002 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004
ERCOT | ERCOT |  | 0.004 | 0.008 | 0.012 | 0.016 | 0.02 | 0.024 | 0.028 | 0.032 | 0.036 | 0.04 | 0.044 | 0.048 | 0.052 | 0.056 | 0.06 | 0.064 | 0.068 | 0.072 | 0.076 | 0.08 | 0.084
FRCC | FRCC |  | 0.004 | 0.007 | 0.011 | 0.014 | 0.018 | 0.021 | 0.025 | 0.028 | 0.032 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
HI | HI |  | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.16 | 0.17 | 0.18 | 0.19 | 0.2 | 0.21
MISO | MISO_IN |  | 0.003 | 0.008 | 0.015 | 0.024 | 0.035 | 0.048 | 0.062 | 0.079 | 0.097 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117 | 0.117
MISO | MISO_MI |  | 0.005 | 0.013 | 0.023 | 0.033 | 0.043 | 0.053 | 0.063 | 0.073 | 0.083 | 0.093 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103 | 0.103
MISO | MISO_MO-IL |  | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.006 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007
MISO | MISO_W |  | 0.012 | 0.024 | 0.037 | 0.046 | 0.055 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065 | 0.065
MISO | MISO_WUMS |  | 0.01 | 0.021 | 0.035 | 0.051 | 0.069 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089 | 0.089
SPP | NE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEISO | NEISO | from NE States | 0.01 | 0.018 | 0.025 | 0.034 | 0.041 | 0.049 | 0.056 | 0.064 | 0.071 | 0.078 | 0.085 | 0.092 | 0.099 | 0.105 | 0.112 | 0.119 | 0.125 | 0.131 | 0.137 | 0.143 | 0.149
Non-RTO Midwest | Non-RTO Midwest |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA | NP15 |  | 0.01 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
NWPP | NWPP |  | 0.005 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.033 | 0.035 | 0.037 | 0.04 | 0.042 | 0.045 | 0.047 | 0.05 | 0.052 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055 | 0.055
NYISO | NYISO_AF |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
NYISO | NYISO_GI |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
NYISO | NYISO_JK |  | 0.019 | 0.044 | 0.069 | 0.094 | 0.119 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144
PJM | PJM EASTERN MAAC |  | 0.006 | 0.022 | 0.041 | 0.061 | 0.08 | 0.1 | 0.117 | 0.135 | 0.152 | 0.17 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187
PJM | PJM REST OF MAAC |  | 0.012 | 0.03 | 0.048 | 0.061 | 0.069 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076 | 0.076
PJM | PJM REST OF RTO |  | 0.003 | 0.008 | 0.013 | 0.019 | 0.028 | 0.037 | 0.047 | 0.058 | 0.071 | 0.084 | 0.098 | 0.112 | 0.125 | 0.136 | 0.147 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158 | 0.158
RMPA | RMPA |  | 0.009 | 0.017 | 0.026 | 0.034 | 0.043 | 0.052 | 0.06 | 0.069 | 0.077 | 0.086 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095 | 0.095
SOCO | SOCO |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA | SP15 |  | 0.01 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SPP | SPP_N |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPP | SPP_S |  | 0 | 0.02 | 0.04 | 0.06 | 0.08 | 0.1 | 0.12 | 0.14 | 0.16 | 0.18 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
TVA | TVA |  | 0.009 | 0.021 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
VACAR | VACAR |  | 0.002 | 0.003 | 0.005 | 0.006 | 0.008 | 0.009 | 0.011 | 0.014 | 0.016 | 0.021 | 0.026 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031 | 0.031

## Table1_LoadBlocks
Table 1 - Load Blocks
Load Block | Season | Number of Hours
B1 | Summer | 10
B2 | Summer | 25
B3 | Summer | 75
B4 | Summer | 100
B5 | Summer | 200
B6 | Summer | 300
B7 | Summer | 400
B8 | Summer | 500
B9 | Summer | 800
B10 | Summer | 1262
B11 | Shoulder | 25
B12 | Shoulder | 200
B13 | Shoulder | 600
B14 | Shoulder | 900
B15 | Shoulder | 1203
B16 | Winter | 25
B17 | Winter | 100
B18 | Winter | 400
B19 | Winter | 700
B20 | Winter | 935
TOTAL
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table2_Demand
Table 2 - Energy Demand
Updated for AEO2011 growth rates after 2020 - 2/8/11
NEEM Region | AEO Region for 2020+ Growth Rate | 2011 Energy (GWh) | 2011-2020 Growth Rate | 2020-2050 Growth Rate
AZ_NM_SNV_Coal | AZNM | 124203 | 1.88% | 1.31%
ENT | SRDA | 159507 | 1.37% | 0.53%
ERCOT | ERCT | 316195 | 1.69% | 0.65%
FRCC | FRCC | 229020 | 1.73% | 1.24%
MAPP_US | MROW | 29828 | 0.87% | 0.78%
MISO_IN | RFCW | 97101 | 1.05% | 0.61% | Modified based on MISO input 2/14/11. they also modified 2020-2050 to match 2011-2020 but BAU is following AEO2011 for 2020-2050
MISO_MI | RFCM | 94678 | 0.8% | 0.79% | "
MISO_MO-IL | SRGW | 96157 | 0.87% | 0.82% | "
MISO_W | MROW | 137739 | 0.85% | 0.78% | "
MISO_WUMS | MROE | 66425 | 1.1% | 0.66% | "
NE | MROW | 29481 | 1.81% | 0.78%
NEISO | NEWE | 129768 | 0.02% | 0% | Based on NEISO gross demands, AEO2011 growth rate post-2020, less New England States Committee on Electricity assumptions on future EE
NonRTO_Midwest | SRCE | 58092 | 1.66% | 0.49%
NP15 | CAMX | 110014 | 0.94% | 1%
NWPP_Coal | NWPP | 246983 | 1.3% | 0.94%
NYISO_A-F (note A) | NYUP | 63281 | 0.2% | 0.51% | Based on BAU Demand Forecasts.xls calculation by King Look 2/11/11
NYISO_G-I (note A) | NYCW | 19524 | 0.14% | 0.85% | "
NYISO_J-K (note A) | NYLI | 73315 | 0.39% | 0.88% | "
PJM_E | RFCE | 135784 | -0.98% | 0.67% | "
PJM_ROM | RFCE | 144050 | 0.86% | 0.67% | "
PJM_ROR | RFCW | 520031 | 0.4% | 0.61% | "
RMPA | RMPA | 72067 | 1.21% | 1.27%
SOCO | SRSE | 249461 | 1.94% | 0.81%
SP15 | CAMX | 179898 | 1.31% | 1%
SPP_N | SPNO | 75955 | 1.22% | 0.91%
SPP_S | SPSO | 163927 | 1.15% | 0.64%
TVA | SRCE | 173627 | 0.97% | 0.49%
VACAR | SRVC | 236109 | 1.62% | 0.96%
ALB | NA | 64239 | 1.57% | 1.41%
BC | NA | 63168 | 1.15% | 0.96%
IESO | NA | 142313 | -0.29% | 0.67%
MAPP_CA | NA | 48058 | 2% | 0.78%
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note A. NYISO demands are bassed on EE reductions that are half of the state targets. The growth rates for the BAU must be lowered to reflect the additional EE. Preliminary values are shown here. Below are the PA values.
NYISO_A-F | NYUP | 65364 | 0.73%
NYISO_G-I | NYCW | 20093 | 0.82%
NYISO_J-K | NYLI | 74987 | 0.99%

## Table3_Peak
Table 3 - Peak Demand
NEEM Region | Reserve Margin Region | AEO Region for 2020+ Growth Rate | 2011 Peak (MW) | 2011-2020 Growth Rate | 2020-2050 Growth Rate
AZ_NM_SNV_Coal | AZ_NM_SNV | AZNM | 27169 | 1.91% | 1.31%
ENT | ENT | SRDA | 29623 | 1.28% | 0.53%
ERCOT | ERCOT | ERCT | 64964 | 1.69% | 0.65%
FRCC | FRCC | FRCC | 46580 | 1.65% | 1.24%
MAPP_US | MAPP_US | MROW | 5512 | 0.89% | 0.78%
MISO_IN | MISO | RFCW | 17792 | 1.11% | 0.61% | Modified based on MISO input 2/14/11. they also modified 2020-2050 to match 2011-2020 but BAU is following AEO2011 for 2020-2050
MISO_MI | MISO | RFCM | 19930 | 0.79% | 0.79% | "
MISO_MO-IL | MISO | SRGW | 18713 | 0.92% | 0.82% | "
MISO_W | MISO | MROW | 25929 | 0.93% | 0.78% | "
MISO_WUMS | MISO | MROE | 12790 | 1.1% | 0.66% | "
NE | SPP | MROW | 5580 | 1.52% | 0.78%
NEISO | NEISO | NEWE | 27165 | 0.49% | 0.12% | Based on NEISO gross demands, AEO2011 growth rate post-2020, less New England States Committee on Electricity assumptions on future EE
NonRTO_Midwest | NonRTO_Midwest | SRCE | 10858 | 1.56% | 0.49%
NP15 | CA | CAMX | 24248 | 1.24% | 1%
NWPP_Coal | NWPP | NWPP | 41760 | 1.01% | 0.94%
NYISO_A-F (Note A) | NYISO | NYUP | 11269 | 0.1% | 0.51% | Based on BAU Demand Forecasts.xls calculation by King Look 2/11/11
NYISO_G-I (Note A) | NYISO | NYCW | 4280 | -0.09% | 0.85% | "
NYISO_J-K (Note A) | NYISO | NYLI | 16622 | 0.1% | 0.88% | "
PJM_E | PJM | RFCE | 31190 | -0.92% | 0.67% | "
PJM_ROM | PJM | RFCE | 25797 | 0.71% | 0.67% | "
PJM_ROR | PJM | RFCW | 95148 | 0.42% | 0.61% | "
RMPA | RMPA | RMPA | 12556 | 1.34% | 1.27%
SOCO | SOCO | SRSE | 48104 | 2.18% | 0.81%
SP15 | CA | CAMX | 35048 | 1.31% | 1%
SPP_N | SPP | SPNO | 15530 | 2.03% | 0.91%
SPP_S | SPP | SPSO | 32752 | 1.06% | 0.64%
TVA | TVA | SRCE | 33073 | 1.62% | 0.49%
VACAR | VACAR | SRVC | 46538 | 1.53% | 0.96%
ALB | ALB | NA | 9176 | 1.63% | 1.41%
BC | BC | NA | 11441 | 1.16% | 0.96%
IESO | IESO | NA | 23625 | -0.29% | 0.68%
MAPP_CA | MAPP_CA | NA | 8007 | 1.69% | 0.78%
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note A. NYISO demands are bassed on EE reductions that are half of the state targets. The growth rates for the BAU must be lowered to reflect the additional EE. Preliminary values are shown here. Below are the PA values.
NYISO_A-F | NYISO | NYUP | 11504 | 0.74%
NYISO_G-I | NYISO | NYCW | 4366 | 0.67%
NYISO_J-K | NYISO | NYLI | 17095 | 0.71%

## Table4_OM
Table 4 - O&M Costs
OK per ExGen, except increase VOM for coal ash as noted below | CRA needs to revise and document retirement/retrofit logic as appropriate. (Ex Gen)
Unit Type | FOM ($2010/kW-yr) | VOM ($2010/MWh)
Coal | 48.22* | 3.56**
CC | 29.68 | 2.37
Peak Gas | 16.62 | 8.31
Peak Oil | 22.55 | 8.31
STOG | 37.15 | 2.37
Nuclear | 112.77 | 2.37
Hydro | 14.24 | NA
Pumped Storage | 23.74 | 2.37
Photovoltaic | 14.66 | NA
Solar Thermal | 60.32 | NA
Wind | 34.22 | NA
Steam Wood | 32.05 | 2.37
Landfill Gas | 120.65 | NA
Geothermal | 89.76 | NA
* For a 30-40 year-old coal unit with no scrubber and no NOx controls.
This is expressed prior to the addition of the $17.90/kW-yr capital expenditure adder.
** For a coal unit with no retrofits.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table5_IntermittentRsvContr
Table 5 - Intermittent Resource Contributions
ExGen participating but deferring to NewGen
NEEM Region | Technology | Reserve Contribution
All Regions | Photovoltaic | 30%
All Regions | Solar Thermal | 30%
All Regions | Offshore Wind | 30% | Based on EWITS ELCC for Isolated Regions Scenario (weighted average extrapolation) and GE integration studies for NY, New England (CRA had 20%)
California | Wind | 25%
Canada | Wind | 20%
ERCOT | Wind | 9%
New York | Wind | 15% | Based on NYISO input and consideration of September 2010 NYISO Wind Integration Study (http://bit.ly/hP7bm3 ) and wind data for subsequent years from the ISO (CRA had 10%)
PJM (-E, -ROM, -ROR) | Wind | 13%
SPP | Wind | 6%
TVA | Wind | 12%
IESO | Wind | 11%
MAPP_CA | Wind | 11%
All Other Regions | Wind | 15%
New Generation Sub-Team Recommendation:
NEEM Region | Technology | Reserve Contribution | Basis
All Regions | Photovoltaic | 0.3 | CRA placeholder
All Regions | Offshore Wind | 0.3 | Based on EWITS ELCC for Isolated Regions Scenario (weighted average extrapolation) and GE integration studies for NY, New England
IESO / Ontario | Wind | 0.11 | Current planning practice (input from S.Chui)
New York | Wind | 0.15 | Based on NYISO input and consideration of September 2010 NYISO Wind Integration Study ( http://bit.ly/hP7bm3 ) and wind data for subsequent years from the ISO
PJM | Wind | 0.13 | CRA placeholder (based on current planning practice)
SPP | Wind | 0.06 | CRA placeholder (based on current planning practice)
TVA | Wind | 0.12 | CRA placeholder (based on current planning practice and added in Jan 25 assumptions draft)
All Other Regions | Wind | 0.15 | Based on EWITS ELCC for All-Onshore (Scenario 1), isolated region analysis

## Table 6_InstalledCapacity
Table 6 - Installed Capacity | This is CRA's 3-17 Version
No changes for BAU Sensitivities 1-9.
Net of reserve derates
NEEM Region | Installed Capacity - 2010 (GW) | Reserve Capacity - 2010 (GW)
ENT | 46.4 | 46.3
FRCC | 56.48 | 56.45
MAPP_US | 9.54 | 8.46
MISO_IN | 20.48 | 20.03
MISO_MI | 26.47 | 26.33
MISO_MO-IL | 24.4 | 24.07
MISO_W | 31.53 | 26.81
MISO_WUMS | 17 | 16.53
NE | 7.7 | 7.58
NEISO | 32.25 | 32.08
NonRTO_Midwest | 14.22 | 14.16
NYISO_A-F | 18.35 | 17.26
NYISO_G-I | 6.25 | 6.25
NYISO_J-K | 15.53 | 15.53
PJM_E | 31.28 | 31.25
PJM_ROM | 36.96 | 36.32
PJM_ROR | 121.59 | 119.31
SOCO | 65.41 | 65.41
SPP_N | 19.03 | 17.88
SPP_S | 43.15 | 40.99
TVA | 39.17 | 39.14
VACAR | 49.86 | 49.85
IESO | 37.94 | 36.78
MAPP_CA | 9.28 | 9.03
Grand Total | 780.24 | 763.79
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table 7_NewBuildCostParameters
Table 7 - New Build Costs and Characteristics
2/15/11- Capital costs changed to match 2015 and 2025 costs from Exhibit 9. Previously, this table mistakenly had costs for 2010 and 2020.
| Capital Costs |  | Performance Data
Technology | 2015 All-in Capital Cost (2010$/kW) | 2025 All-in Capital Cost (2010$/kW) | Total FOM (2010$/kW-yr) | Total VOM (2010$/MWh) | 2010 Heat Rate - HHV (Btu/kWh) | 2015+ Heat Rate - HHV (Btu/kWh)
Nuclear | 5462.3485 | 5080.9914 | 88.75 | 2.04 | 10488 | 10488
Advanced Coal | 2844.2788 | 2742.7073 | 29.67 | 4.25 |  | 8800
CC H-Frame | 1020.5714 | 984.75 | 14.39 | 3.43 | 7050 | 6430
CT | 701.83 | 678.08 | 6.7 | 9.87 | 9750 | 9750
IGCC | 3215.8931 | 3100.8573 | 48.9 | 6.87 | 8700 | 8700
IGCC w/seq | 5221.3502 | 4802.4573 | 69.3 | 8.04 | 10700
Wind | 2390.2629 | 2216.12 | 28.07 | 0 | NA | NA
Wind Offshore | 5655.4914 | 4801.92 | 53.33 | 0 | NA | NA
Photovoltaic | 4505.2057 | 3825.92 | 16.7 | 0 | NA | NA
Solar Thermal | 4445.8057 | 3775.52 | 64 | 0 | NA | NA
Landfill Gas | 2489.5433 | 2400.1367 | 120.3265 | 0 | 13648 | 13648
Biomass | 3680.3359 | 3128.9073 | 100.5 | 5 | 13500 | 13500
Geothermal | 4044.6057 | 3748.82 | 84.27 | 9.64 | NA | NA
CRA only models H-Frame CC so F-frame CC not listed.
Wind Options A&B based on New Gen Subteam Recommendations (see summary document)
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note on F7: CRA International: add 400 to start at AEO 2010 starting value
Note on G11: CRA International: ratio

## Table11_CCSRetro
Table 11 - Carbon Catpure Retrofit Example
Waiting for input from CRA on retirement/retrofit logic, including in third to last para of sec 3.55 that there are three policy options, but “retirement” is only mentioned in the last case of command-and-control”. We wish to know which of the three policies will be modeled and under which can the model decide about retirements, and how does it do it – what is its logic? | Probably no change for BAU sensitivities 1-7, but for 8 raise capital portion , then possibly change for 9 depending on how CRA retrofit logic functions or needs change -- CRA should document. (Ex Gen).
Retrofit | Unit Size (MW) | *Capital Cost (2010$/kW) | Fixed O&M ($2010/kW-yr) | Variable O&M ($2010/MWh) | Heat Rate Penalty | Capacity Penalty
Carbon Capture | any | 1287 | 1.58 | 2.8 | 30% | 23.1%
* Based on the capacity prior to the retrofit derate.
Note: Units must have existing or planned FGDs and SCRs to be eligible for this retrofit.

## Table 12_FCR
Table 12 - Real Capital Fixed Charge Rates for New Construction (based on 5% Real Discount Rate)
Technology | Operating Life (yrs) | FCR
NG Combined-Cycle | 25 | 11.3%
NG Combustion Turbine | 20 | 11.8%
Advanced Pulverized Coal, Coal IGCC, Coal IGCC-CCS | 40 | 10.5%
Nuclear | 40 | 11.2%
Photvoltaics | 20 | 11.8%
Biomass | 30 | 11.6%
Landfill Gas | 20 | 11.8%
Wind | 20 | 11.8%
Wind Offshore | 20 | 11.8%
Solar Thermal | 20 | 11.8%
Geothermal | 20 | 11.8%
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table13_CAIRIV
Table 13 - CAIR and Title IV emission constraints
Emission Constraint | Pollutant | Year | Cap | Units
CAIR NOx Seasonal | NOx | 2009 | 0.57 | MM Short tons
CAIR NOx Seasonal | NOx | 2015 | 0.48 | MM Short tons
TitleIV SO2 | SO2 | 2010 | 8.95 | MM Short tons
CAIR NOx Annual | NOx | 2010 | 1.52 | MM Short tons
CAIR NOx Annual | NOx | 2015 | 1.27 | MM Short tons
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table14_IntermittentGenLimits
Table 14 - Intermittent Generation Limits (annual MWh basis)
Intermittency Region | NEEM Regions | CRA Initial | SSC Consensus
SPP | SPP-S, SPP-N, NE | 20% | 25%
PJM | PJM_E, PJM_ROM, PJM_ROR | 20% | 25%
MAPP_CA | MAPP_CA | 20% | 25%
MAPP_US | MAPP_US | 20% | 25%
MISO | MISO_W, MISO_MI, MISO_WUMS, MISO_IN, MISO_MO_IL | 20% | 25%
Non-RTO Midwest | Non-RTO Midwest | 20% | 25%
New York | NYISO_A-F, NYISO_G-I, NYISO_J-K | 20% | 25%
NEISO | NEISO | 20% | 25%
ENT | ENT | 20% | 25%
TVA | TVA | 20% | 25%
VACAR | VACAR | 20% | 25%
SOCO | SOCO | 20% | 25%
FRCC | FRCC | 20% | 25%
IESO | IESO | 20% | 25%
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table15_Reserve Margin
Table 15 - Reserve Margin Regions, Reserve Requirements, NEEM Regions
Working Draft
Reserve Margin Area | Reserve Requirement | NEEM Region(s)
ALB | 18% | ALB
AZ_NM_SNV | 15.7% | AZ_NM_SNV
BC | 18% | BC
CA | 16.6% | NP15
SP15
ENT | 14% | ENT
ERCOT | NA | ERCOT
FRCC | 16% | FRCC
MAPP_US | 14% | MAPP_US
MAPP_CA | 12% | MAPP_CA
MISO | 17.4%* | MISO_IN
MISO_MI
MISO_MO-IL
MISO_W
MISO_WUMS
NEISO | 16% | NEISO
NonRTO_Midwest | 14% | NonRTO_Midwest
NWPP | 18% | NWPP
NYISO | 16.5%* | NYISO_A-F
NYISO_GHI
NYISO_JK
NYISO_GHI_JK | -5% | NYISO_GHI
NYISO_JK
NYISO_JK | -8% | NYISO_JK
OH (IESO) | 17% | OH
PJM | 15.3%* | PJM_E
PJM_ROM
PJM_ROR
PJM_E | -2.2% | PJM_E**
RMPA | 14% | RMPA
SOCO | 14% | SOCO
SPP | 13.6% | NE
SPP_N
SPP_S
TVA | 15% | TVA
VACAR | 14% | VACAR
* Based on coincident peak in reserve margin area. For PJM, CRA will apply a diversity factor to the non-coincident peaks.
** For purposes of this study, set equal to actual 2010 Reserve Margin
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table16_MMCoalPricesIndicative
Table 16 - Indicative 2012 Minemouth Coal Prices, with Proposed EPA Transport Rule
| 2012 Minemouth Price, 2010$/MMBtu | MMBtu per Ton | 2012 Minemouth Price, 2010$ per Ton
Central Appalachian Compliance | 2.2909 | 25.0138 | 57.3045
Illinois Basin, medium-sulfur | 1.7686 | 23.0049 | 40.6871
Northern Appalachian, high-Btu, high-sulfur | 2.006 | 25.877 | 51.91
Power River Basin South | 0.68846 | 17.6 | 12.1169
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table17_CoalCharacteristics
Table 17 - Coal Characteristics
|  | lbs/MMBtu | lbs/Tbtu
Coal Name | Rank | SO2 | Hg | Btu/lb | MMBtu/Ton
Northern Appalachia High Btu Low Sulfur | Bituminous | 2.4422 | 12.3 | 12840.4683 | 25.6809
Northern Appalachia High Btu High Sulfur | Bituminous | 4.0671 | 12.5 | 12938.4887 | 25.877
Northern Appalachia Low Btu Low Sulfur | Bituminous | 1.7612 | 16 | 12097.5848 | 24.1952
Northern Appalachia Low Btu High Sulfur | Bituminous | 3.7703 | 20.9 | 11515.6746 | 23.0313
Central Appalachia Compliance | Bituminous | 1.1188 | 5.9 | 12506.9213 | 25.0138
Central Appalachia Hi Hg Btu Non-Compliance | Bituminous | 2 | 8.2 | 12325.2895 | 24.6506
Southern Appalachia | Bituminous | 2.5225 | 8.7 | 11747.2074 | 23.4944
Illinois Basin Hi Sulphur | Bituminous | 2.5 | 4.5 | 12091.2253 | 24.1825
Illinois Basin Hi Sulphur | Bituminous | 3.5 | 6.5 | 11502.4377 | 23.0049
Illinois Basin Hi Sulphur | Bituminous | 5 | 6.3 | 11664.9421 | 23.3299
Central Basin | Bituminous | 4.9245 | 12.7 | 12174.0026 | 24.348
Gulf Lignite | Lignite | 3.3695 | 10.8 | 6839.7016 | 13.6794
Lignite | Lignite | 2.3001 | 10.8 | 6584.6302 | 13.1693
Montana Powder River Basin | Subbituminous | 1.1836 | 5.2 | 9052.2977 | 18.1046
Northern (WY) Powder River Basin | Subbituminous | 0.83393 | 7.1 | 8400 | 16.8
Southern (WY) Powder River Basin | Subbituminous | 0.70656 | 5.8 | 8800 | 17.6
Wyoming - Other | Subbituminous | 1.1432 | 3.7 | 9184.6788 | 18.3694
Rocky Mountain Colorado | WesternBit | 0.98036 | 3.7 | 11218.0809 | 22.4362
Rocky Mountain Utah | WesternBit | 1.2838 | 4.1 | 11790.4682 | 23.5809
Arizona Bituminous | Bituminous | 0.92878 | 4.2 | 10914.6278 | 21.8293
New Mexico Bituminous | Bituminous | 1.5459 | 4.2 | 9392.8132 | 18.7856
Import | Bituminous | 1 | 5.5 | 12000 | 24

## Table18_MRN-NEEMRegionMap
Table 18. MRN and NEEM Region Mapping
NEEM Region | MRN Region
AZ_NM_SNV_Coal | WEST
ENT | MSVL
ERCOT | OKTX
FRCC | SE
MAPP_US | MAPP
MISO_IN | ECAR
MISO_MI | ECAR
MISO_MO-IL | MSVL
MISO_W | MAPP
MISO_WUMS | MSVL
NE | MAPP
NEISO | NYNE
NonRTO_Midwest | ECAR
NP15 | CAL
NWPP_Coal | WEST
NYISO_A-F | NYNE
NYISO_G-I | NYNE
NYISO_J-K | NYNE
PJM_E | PJM
PJM_ROM | PJM
PJM_ROR | ECAR/SE split
RMPA | WEST
SOCO | SE
SP15 | CAL
SPP_N | MAPP
SPP_S | OKTX
TVA | SE
VACAR | SE
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Table23-24_Elasticities
Default values of Elasticities in the MRN Model
|  | Non-energy Sectors |  |  |  |  | Energy Sectors |  |  | Final Demand
|  | AGR | EIS | MAN | SRV | TRN | CRU | GAS | OIL | C | G | I
es_s | Top level elasticity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0
es_e | Energy versus value-added | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | NA | NA | NA
es_oil | Oil versus non-energy | 0 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
es_va | Capital vesus Labor | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | NA | NA | NA
es_ele | Electricity versus Coal-gas | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.8 | 0.8
es_cg | Coal versus Gas | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
es_n | Non-energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
etae | Elasticity of export supply | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
es_dm | Domestic versus imports | 3 | 3 | 3 | 1 | 1 | 3 | 3 | 3
NA: not applicable
Deafault Resource Supply Elasticities in the MRN Model
|  | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Crude Oil | CRU | 0.3 | 0.51 | 0.65 | 0.76 | 0.83 | 0.88 | 0.91 | 0.94 | 0.96
Natural gas | GAS | 0.6 | 0.72 | 0.8 | 0.86 | 0.9 | 0.93 | 0.95 | 0.97 | 0.98
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.