## Exhibit4A_HydroShapes
Appendix A, Exhibit 4a - NEEM Hydro Shapes
hydro Capacity Factors by Block - Eastern Interconnection
(Blanks indicate no hydro from non-power dam potential in the region)
New Hydro from non-power dams |  | Summer | [9 empty] | Shoulder |  |  |  |  | Winter |  |  |  |  | Annual
| Hours | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935 | Capacity Factor
NEEM Region | Year | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | (calculated)
ENT | All | 0.172 | 0.222 | 0.238 | 0.245 | 0.24 | 0.241 | 0.258 | 0.242 | 0.284 | 0.299 | 0.173 | 0.378 | 0.387 | 0.43 | 0.404 | 0.476 | 0.543 | 0.533 | 0.524 | 0.515 | 0.378
FRCC | All | 0.352 | 0.318 | 0.307 | 0.294 | 0.282 | 0.262 | 0.255 | 0.294 | 0.259 | 0.252 | 0.492 | 0.336 | 0.33 | 0.271 | 0.297 | 0.249 | 0.223 | 0.22 | 0.217 | 0.231 | 0.267
IESO | All
MAPP_CA | All
MAPP_US | All
MISO_IN | All
MISO_MI | All
MISO_MO-IL | All | 0.461 | 0.559 | 0.592 | 0.618 | 0.626 | 0.646 | 0.681 | 0.623 | 0.684 | 0.719 | 0.366 | 0.487 | 0.503 | 0.556 | 0.547 | 0.368 | 0.418 | 0.406 | 0.397 | 0.39 | 0.56
MISO_W | All
MISO_WUMS | All | 0.456 | 0.504 | 0.52 | 0.558 | 0.59 | 0.62 | 0.653 | 0.598 | 0.62 | 0.654 | 0.367 | 0.529 | 0.545 | 0.598 | 0.581 | 0.41 | 0.458 | 0.441 | 0.431 | 0.422 | 0.56
NE | All
NEISO | All | 0.189 | 0.202 | 0.207 | 0.242 | 0.278 | 0.302 | 0.332 | 0.315 | 0.372 | 0.402 | 0.381 | 0.607 | 0.619 | 0.684 | 0.658 | 0.643 | 0.652 | 0.641 | 0.634 | 0.637 | 0.522
NonRTO_Midwest | All | 0.204 | 0.224 | 0.231 | 0.248 | 0.261 | 0.268 | 0.29 | 0.287 | 0.345 | 0.365 | 0.286 | 0.511 | 0.517 | 0.563 | 0.537 | 0.614 | 0.682 | 0.682 | 0.674 | 0.668 | 0.48
NYISO_A-F | All
NYISO_G-I | All
NYISO_J-K | All
PJM_E | All
PJM_ROM | All | 0.23 | 0.244 | 0.249 | 0.261 | 0.27 | 0.274 | 0.293 | 0.3 | 0.342 | 0.358 | 0.326 | 0.541 | 0.544 | 0.587 | 0.563 | 0.612 | 0.63 | 0.633 | 0.627 | 0.636 | 0.479
PJM_ROR | All | 0.363 | 0.436 | 0.46 | 0.481 | 0.488 | 0.502 | 0.532 | 0.493 | 0.551 | 0.58 | 0.327 | 0.507 | 0.517 | 0.571 | 0.554 | 0.446 | 0.501 | 0.492 | 0.483 | 0.476 | 0.527
SOCO | All | 0.117 | 0.142 | 0.151 | 0.154 | 0.151 | 0.15 | 0.159 | 0.153 | 0.173 | 0.182 | 0.136 | 0.286 | 0.289 | 0.312 | 0.296 | 0.354 | 0.424 | 0.408 | 0.397 | 0.382 | 0.267
SPP_N | All
SPP_S | All | 0.28 | 0.432 | 0.482 | 0.503 | 0.493 | 0.512 | 0.55 | 0.468 | 0.518 | 0.552 | 0.098 | 0.255 | 0.268 | 0.305 | 0.284 | 0.143 | 0.2 | 0.192 | 0.185 | 0.174 | 0.358
TVA | All | 0.251 | 0.273 | 0.281 | 0.284 | 0.279 | 0.274 | 0.286 | 0.291 | 0.322 | 0.332 | 0.262 | 0.423 | 0.422 | 0.443 | 0.429 | 0.586 | 0.637 | 0.629 | 0.62 | 0.616 | 0.426
VACAR | All | 0.188 | 0.182 | 0.18 | 0.182 | 0.184 | 0.18 | 0.19 | 0.214 | 0.213 | 0.218 | 0.211 | 0.298 | 0.303 | 0.315 | 0.308 | 0.304 | 0.324 | 0.318 | 0.311 | 0.314 | 0.267
ERCOT | All | 0.22 | 0.284 | 0.305 | 0.299 | 0.277 | 0.269 | 0.272 | 0.239 | 0.243 | 0.252 | 0.167 | 0.272 | 0.271 | 0.278 | 0.268 | 0.226 | 0.255 | 0.247 | 0.241 | 0.238 | 0.257
NWPP | All | 0.362 | 0.397 | 0.408 | 0.425 | 0.435 | 0.443 | 0.452 | 0.407 | 0.441 | 0.463 | 0.26 | 0.321 | 0.322 | 0.331 | 0.331 | 0.286 | 0.315 | 0.315 | 0.308 | 0.311 | 0.372
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit9_CapitalCostDetail
Appendix A, Exhibit 9 - Capital Cost Detail
| Technology |  | AEO: Base Overnight Costs in 2011 (2010$/kW) | Learning by 2025 | Base Overnight Capital Costs in 2025 ($2010/kW) | Gas Pipeline Cost | Electrical transmission | Rail Spur | Nuclear Decommissioning Cost | All-in Capital Cost in 2011 w/o IDC ($2010/kW) | All-in Capital Cost in 2025 w/o IDC ($2010/kW) | Sources
Nuclear | Nuclear |  | 5339 | 10% | 4805.1 | 0 | 21.92 | 0 | 253.9714 | 5614.8914 | 5080.9914 | [1]
PC Bituminous | Advanced Coal |  | 2844 | 5% | 2701.8 | 0 | 21.92 | 18.9873 | 0 | 2884.9073 | 2742.7073 | [2]
CC F-Frame | CC F-Frame |  | 978 | 5% | 929.1 | 9.98 | 21.92 | 0 | 0 | 1009.9 | 961 | [3]
CC H-Frame | CC H-Frame |  | 1003 | 5% | 952.85 | 9.98 | 21.92 | 0 | 0 | 1034.9 | 984.75 | [4]
CT F -Frame | CT F-Frame |  | 665 | 5% | 631.75 | 24.41 | 21.92 | 0 | 0 | 711.33 | 678.08 | [5]
IGCC Bituminous | IGCC |  | 3221 | 5% | 3059.95 | 0 | 21.92 | 18.9873 | 0 | 3261.9073 | 3100.8573 | [6]
IGCC Bituminous w/ Sequestration | IGCC w/seq |  | 5348 | 10.97% | 4761.55 | 0 | 21.92 | 18.9873 | 0 | 5388.9073 | 4802.4573 | [7]
Wind Cost Class 1 & 2 | Wind (options B&A) |  | 2438 | 10% | 2194.2 | 0 | 21.92 | 0 | 0 | 2459.92 | 2216.12 | [8]
Wind Offshore | Wind Offshore |  | 5975 | 20% | 4780 | 0 | 21.92 | 0 | 0 | 5996.92 | 4801.92 | [9]
PV | Photovoltaic |  | 4755 | 20% | 3804 | 0 | 21.92 | 0 | 0 | 4776.92 | 3825.92 | [10]
Solar Thermal | Solar Thermal |  | 4692 | 20% | 3753.6 | 0 | 21.92 | 0 | 0 | 4713.92 | 3775.52 | [11]
Landfill Gas | Landfill Gas |  | 2503.386 | 5% | 2378.2167 | 0 | 21.92 | 0 | 0 | 2525.306 | 2400.1367 | [12]
Biomass | Biomass |  | 3860 | 20% | 3088 | 0 | 21.92 | 18.9873 | 0 | 3900.9073 | 3128.9073 | [13]
Geothermal | Geothermal |  | 4141 | 10% | 3726.9 | 0 | 21.92 | 0 | 0 | 4162.92 | 3748.82 | [14]
| US Hydro |  | 3076 | 0 | 3076 |  | 21.92 |  |  | 3098 | 3098
Wind Options A&B based on New Gen Subteam Recommendations (see summary document)
| [1] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
22% Owner's costs also included, Table 12-1. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
Nuclear Decommissioning Cost: CRA analysis.
| [2] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 3-2. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [3] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 5-1. Owner's Cost: CRA analysis. Gas pipeline source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3.
| [4] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 6-1. Gas pipeline source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Electric transmission source: PJM's
CONE Combined Cycle Revenue Requirements Update, Aug 26, 2008, Table 2, page 3.
| [5] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 9-1. Gas pipeline source: PJM's "CONE Revenue Requirements 2008 Update", Table 5, page 14. PJM's "CONE Revenue Requirements 2008 Update", Table 5, p14.
| [6] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 10-2. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [7] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Learning for IGCC with CCS equals the weighted average of the 5% learning for IGCC
and the 20% learning for CCS from AEO 2010. Contingency and Optimism factors included in AEO 2011 ER overnight costs; 20% Owner's costs also included, Table 11-1. Electric transmission source:
PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur source: CRA assumption.
| [8] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
6% Owner's costs also included, Table 21-1. Electric transmission source: NREL's Wind Deployment System (WinDS) Model - average interconnection cost for the least expensive 300 GW in the US.
| [9] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
25% Owner's costs also included, Table 22-1. Electric transmission source: assumed to be located near load center.
| [10] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
12% Owner's costs also included, Table 24-2. Electric transmission source: Assumed to be the same as wind.
| [11] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
15% Owner's costs also included, Table 23-1. Electric transmission source: Assumed to be the same as wind.
| [12] | AEO 2010 Assumptions, Tables 8.2 & 8.3. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Electrical transmission cost assumed to be the same as nuclear, coal, CC's, etc.
| [13] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
20% Owner's costs also included, Table 14-1. Electric transmission source: PJM's "CONE Combined Cycle Revenue Requirements Update", Aug 26, 2008, Table 2, page 3. Rail spur: CRA assumption.
| [14] | Overnight Capital Costs: AEO 2011 ER, Table 1. Learning Assumptions: AEO 2010 Assumptions, Table 8.3. Contingency and Optimism factors included in AEO 2011 ER overnight costs;
18% Owner's costs also included, Table 17-1. Electric transmission source: Assumed to be the same as wind.
All-in Capital Cost w/o IDC ($2010/kW)
| Technology |  | 2011 | 2015 | 2020 | 2025 | 2030
| Nuclear |  | 5615 | 5462 | 5272 | 5081 | 5081
| Advanced Coal |  | 2885 | 2844 | 2793 | 2743 | 2743
| CC H-Frame |  | 1035 | 1021 | 1003 | 985 | 985
| CT |  | 711 | 702 | 690 | 678 | 678
| IGCC |  | 3262 | 3216 | 3158 | 3101 | 3101
| IGCC w/seq |  | 5389 | 5221 | 5012 | 4802 | 4802
| Wind |  | 2460 | 2390 | 2303 | 2216 | 2216
| Wind Offshore |  | 5997 | 5655 | 5229 | 4802 | 4802
| Photovoltaic |  | 4777 | 4505 | 4166 | 3826 | 3826
| Solar Thermal |  | 4714 | 4446 | 4111 | 3776 | 3776
| Landfill Gas |  | 2525 | 2490 | 2445 | 2400 | 2400
| Biomass |  | 3901 | 3680 | 3405 | 3129 | 3129
| Geothermal |  | 4163 | 4045 | 3897 | 3749 | 3749
| US Hydro |  | 3098 | 3098 | 3098 | 3098 | 3098
Note: 2010 costs are assumed to equal 2011 costs. 2015 and 2020 costs are interpolated on a straightline basis between 2010 and 2025. 2030 costs are assumed to equal 2025 costs.
CCs are assumed to use F-Frame technology until 2015 when the switch is made to H-Frame technology.

## Exhibit12_NewResourceLimits
Appendix A, Exhibit 12 - New Resource Limits
Cumulative New Build GW Limit Potential by NEEM Region | [5 empty] | Note: Forced New Builds are included in this constraint
| Pulverized Coal | Nuclear | On-Shore Wind Class 3 | On-Shore Wind Class 4+ | Off-Shore Wind | Biomass | Photo-voltaic | Landfill Gas | Geoth- ermal | Solar Thermal | IGCC-CCS | Hydro from Non-Power Dams
AZ_NM_SNV | ∞ | ∞ | 224.9 | 107 | - | 6.5 | 10 | 0.05 | 1.5 | 10 | ∞
ENT | ∞ | ∞ | 2.3 | 0.1 | - | 10.1 | 5 | 0.1 | 0 | 0 | ∞ | 1.109
ERCOT | ∞ | ∞ | 286.9 | 97.2 | - | 4.1 | 10 | 0.4 | 0 | 0 | ∞ | 0.628
FRCC | ∞ | ∞ | - | - | - | 2 | 10 | 0.2 | 0 | 0 | ∞ | 0.028
MAPP_US | ∞ | ∞ | 279.5 | 602.5 | - | 5.4 | 1 | 0 | 0 | 0 | ∞
MISO_IN | ∞ | ∞ | 102.3 | 0 | 0.8 | 6.1 | 1.3 | 0.1 | 0 | 0 | ∞
MISO_MI | ∞ | ∞ | 56.8 | 0.6 | 4.4 | 6.1 | 1.3 | 0.1 | 0 | 0 | ∞
MISO_MO_IL | ∞ | ∞ | 105.7 | 5.9 | - | 8.9 | 7 | 0.4 | 0 | 0 | ∞ | 0.28
MISO_W | ∞ | ∞ | 775 | 1199.9 | - | 5.4 | 1 | 0 | 0 | 0 | ∞
MISO_WUMS | ∞ | ∞ | 16.5 | 0.3 | 2.1 | 3.2 | 2 | 0.2 | 0 | 0 | ∞ | 0.001
NE | ∞ | ∞ | 417.8 | 464.2 | - | 10.8 | 2 | 0.1 | 0 | 0 | ∞
NEISO | 0 | ∞ | 16.9 | 5.28 | 8.5 | 1.7 | 12 | 0.7 | 0 | 0 | 4 | 0.003
NonRTO_Midwest | ∞ | ∞ | 0.1 | 0 | - | 6.1 | 1.3 | 0.1 | 0 | 0 | ∞ | 0.746
NP15 | 0 | 0 | 10.8 | 3.4 | 0.1 | 0.8 | 10 | 0.6 | 0.6 | 0.1 | ∞
NWPP | ∞ | ∞ | 653.3 | 591.1 | 0.2 | 9.1 | 5 | 0.3 | 0.5 | 0 | ∞ | 0.335
NYISO_A-F | 0 | ∞ | 12.7 | 0.8 | 0.5 | 1 | 4 | 0.4 | 0 | 0 | ∞
NYISO_G-I | 0 | 0 | 0.3 | 0.1 | 0.2 | 0.8 | 2 | 0.2 | 0 | 0 | ∞
NYISO_J-K | 0 | 0 | 0.2 | 0.2 | 2.4 | 0 | 4 | 0.4 | 0 | 0 | 0
PJM_E | 0 | ∞ | 3.2 | 0.5 | 9.6 | 0.3 | 2 | 0.1 | 0 | 0 | ∞
PJM_ROM | ∞ | ∞ | 5.8 | 1.2 | 16.9 | 2.4 | 4 | 0.3 | 0 | 0 | ∞ | 0.678
PJM_ROR | ∞ | ∞ | 50.4 | 3.2 | 20.2 | 10.6 | 6.9 | 0.4 | 0 | 0 | ∞ | 0.503
RMPA | ∞ | ∞ | 417.1 | 539.9 | - | 3.7 | 5 | 0.1 | 2.6 | 9.4 | ∞
SOCO | ∞ | ∞ | 0.1 | 0 | - | 6.6 | 2 | 0.1 | 0 | 0 | ∞ | 0.867
SP15 | 0 | 0 | 31.2 | 14.9 | - | 0.7 | 10 | 0.6 | 1.5 | 10 | ∞
SPP_N | ∞ | ∞ | 292.8 | 597.7 | - | 6.4 | 2 | 0.1 | 0 | 0 | ∞
SPP_S | ∞ | ∞ | 420.4 | 496.5 | - | 4.5 | 2 | 0.1 | 0 | 0 | ∞ | 0.091
TVA | ∞ | ∞ | 0.1 | 0 | - | 7.4 | 2 | 0.1 | 0 | 0 | ∞ | 0.027
VACAR | ∞ | ∞ | 2.8 | 0.7 | 39.3 | 7 | 1.3 | 0.1 | 0 | 0 | ∞ | 0.052
ALB | 0 | ∞ | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BC | 0 | ∞ | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OH | 0 | ∞ | 0 | 300 | 6.4 | 0 | 0.1 | 0 | 0 | 0 | 0
MAPP_CA | 0 | ∞ | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | ∞ | ∞ | 4202.7 | 5338.5 | 111.5 | 137.7 | 126.1 | 6.5 | 6.7 | 29.5 | ∞ | 5.348
New Pulverized Coal assumed not to be built in California, New York, New England, PJM East, and Canada
New Nuclear assumed not to be built in California or near New York City
CCS is a proposed CRA assumption. |  | PV and solar thermal are proposed CRA assumptions.
On- and Off-shore wind resource potential based on Win DS base case
Biomass based on CRA judgment, informed by USDA/DOE 2005 "Billion Ton Study".
Landfill gas based on CRA judgment, informed by EPA NEEDS report (2006).
Geothermal based on Lovekin & Pletka, GRC Transactions, vol. 33, 2009 (note: could be used for capital costs in lieu of AEO 2011)
Onshore Winds have had a Class 3 category added and Class 4+ values changed based on NREL data, see Exhibit 11
Cumulative GW of New Build Allowed in Total U.S. and Canada through This Year
Note: If %, represents % of total in table above; Forced Builds are included in constraint; if no figure listed the table above applies
| 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Pulverized Coal | 0 | F | F+10
Nuclear | 0 | F1 | *F2 | *F2+15 | *F2+50 | *F2+100 | *F2+150 | *F2+200 | *F2+250
On-Shore Wind | 0 | F | F+175
Off-Shore Wind | 0 | F | F+20
Biomass | 0 | F | 25% | 0.5 | 75% | 100%
Photovoltaic | 0 | F | 10
Landfill Gas | 0 | F | 33% | 0.67 | 100%
Geo Thermal | 0 | F | 33%
Solar Thermal | 0 | F | 33%
IGCC-CCS | 0 | F | F+2 | F+12 | F+32
IGCC | 0 | F | F+60
CCS Retrofits | 0 | F | F+5 | F+25 | F+65
Hydro from non-power dams |  |  | 0.5 | 1
F: Forced builds only | * F2 = F1 + (2016-2020 nuclear builds)
Represents practical constraints on building over time, such as permitting/siting, construction lead times. CRA assumptions.
2020 limits in place for all technologies, most other types unlimited (other than in table above) by 2025
Transfer limits, reserve margins, hurdle rates, and intermittent resource limits will limit construction inside any particular NEEM region
Nuclear likely to be highly economic in certain scenarios, thus on-going limitations in place to represent licensing issues.
IGCC-CCS not available until 2020 (for economic builds); CCS Retrofits available in the same year.
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## Exhibit22_RPS Summary
Exhibit 22 RPS Summary. Details on the RPS calculation are in a separate document Appendix C
National, Regional and State RPS are applied in this future. Qualifying resources for national and super-regional RPS include: hydro (existing and new, including canadian), wind, solar, biomass and landfill gas. Qualifying resources for state RPS vary (see Appendix C)
| NEEM Regions Covered | Load Covered | ACP | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
National RPS
Eastern Interconnect | All except Ontario | 100 | None | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
Super Regional RPS
Northeast | NYISO (A-F, G-I, J-K), NEISO | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
PJM East | PJM_E, PJM_ROM | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
PJM ROR | PJM_ROR | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
Midwest | MISO (W, MI, WUMS, MO-IL, IN), MAPP (CA, US), Non-RTO Midwest | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
Southwest | SPP (N, S), NE, ENT | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
Southeast | SOCO, TVA, VACAR, FRCC | 100 | 200 | 1.5% | 3% | 4.5% | 6% | 7.5% | 9% | 10.5% | 12% | 13.5% | 15% | 16.5% | 18% | 19.5% | 21% | 22.5% | 24% | 25.5% | 27% | 28.5% | 30%
State | Tier | Load Covered (%) | Penalty or ACP ($/MWh) | Target
|  |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Connecticut | RE | 100 | 55 | 11% | 12% | 13% | 14% | 15.5% | 17% | 18.5% | 20% | 22.5% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23%
Delaware | RE | 100 | 80 | 4.982% | 6.8% | 8.1% | 9.4% | 10.7% | 12% | 13.25% | 14.5% | 15.75% | 17% | 17.75% | 18.5% | 19.25% | 20% | 20.75% | 21.5% | 22.5% | 22.5% | 22.5% | 22.5%
| Solar | 100 | 500 | 0.018% | 0.2% | 0.4% | 0.6% | 0.8% | 1% | 1.25% | 1.5% | 1.75% | 2% | 2.25% | 2.5% | 2.75% | 3% | 3.25% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5%
District of Columbia | RE | 100 | 50 | 3.96% | 4.93% | 6.4% | 7.87% | 9.33% | 11.29% | 13.25% | 15.2% | 17.15% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6% | 19.6%
| Solar | 100 | 500 | 0.04% | 0.07% | 0.1% | 0.13% | 0.17% | 0.21% | 0.25% | 0.3% | 0.35% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4% | 0.4%
Illinois | RE | 88.5 | 19.1 | 5.5% | 6.482% | 7.46% | 8.365% | 9.2% | 10.11% | 11.52% | 12.93% | 14.34% | 15.75% | 17.16% | 18.57% | 19.98% | 21.39% | 22.8% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5%
| Solar | 88.5 | 19.1 | 0% | 0.0175% | 0.04% | 0.135% | 0.3% | 0.645% | 0.735% | 0.825% | 0.915% | 1.005% | 1.095% | 1.185% | 1.275% | 1.365% | 1.455% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Kansas | All RE | 81.5 | 100 | 10% | 10% | 10% | 10% | 10% | 15% | 15% | 15% | 15% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
Maine | RE | 98.3 | 60.93 | 34% | 35% | 36% | 37% | 38% | 39% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
Maryland | RE | 98 | 40 | 4.95% | 6.4% | 8% | 10% | 10.1% | 12.2% | 12.55% | 14.9% | 16.2% | 16.5% | 16.85% | 18% | 18% | 18% | 18% | 18% | 18% | 18% | 18% | 18%
| Solar | 98 | 300 | 0.05% | 0.1% | 0.2% | 0.3% | 0.4% | 0.5% | 0.55% | 0.9% | 1.2% | 1.5% | 1.85% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
Massachusetts | RE | 100 | 60.93 | 9.444% | 10.33% | 11.18% | 11.99% | 12.73% | 13.69% | 14.69% | 15.69% | 16.69% | 17.69% | 18.69% | 19.69% | 20.69% | 21.69% | 22.69% | 23.69% | 24.69% | 25.69% | 26.69% | 27.69%
| Solar | 100 | 600 | 0.1564% | 0.2713% | 0.4207% | 0.6149% | 0.8674% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066% | 0.9066%
Michigan | RE | 100 | 40 | Target 2012: 4.8%; Target 2013: 5.645%; Target 2014: 6.75%; Target 2015: 10%
Minnesota | Xcel | 47.8 | 100 | 15% | 18% | 18% | 18% | 18% | 25% | 25% | 25% | 25% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Other Utilities RE | 52.2 | 100 | 7% | 12% | 12% | 12% | 12% | 17% | 17% | 17% | 17% | 20% | 20% | 20% | 20% | 20% | 25% | 25% | 25% | 25% | 25% | 25%
Missouri | RE | 70 | 100 | 1.96% | 1.96% | 1.96% | 4.9% | 4.9% | 4.9% | 4.9% | 9.8% | 9.8% | 9.8% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7% | 14.7%
| Solar | 70 | 600 | 0.04% | 0.04% | 0.04% | 0.1% | 0.1% | 0.1% | 0.1% | 0.2% | 0.2% | 0.2% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3%
New Hampshire | RE | 98.2 | 60.93 | 9.5% | 10.5% | 11.5% | 12.5% | 13.5% | 14.5% | 15.5% | 16.5% | 17.5% | 18.5% | 19.5% | 20.5% | 21.5% | 22.5% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5% | 23.5%
| Solar | 98.2 | 160.01 | 0.08% | 0.15% | 0.2% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3% | 0.3%
New Jersey | RE | 98.3 | 50 | 7.992% | 8.82% | 9.643% | 10.48% | 11.31% | 12.15% | 12.98% | 14.82% | 16.68% | 18.53% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38% | 20.38%
| Solar (in GWh) | 98.3 | 693 | 306 | 442 | 596 | 772 | 965 | 1150 | 1357 | 1591 | 1858 | 2164 | 2518 | 2928 | 3433 | 3989 | 4610 | 5316 | 5316 | 5316 | 5316 | 5316
| Offshore Wind (in MW) |  |  | Target 2021: 1100
New York | RE | 100 | 20 | 3.39% | 4.54% | 5.6% | 6.83% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09% | 8.09%
North Carolina | RE | 100 | 40 | 0% | 2.93% | 2.93% | 2.93% | 5.86% | 5.86% | 5.86% | 9.8% | 9.8% | 9.8% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3% | 12.3%
| Solar | 100 | 200 | 0.02% | 0.07% | 0.07% | 0.07% | 0.14% | 0.14% | 0.14% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2% | 0.2%
Ohio | RE | 88.6 | 45 | 0.97% | 1.44% | 1.91% | 2.38% | 3.35% | 4.32% | 5.28% | 6.24% | 7.2% | 8.16% | 9.12% | 10.08% | 11.04% | 12% | 12% | 12% | 12% | 12% | 12% | 12%
| Solar | 88.6 | 400 | 0.03% | 0.06% | 0.09% | 0.12% | 0.15% | 0.18% | 0.22% | 0.26% | 0.3% | 0.34% | 0.38% | 0.42% | 0.46% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Pennsylvania | RE | 97.3 | 45 | 2.98% | 3.467% | 3.949% | 4.416% | 4.856% | 5.25% | 5.707% | 6.16% | 6.61% | 7.057% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5% | 7.5%
| Solar | 97.3 | 654.37 | 0.0203% | 0.0325% | 0.051% | 0.084% | 0.144% | 0.25% | 0.2933% | 0.34% | 0.39% | 0.4433% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Rhode Island | RE | 99.3 | 60.93 | 5.5% | 6.5% | 7.5% | 8.5% | 10% | 11.5% | 13% | 14.5% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16% | 16%
Wisconsin | RE | 100 | 40 | 6.125% | 6.125% | 6.125% | 6.125% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12% | 10.12%
Montana | RE | 66.6 | 10 | 10% | 10% | 10% | 10% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
New Mexico | RE | 100 | 40 | 5.314% | 5.314% | 5.314% | 5.314% | 8.859% | 9.067% | 9.275% | 9.483% | 9.691% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51% | 12.51%
| Solar | 100 | 200 | 2.031% | 2.031% | 2.031% | 2.031% | 3.046% | 3.046% | 3.046% | 3.046% | 3.046% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062% | 4.062%
Texas | New RE (MW) | 75.9 | 50 | 3384 | 4376 | 4376 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
| Existing RE (MW) | 75.9 | 50 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880
North Dakota | RE | 100 | 10 | 0 | 0 | 0 | 0 | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
Oklahoma | RE | 100 | 10 |  |  |  |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
South Dakota | RE | 71 | 35 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Vermont | RE | 90 | 60.93 | 0.1 | 0.1 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Virginia | RE - 15% of base year (2007) sales by 2025 | 100 | 10 | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Nebraska | RE | 100 | 10 | 0.01 | 0.02 | 0.03 | 0.04 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Louisiana | 233 MW by 2014 | NOT MODELED
West Virginia | 25% by 2025 | NOT MODELED
Areas in RED have been edited given state input
Note on A18: Tyler Ruthven: CHP tier removed as it is not RE
Note on B18: Tyler Ruthven: Tier 1 (all RE) and Tier 2 (Bio RE) combined
Note on C18: Tyler Ruthven: RPS covers IOUs (93.4% of load) but as MOUs are required to come up w/similar RPS, Load % increased to 100%
Note on B19: Tyler Ruthven: RE New and RE Existing Tiers combined
Note on C19: Tyler Ruthven: PS covers ~70% of DE Load (prior to expiration of secondary RPS requirement it covered ~57%) but MOUs required to come up w/simialar RPS requirements by 2013 there fore value is listed as 100%
Note on D19: Tyler Ruthven: DE ACP increasings if a utility uses ACP for more than 1 compliance year. Max value is used for modeling purposes
Note on C20: Tyler Ruthven: PS covers ~70% of DE Load (prior to expiration of secondary RPS requirement it covered ~57%) but MOUs required to come up w/simialar RPS requirements by 2013 there fore value is listed as 100%
Note on D20: Tyler Ruthven: DE ACP increasings if a utility uses ACP for more than 1 compliance year. Max value is used for modeling purposes
Note on A21: Tyler Ruthven: Hydro/MSW tier removed as it expires in 2020
Note on A23: Tyler Ruthven: IL IOU and Competitive Supplier RPSs combined
Note on B23: Tyler Ruthven: Wind and all RE Tiers combined.
Note on C23: Tyler Ruthven: IOU and Competitive Suppliers RPS combined
Note on D23: Tyler Ruthven: Non-IOU ACP applied
Note on C24: Tyler Ruthven: IOU and Competitive Suppliers RPS combined
Note on D24: Tyler Ruthven: Non-IOU ACP applied
Note on D25: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $100 ACP value is set
Note on B26: Tyler Ruthven: Existing Tier (30%) and New RE Tier Combined
Note on D26: Tyler Ruthven: ACP for new RE
Note on A27: Tyler Ruthven: Tier 2 removed as it zeroes out in 2018
Note on C27: Tyler Ruthven: RPS currently covers 93.4% of load but this number will increase when current exemptions lapse therefore it is set at 98%
Note on C28: Tyler Ruthven: RPS currently covers 93.4% of load but this number will increase when current exemptions lapse therefore it is set at 98%
Note on D28: Tyler Ruthven: Solar ACP declines over time from $400 in 2010 to $50 in 2023. Listed value is set at $300
Note on A29: Tyler Ruthven: Tier 3 (MSW) removed as it is not renewable
Note on B29: Tyler Ruthven: Includes both Tier 1 (New RE) and Tier 2 (existing RE). Tier 2 target is 3.6% a year
Note on C29: J Tyler Ruthven: Adjusted from 86 to reflect MA belief that MOUs will meet targets
Note on B30: J Tyler Ruthven: MA Solar targets are assumptions based on MA's 400 MW solar target
Note on C30: J Tyler Ruthven: Adjusted from 86 to reflect MA belief that MOUs will meet targets
Note on A31: Tyler Ruthven: Beyond 2015, utilities are required to purchase the same # of RECs as in 2015, not 10% of load
Note on D31: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on B32: Tyler Ruthven: 1/6 of the target must be met by non-wind/solar resources
Note on D32: Tyler Ruthven: Penalty for non-compliance is monetary penalty no greater than the cost of compliance - so non-compliance not expected and ACP set at $100
Note on D33: Tyler Ruthven: Penalty for non-compliance is monetary penalty no greater than the cost of compliance - so non-compliance not expected and ACP set at $100
Note on D34: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $100 ACP value is set
Note on D35: Tyler Ruthven: Penalty for non-compliance is twice the market value of RECs so don't expect any compliance through ACP so $600 ACP value is set
Note on B36: Tyler Ruthven: Tier 1 (New RE), Tier 3 (Existing Bio) and Tier 4 (existing hydro) combined
Note on D36: Tyler Ruthven: ACP for New RE Tier
Note on B38: Tyler Ruthven: Tier 1 (non-hydro RE) and Tier 2 (all RE) combined
Note on B40: Tyler Ruthven: Recent law creates an Offshore wind tier to support the building of 1100 MW of offshore wind - these facilities will reduce the overall RPS target by the corresponding amount
Note on B41: Tyler Ruthven: Includes Customer-sited Tier (~0.5% point mostly from solar and anaerobic digestors) and Main Tier resources. Does not include Baseline Resources (accounts for ~20% points from NY and imported Hydro) nor the 1% point voluntary goal nor government purchasing requirements
Note on C41: Tyler Ruthven: NY RPS covers 84.7% of load - LIPA is exempt. However, LIPA is pursuing identical goals to the NY RPS therefore its load is included.
Note on D41: Tyler Ruthven: ACP set at approximate level of previous NYSERDA REC purchases
Note on A42: Tyler Ruthven: IOU and MOU/Coop targets combined
Note on B42: Tyler Ruthven: Includes Tier 1 (RE), Tier 3 (Swine Waste) and Tier 4 (Poultry Waste). IOUs can meet 25% of the targets with EE and MOUs can meet 100% of the target with EE. It is assumed here that none of the targets are met with EE.
Note on C42: Tyler Ruthven: IOU and MOU/Coop targets combined so that 100% of load is covered
Note on D42: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on D43: Tyler Ruthven: No Information on ACP found so proxy value of $200 used
Note on A46: Tyler Ruthven: Tier 2 removed as it is not renewable; % values reduced by .02% according to PA modeling
Note on B48: Tyler Ruthven: New RE and Existing RE tiers combined
Note on D49: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on B51: Tyler Ruthven: Combined Tier 1 (all RE), Tier 3 (Wind) and Tier 4 (bio) with MOU RPS
Note on C51: Tyler Ruthven: Combined IOU and MOU RPS
Note on D51: Tyler Ruthven: No Information on ACP found so proxy value of $40 used
Note on B52: Tyler Ruthven: Combined Tier 2 (solar) with Tier 5 (DG)
Note on C52: Tyler Ruthven: Combined IOU and MOU RPS
Note on D52: Tyler Ruthven: No Information on ACP found so proxy value of $200 used
Note on B53: Tyler Ruthven: Targets are in MW
Note on B54: Tyler Ruthven: Targets are in MW
Note on A55: J Tyler Ruthven: ND has indicated that their Voluntary RPS should be modeled in full
Note on D55: J Tyler Ruthven: ND has supported a token $10 ACP
Note on A56: J Tyler Ruthven: OK has indicated that their utilities will meet their RPS target
Note on A58: J Tyler Ruthven: VT has indicated that their Voluntary RPS should be modeled as mandatory
Note on A59: J Tyler Ruthven: VA has indicated that their Voluntary RPS should be modeled in full
Note on A62: J Tyler Ruthven: WV RPS is not voluntary but as it can be met entirely by EE and partially by Natural Gas, Coal or Carbon offsets it is modeled as voluntary

## Exhibit24_CarbonModeling
Values raised from $1.86 based on recent decisions within RGGI
| 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
RGGI States $/tCO2 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89 | 1.89
Cost adder only applicable to RGGI states: |  | CT, DE, MA, MD, ME, NH, NJ, NY, RI and VT
Sources
CRA information
RGGI Nov. 12 Stakeholder Meeting RGGI Modeling Review |  | http://www.rggi.org/stakeholder_meeting

## Exhibit25_Renewable Incentives
Production Tax Credit and Investment Tax Credit Policy Sunsets
PTC and ITC are removed and are not modeled in any year
Details | PTC | Tax credit of ~$22/MWh (2010 $) for every MWh produced for a 10 year period after installation | Primarily utilized by wind generation | http://www.dsireusa.org/incentives/incentive.cfm?Incentive_Code=US13F&re=1&ee=1
| ITC | Tax credit equal to 30% the value of the capital cost of an applicable facility given immediately after the facility is installed | Primarily utilized by solar generation | http://www.dsireusa.org/incentives/incentive.cfm?Incentive_Code=US13F&re=1&ee=1

## Table5_IntermittentRsvContr
Table 5 - Intermittent Resource Contributions
NEEM Region | Technology | Reserve Contribution
All Regions | Photovoltaic | 30%
All Regions | Solar Thermal | 30%
All Regions | Offshore Wind | 30% | Based on EWITS ELCC for Isolated Regions Scenario (weighted average extrapolation) and GE integration studies for NY, New England (CRA had 20%)
California | Wind | 25%
Canada | Wind | 20%
ERCOT | Wind | 9%
New York | Wind | 15% | Based on NYISO input and consideration of September 2010 NYISO Wind Integration Study (http://bit.ly/hP7bm3 ) and wind data for subsequent years from the ISO (CRA had 10%)
PJM (-E, -ROM, -ROR) | Wind | 13%
SPP (including NE) | Wind | 15% | Changed per SSC approval of SPP request for change
TVA | Wind | 12%
IESO | Wind | 11%
MAPP_CA | Wind | 11%
All Other Regions | Wind | 15%

## Table 7_NewBuildCostParameters
Table 7 - New Build Costs and Characteristics
2/15/11- Capital costs changed to match 2015 and 2025 costs from Exhibit 9. Previously, this table mistakenly had costs for 2010 and 2020.
| Capital Costs |  | Performance Data
Technology | 2015 All-in Capital Cost (2010$/kW) | 2025 All-in Capital Cost (2010$/kW) | Total FOM (2010$/kW-yr) | Total VOM (2010$/MWh) | 2010 Heat Rate - HHV (Btu/kWh) | 2015+ Heat Rate - HHV (Btu/kWh)
Nuclear | 5462.3485 | 5080.9914 | 88.75 | 2.04 | 10488 | 10488
Advanced Coal | 2844.2788 | 2742.7073 | 29.67 | 4.25 | 9200 | 8800
CC H-Frame | 1020.5714 | 984.75 | 14.39 | 3.43 | 7050 | 6430
CT | 701.83 | 678.08 | 6.7 | 9.87 | 9750 | 9750
IGCC | 3215.8931 | 3100.8573 | 48.9 | 6.87 | 8700 | 8700
IGCC w/seq | 5221.3502 | 4802.4573 | 69.3 | 8.04 | 10700 | 10235
Wind | 2390.2629 | 2216.12 | 28.07 | 0 | NA | NA
Wind Offshore | 5655.4914 | 4801.92 | 53.33 | 0 | NA | NA
Photovoltaic | 4505.2057 | 3825.92 | 16.7 | 0 | NA | NA
Solar Thermal | 4445.8057 | 3775.52 | 64 | 0 | NA | NA
Landfill Gas | 2489.5433 | 2400.1367 | 120.3265 | 0 | 13648 | 13648
Biomass | 3680.3359 | 3128.9073 | 100.5 | 5 | 13500 | 13500
Geothermal | 4044.6057 | 3748.82 | 84.27 | 9.64 | NA | NA
US Hydro | 3098 | 3098 | 14.24 | 0 | NA | NA
CRA only models H-Frame CC so F-frame CC not listed.
Wind Options A&B based on New Gen Subteam Recommendations (see summary document)
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note on F7: CRA International: add 400 to start at AEO 2010 starting value
Note on G11: CRA International: ratio

## Table14_IntermittentGenLimits
Table 14 - Intermittent Generation Limits (annual MWh basis)
Duplicates of Super-Regions
Intermittency Region | NEEM Regions | Inter-mittency Limit
Southwest | SPP-S, SPP-N, NE, ENT | 0.35
PJM_ROR | PJM_ROR | 0.35
PJM-MAAC | PJM_E, PJM_ROM | 0.35
Midwest | MISO_W, MISO_MI, MISO_WUMS, MISO_IN, MISO_MO_IL, MAPP_CA, MAPP_US, Non-RTO Midwest | 0.35
Northeast | NYISO_A-F, NYISO_G-I, NYISO_J-K, NEISO | 0.35
South | TVA, VACAR, SOCO, FRCC | 0.35
IESO | IESO | 0.35
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## F6S1-Rev Xfr Limit
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regioonal Implementation
Sensitivity | F6S1-Rev Xfr Limit 25% | Revised transfer capability - overload charges at 25% of the average shadow prices
Worksheets Affected

## F6S2-High Load Growth
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation
Sensitivity | F6S2-High Load Growth | High load growth
Worksheets Affected
| Table 2 | BELOW
| Table 3 | BELOW
Table 2 - Energy Demand | [5 empty] | Table 3 - Peak Demand
Updated for AEO2011 growth rates after 2020 - 2/8/11 |  |  |  |  | Growth Adder
1%
NEEM Region | AEO Region for 2020+ Growth Rate | 2011 Energy (GWh) | 2011-2020 Growth Rate | 2020-2050 Growth Rate |  | NEEM Region | Reserve Margin Region | AEO Region for 2020+ Growth Rate | 2011 Peak (MW) | 2011-2020 Growth Rate | 2020-2050 Growth Rate
AZ_NM_SNV_Coal | AZNM | 124203 | 0.029 | 0.0232 |  | AZ_NM_SNV_Coal | AZ_NM_SNV | AZNM | 27169 | 0.0293 | 0.0232
ENT | SRDA | 159507 | 0.0239 | 0.0154 |  | ENT | ENT | SRDA | 29623 | 0.0229 | 0.0154
ERCOT | ERCT | 316195 | 0.0271 | 0.0166 |  | ERCOT | ERCOT | ERCT | 64964 | 0.0271 | 0.0166
FRCC | FRCC | 229020 | 0.0275 | 0.0225 |  | FRCC | FRCC | FRCC | 46580 | 0.0266 | 0.0225
MAPP_US | MROW | 29828 | 0.0188 | 0.0179 |  | MAPP_US | MAPP_US | MROW | 5512 | 0.019 | 0.0179
MISO_IN | RFCW | 97101 | 0.0206 | 0.0162 |  | MISO_IN | MISO | RFCW | 17792 | 0.0212 | 0.0162
MISO_MI | RFCM | 94678 | 0.0181 | 0.018 |  | MISO_MI | MISO | RFCM | 19930 | 0.018 | 0.018
MISO_MO-IL | SRGW | 96157 | 0.0188 | 0.0183 |  | MISO_MO-IL | MISO | SRGW | 18713 | 0.0193 | 0.0183
MISO_W | MROW | 137739 | 0.0186 | 0.0179 |  | MISO_W | MISO | MROW | 25929 | 0.0194 | 0.0179
MISO_WUMS | MROE | 66425 | 0.0211 | 0.0167 |  | MISO_WUMS | MISO | MROE | 12790 | 0.0211 | 0.0167
NE | MROW | 29481 | 0.0283 | 0.0179 |  | NE | SPP | MROW | 5580 | 0.0254 | 0.0179
NEISO | NEWE | 129768 | 0.0102 | 0.01 |  | NEISO | NEISO | NEWE | 27165 | 0.015 | 0.0112
NonRTO_Midwest | SRCE | 58092 | 0.0268 | 0.0149 |  | NonRTO_Midwest | NonRTO_Midwest | SRCE | 10858 | 0.0257 | 0.0149
NP15 | CAMX | 110014 | 0.0195 | 0.0201 |  | NP15 | CA | CAMX | 24248 | 0.0225 | 0.0201
NWPP_Coal | NWPP | 246983 | 0.0231 | 0.0195 |  | NWPP_Coal | NWPP | NWPP | 41760 | 0.0202 | 0.0195
NYISO_A-F (note A) | NYUP | 63281 | 0.012 | 0.0152 |  | NYISO_A-F (Note A) | NYISO | NYUP | 11269 | 0.011 | 0.0152
NYISO_G-I (note A) | NYCW | 19524 | 0.0115 | 0.0186 |  | NYISO_G-I (Note A) | NYISO | NYCW | 4280 | 0.0091 | 0.0186
NYISO_J-K (note A) | NYLI | 73315 | 0.0139 | 0.0189 |  | NYISO_J-K (Note A) | NYISO | NYLI | 16622 | 0.0111 | 0.0189
PJM_E | RFCE | 135784 | 0.0001 | 0.0168 |  | PJM_E | PJM | RFCE | 31190 | 0.0007 | 0.0168
PJM_ROM | RFCE | 144050 | 0.0187 | 0.0168 |  | PJM_ROM | PJM | RFCE | 25797 | 0.0172 | 0.0168
PJM_ROR | RFCW | 520031 | 0.014 | 0.0162 |  | PJM_ROR | PJM | RFCW | 95148 | 0.0143 | 0.0162
RMPA | RMPA | 72067 | 0.0222 | 0.0228 |  | RMPA | RMPA | RMPA | 12556 | 0.0235 | 0.0228
SOCO | SRSE | 249461 | 0.0296 | 0.0182 |  | SOCO | SOCO | SRSE | 48104 | 0.032 | 0.0182
SP15 | CAMX | 179898 | 0.0232 | 0.0201 |  | SP15 | CA | CAMX | 35048 | 0.0233 | 0.0201
SPP_N | SPNO | 75955 | 0.0223 | 0.0192 |  | SPP_N | SPP | SPNO | 15530 | 0.0305 | 0.0192
SPP_S | SPSO | 163927 | 0.0216 | 0.0165 |  | SPP_S | SPP | SPSO | 32752 | 0.0207 | 0.0165
TVA | SRCE | 173627 | 0.0198 | 0.0149 |  | TVA | TVA | SRCE | 33073 | 0.0263 | 0.0149
VACAR | SRVC | 236109 | 0.0264 | 0.0197 |  | VACAR | VACAR | SRVC | 46538 | 0.0254 | 0.0197
ALB | NA | 64239 | 0.0259 | 0.0242 |  | ALB | ALB | NA | 9176 | 0.0264 | 0.0242
BC | NA | 63168 | 0.0216 | 0.0197 |  | BC | BC | NA | 11441 | 0.0217 | 0.0197
IESO | NA | 142313 | 0.0071 | 0.0168 |  | IESO | IESO | NA | 23625 | 0.0071 | 0.0169
MAPP_CA | NA | 48058 | 0.0302 | 0.0179 |  | MAPP_CA | MAPP_CA | NA | 8007 | 0.0271 | 0.0179
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling. | [5 empty] | The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder. | [5 empty] | As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## F6S3-High Gas $
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/Regional Implementation
Sensitivity | F6S3-High Gas $ | High gas prices
Worksheets Affected | Exhibit 16A - HH Gas Prices | Below
| Exhibit 16B - Natural Gas Prices | Next sheet
| Exhibit 21 - MRN Inputs | Not relevant since MRN not run for Sensitivities
Appendix A, Exhibit 16 - Natural Gas Prices, High Case
Shift in Price from
Year | BAU Henry Hub Spot Price (2010$/MMBtu) | Hi Gas Henry Hub Price (2010$/mmBtu) | Increase in Price in 2010$/mmbtu for 16B | Increase in 2009$/mmBtu for Exhibit 19 below | AEO2011 HH (2009$/MMBtu) | AEO2011 in 2010$/MMBtu | AEO 2010 Reference HH (2008$/MMBtu) | AEO2010 in 2010$/MMBtu | AEO2011 | AEO2010 | Composite Price in 2010$/MMBtu | AEO2010 Hi Gas Scenario in 2008 $/mmbtu | Ratio of 2010 Hi Gas to Reference
2011 | 4.52 | 4.9871 | 0.46716 | 0.4631 | 4.4807 | 4.52 | 5.6827 | 5.7863 | 100% | 0% | 4.52 | 6.27 | 1.1034
2012 | 4.6066 | 5.4749 | 0.86838 | 0.86084 | 4.5665 | 4.6066 | 6.1725 | 6.2851 | 92.86% | 7.143% | 4.7265 | 7.15 | 1.1584
2013 | 4.743 | 5.8798 | 1.1368 | 1.1269 | 4.7018 | 4.743 | 6.129 | 6.2408 | 85.71% | 14.29% | 4.957 | 7.27 | 1.1862
2014 | 4.8077 | 6.216 | 1.4083 | 1.3961 | 4.7659 | 4.8077 | 6.0861 | 6.1971 | 78.57% | 21.43% | 5.1054 | 7.41 | 1.2175
2015 | 4.8478 | 6.3994 | 1.5516 | 1.5381 | 4.8057 | 4.8478 | 6.2707 | 6.3851 | 71.43% | 28.57% | 5.287 | 7.59 | 1.2104
2016 | 4.877 | 6.5602 | 1.6832 | 1.6685 | 4.8346 | 4.877 | 6.377 | 6.4933 | 64.29% | 35.71% | 5.4543 | 7.67 | 1.2028
2017 | 4.9247 | 6.7013 | 1.7766 | 1.7611 | 4.882 | 4.9247 | 6.385 | 6.5014 | 57.14% | 42.86% | 5.6005 | 7.64 | 1.1966
2018 | 5.0029 | 6.8959 | 1.893 | 1.8766 | 4.9594 | 5.0029 | 6.434 | 6.5514 | 50% | 50% | 5.7771 | 7.68 | 1.1937
2019 | 5.0807 | 7.1947 | 2.114 | 2.0957 | 5.0365 | 5.0807 | 6.5062 | 6.6249 | 42.86% | 57.14% | 5.9631 | 7.85 | 1.2065
2020 | 5.2234 | 7.2971 | 2.0738 | 2.0558 | 5.178 | 5.2234 | 6.64 | 6.7611 | 35.71% | 64.29% | 6.2119 | 7.8 | 1.1747
2021 | 5.3794 | 7.2702 | 1.8908 | 1.8744 | 5.3327 | 5.3794 | 6.7401 | 6.863 | 28.57% | 71.43% | 6.4391 | 7.61 | 1.1291
2022 | 5.533 | 7.6139 | 2.0809 | 2.0628 | 5.4849 | 5.533 | 6.9289 | 7.0553 | 21.43% | 78.57% | 6.7291 | 7.84 | 1.1315
2023 | 5.7164 | 8.0698 | 2.3534 | 2.3329 | 5.6668 | 5.7164 | 6.9571 | 7.084 | 14.29% | 85.71% | 6.8886 | 8.15 | 1.1715
2024 | 5.8971 | 8.4842 | 2.5871 | 2.5646 | 5.8459 | 5.8971 | 6.9144 | 7.0405 | 7.143% | 92.86% | 6.9588 | 8.43 | 1.2192
2025 | 6.0656 | 8.8689 | 2.8033 | 2.7789 | 6.0129 | 6.0656 | 6.9918 | 7.1193 | 0% | 100% | 7.1193 | 8.71 | 1.2458
2026 | 6.2063 | 9.0827 | 2.8764 | 2.8514 | 6.1524 | 6.2063 | 7.152 | 7.2825 | 0% | 100% | 7.2825 | 8.92 | 1.2472
2027 | 6.335 | 9.3067 | 2.9718 | 2.9459 | 6.2799 | 6.335 | 7.292 | 7.425 | 0% | 100% | 7.425 | 9.14 | 1.2534
2028 | 6.4203 | 9.6733 | 3.253 | 3.2247 | 6.3645 | 6.4203 | 7.5303 | 7.6676 | 0% | 100% | 7.6676 | 9.5 | 1.2616
2029 | 6.4822 | 9.9584 | 3.4762 | 3.446 | 6.4259 | 6.4822 | 7.7743 | 7.9161 | 0% | 100% | 7.9161 | 9.78 | 1.258
2030 | 6.5596 | 10.1824 | 3.6228 | 3.5913 | 6.5026 | 6.5596 | 8.0498 | 8.1967 | 0% | 100% | 8.1967 | 10 | 1.2423
2031 | 6.6804 | 10.1111 | 3.4307 | 3.4009 | 6.6224 | 6.6804 | 8.389 | 8.542 | 0% | 100% | 8.542 | 9.93 | 1.1837
2032 | 6.818 | 10.3657 | 3.5477 | 3.5169 | 6.7588 | 6.818 | 8.4968 | 8.6518 | 0% | 100% | 8.6518 | 10.18 | 1.1981
2033 | 6.9363 | 10.7119 | 3.7756 | 3.7428 | 6.876 | 6.9363 | 8.5296 | 8.6852 | 0% | 100% | 8.6852 | 10.52 | 1.2333
2034 | 7.0702 | 10.9766 | 3.9065 | 3.8725 | 7.0088 | 7.0702 | 8.7486 | 8.9082 | 0% | 100% | 8.9082 | 10.78 | 1.2322
2035 | 7.2541 | 11.0785 | 3.8243 | 3.7911 | 7.1911 | 7.2541 | 8.8799 | 9.0418 | 0% | 100% | 9.0418 | 10.88 | 1.2252
Between 2035 and 2050, CRA proposes to increase gas prices at the |  |  |  |  | EIA Case ID |  | EIA Case ID
same rate of increase for the 2030-2035 period. |  |  |  |  | d120810c |  | d111809a
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
|  |  |  | From AEO2011 Refernce |  | 2008 | 2009 | 2010
|  |  |  | GDP Chain-type Price Index (2005=1.000) |  | 1.086 | 1.0962 | 1.1058
1.0088
Not relevant since MRN not run for Sensitivities
Exhibit 21 Gas Wellhead Price |  |  | Price rise starts in 2011 | [5 empty] | 2035-2050 use 2035 price increase
|  | Price increase | 0 | 1.5381 | 2.0558 | 2.7789 | 3.5913 | 3.7911 | 3.7911 | 3.7911 | 3.7911
|  |  | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
BAU Gas Wellhead price (2009 dollars per million Btu)
High Gas Wellhead price (2009 dollars per million Btu)

## F6S3_Exhibit16B
Appendix A, Exhibit 16B - Natural Gas Prices, High Case | Increase in Price from BAU_Sen5_High_Gas$ | [7 empty] | 1.0088 | convert 2009$ to 2010$
BAU Hi Gas Cost Sensitivity |  |  | 0.46716 | 0.86838 | 1.1368 | 1.4083 | 1.5516 | 1.6832 | 1.7766 | 1.893 | 2.114 | 2.0738 | 1.8908 | 2.0809 | 2.3534 | 2.5871 | 2.8033 | 2.8764 | 2.9718 | 3.253 | 3.4762 | 3.6228 | 3.4307 | 3.5477 | 3.7756 | 3.9065 | 3.8243
Between 2035 and 2050, CRA proposes to increase gas prices at the
| 2010$/MMBtu |  |  |  | same rate of increase for the 2030-2035 period.
| Region | Season | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| ALB | Summer | 4.6372 | 4.8884 | 5.1068 | 5.2483 | 5.5116 | 5.9432 | 6.2066 | 6.483 | 6.814 | 6.9038 | 6.8608 | 7.2309 | 7.6934 | 8.0671 | 8.4033 | 8.5764 | 8.7818 | 9.193 | 9.5262 | 9.7728 | 9.6807 | 9.9177 | 10.2956 | 10.6265 | 10.7543
| ALB | Winter | 4.9672 | 5.2184 | 5.5268 | 5.6683 | 5.9516 | 6.4232 | 6.6966 | 6.993 | 7.334 | 7.4438 | 7.4208 | 7.8009 | 8.2834 | 8.6671 | 9.0233 | 9.2164 | 9.4218 | 9.853 | 10.2062 | 10.4628 | 10.3807 | 10.6277 | 11.0256 | 11.3765 | 11.5243
| ALB | Shoulder | 4.8072 | 5.0184 | 5.2468 | 5.3883 | 5.6516 | 6.1032 | 6.3766 | 6.643 | 6.984 | 7.0838 | 7.0408 | 7.4209 | 7.8934 | 8.2571 | 8.6033 | 8.7864 | 9.0018 | 9.403 | 9.7462 | 10.0028 | 9.9107 | 10.1577 | 10.5356 | 10.8765 | 11.0043
| AZ_NM_SNV_Gas | Summer | 5.0272 | 5.1784 | 5.4068 | 5.6283 | 5.8116 | 6.0632 | 6.2766 | 6.543 | 6.914 | 6.9938 | 6.9708 | 7.3509 | 7.7634 | 8.1171 | 8.4333 | 8.6364 | 8.8618 | 9.273 | 9.6062 | 9.8428 | 9.7407 | 9.9777 | 10.3256 | 10.6165 | 10.6943
| AZ_NM_SNV_Gas | Winter | 5.1872 | 5.5584 | 5.8568 | 6.1283 | 6.3216 | 6.5732 | 6.8066 | 7.093 | 7.474 | 7.5838 | 7.5708 | 7.9709 | 8.3934 | 8.7671 | 9.0933 | 9.3164 | 9.5618 | 9.993 | 10.3262 | 10.5728 | 10.4907 | 10.7277 | 11.0956 | 11.4065 | 11.5143
| AZ_NM_SNV_Gas | Shoulder | 5.0072 | 5.2984 | 5.5668 | 5.7983 | 5.9816 | 6.2432 | 6.4566 | 6.743 | 7.114 | 7.2038 | 7.1708 | 7.5609 | 7.9834 | 8.3471 | 8.6633 | 8.8764 | 9.1118 | 9.523 | 9.8562 | 10.1028 | 10.0007 | 10.2377 | 10.5956 | 10.8865 | 10.9743
| BC | Summer | 4.5872 | 4.7884 | 5.0068 | 5.1583 | 5.4116 | 5.8332 | 6.0966 | 6.363 | 6.694 | 6.7838 | 6.7308 | 7.1009 | 7.5534 | 7.9271 | 8.2533 | 8.4364 | 8.6418 | 9.033 | 9.3762 | 9.6228 | 9.5207 | 9.7477 | 10.1256 | 10.4565 | 10.5743
| BC | Winter | 5.0672 | 5.3484 | 5.6368 | 5.7883 | 6.0616 | 6.5432 | 6.8366 | 7.123 | 7.474 | 7.5838 | 7.5608 | 7.9509 | 8.4434 | 8.8271 | 9.1933 | 9.3864 | 9.6018 | 10.023 | 10.3762 | 10.6428 | 10.5607 | 10.8177 | 11.2256 | 11.5765 | 11.7243
| BC | Shoulder | 4.7672 | 5.0184 | 5.2568 | 5.3983 | 5.6716 | 6.1132 | 6.3866 | 6.663 | 7.004 | 7.1038 | 7.0608 | 7.4309 | 7.9034 | 8.2871 | 8.6233 | 8.8064 | 9.0118 | 9.423 | 9.7662 | 10.0228 | 9.9407 | 10.1777 | 10.5556 | 10.8965 | 11.0343
| ENT | Summer | 5.0372 | 5.2784 | 5.5768 | 5.7883 | 6.0116 | 6.2332 | 6.3766 | 6.563 | 6.844 | 6.9038 | 6.8608 | 7.1609 | 7.5934 | 7.9771 | 8.3333 | 8.5264 | 8.7418 | 9.093 | 9.3462 | 9.5428 | 9.4707 | 9.7277 | 10.0456 | 10.3165 | 10.4243
| ENT | Winter | 5.2572 | 5.6584 | 6.0068 | 6.2383 | 6.4616 | 6.6832 | 6.8466 | 7.043 | 7.324 | 7.4038 | 7.3608 | 7.6909 | 8.1234 | 8.5371 | 8.8933 | 9.1064 | 9.3318 | 9.683 | 9.9462 | 10.1428 | 10.0807 | 10.3577 | 10.6956 | 10.9765 | 11.1043
| ENT | Shoulder | 5.1172 | 5.4084 | 5.7268 | 5.9383 | 6.1616 | 6.3832 | 6.5266 | 6.723 | 7.004 | 7.0738 | 7.0208 | 7.3409 | 7.7734 | 8.1671 | 8.5233 | 8.7264 | 8.9418 | 9.283 | 9.5462 | 9.7528 | 9.6807 | 9.9377 | 10.2556 | 10.5365 | 10.6543
| ERCOT | Summer | 5.0572 | 5.2784 | 5.5568 | 5.7683 | 5.9816 | 6.2032 | 6.3566 | 6.543 | 6.824 | 6.8938 | 6.8508 | 7.1609 | 7.5834 | 7.9771 | 8.3233 | 8.5164 | 8.7318 | 9.083 | 9.3362 | 9.5328 | 9.4507 | 9.7177 | 10.0356 | 10.3065 | 10.4143
| ERCOT | Winter | 5.1572 | 5.5984 | 5.9468 | 6.1583 | 6.4016 | 6.6332 | 6.7866 | 6.983 | 7.274 | 7.3538 | 7.3108 | 7.6409 | 8.0834 | 8.4871 | 8.8433 | 9.0464 | 9.2718 | 9.623 | 9.8862 | 10.0928 | 10.0207 | 10.2977 | 10.6256 | 10.9065 | 11.0343
| ERCOT | Shoulder | 5.0872 | 5.3684 | 5.6868 | 5.8883 | 6.1216 | 6.3432 | 6.4966 | 6.693 | 6.964 | 7.0438 | 6.9908 | 7.3109 | 7.7434 | 8.1371 | 8.4933 | 8.6864 | 8.9018 | 9.253 | 9.5062 | 9.7128 | 9.6407 | 9.8877 | 10.2156 | 10.4965 | 10.6143
| FRCC | Summer | 6.2472 | 6.4284 | 6.6268 | 6.8383 | 7.0316 | 7.2232 | 7.3766 | 7.543 | 7.804 | 7.8838 | 7.8008 | 8.1509 | 8.6034 | 9.0271 | 9.4133 | 9.6064 | 9.8218 | 10.173 | 10.4362 | 10.6428 | 10.5507 | 10.7977 | 11.1456 | 11.4065 | 11.5443
| FRCC | Winter | 6.2472 | 6.6884 | 6.9468 | 7.1783 | 7.3916 | 7.5832 | 7.7366 | 7.903 | 8.174 | 8.2538 | 8.1908 | 8.5409 | 9.0134 | 9.4471 | 9.8433 | 10.0464 | 10.2618 | 10.613 | 10.8862 | 11.1028 | 11.0207 | 11.2777 | 11.6256 | 11.8965 | 12.0543
| FRCC | Shoulder | 6.2172 | 6.4884 | 6.6968 | 6.9283 | 7.1216 | 7.3132 | 7.4666 | 7.633 | 7.894 | 7.9738 | 7.9008 | 8.2509 | 8.7034 | 9.1271 | 9.5133 | 9.7164 | 9.9318 | 10.283 | 10.5462 | 10.7528 | 10.6707 | 10.9177 | 11.2656 | 11.5365 | 11.6743
| HQ | Summer | 4.2472 | 4.9984 | 5.5668 | 5.9583 | 5.9816 | 5.9632 | 6.0666 | 6.213 | 6.444 | 6.4238 | 6.2708 | 6.5209 | 6.9134 | 7.2171 | 7.5433 | 7.6764 | 7.8418 | 8.213 | 8.5262 | 8.7828 | 8.6907 | 8.8877 | 9.1956 | 9.3965 | 9.3043
| HQ | Winter | 6.9372 | 6.6084 | 7.0268 | 7.4483 | 7.4216 | 7.3532 | 7.4566 | 7.603 | 7.834 | 7.8138 | 7.6608 | 7.9409 | 8.3534 | 8.6771 | 9.0433 | 9.1764 | 9.3518 | 9.763 | 10.0962 | 10.3828 | 10.3107 | 10.5477 | 10.8756 | 11.0865 | 10.9843
| HQ | Shoulder | 4.6272 | 5.4184 | 5.9668 | 6.3683 | 6.3816 | 6.3432 | 6.4466 | 6.593 | 6.824 | 6.7938 | 6.6508 | 6.9009 | 7.3034 | 7.6071 | 7.9433 | 8.0764 | 8.2418 | 8.623 | 8.9362 | 9.2028 | 9.1107 | 9.3177 | 9.6456 | 9.8365 | 9.7443
| MAPP_CA | Summer | 4.6972 | 4.9284 | 5.1268 | 5.3383 | 5.5716 | 5.8132 | 6.0166 | 6.253 | 6.594 | 6.6838 | 6.6108 | 6.9209 | 7.3434 | 7.7271 | 8.1233 | 8.3064 | 8.5118 | 8.903 | 9.2162 | 9.4528 | 9.3507 | 9.5777 | 9.9356 | 10.2365 | 10.3543
| MAPP_CA | Winter | 5.0472 | 5.3084 | 5.5968 | 5.8183 | 6.0616 | 6.3232 | 6.5566 | 6.803 | 7.154 | 7.2538 | 7.2208 | 7.5309 | 7.9734 | 8.3771 | 8.8033 | 9.0064 | 9.2318 | 9.623 | 9.9562 | 10.2128 | 10.1207 | 10.3677 | 10.7256 | 11.0565 | 11.2043
| MAPP_CA | Shoulder | 4.8672 | 5.0684 | 5.2968 | 5.5083 | 5.7416 | 5.9832 | 6.2066 | 6.443 | 6.784 | 6.8738 | 6.8308 | 7.1409 | 7.5634 | 7.9471 | 8.3633 | 8.5564 | 8.7718 | 9.153 | 9.4762 | 9.7228 | 9.6207 | 9.8577 | 10.2156 | 10.5265 | 10.6443
| MAPP_US | Summer | 4.6972 | 4.9284 | 5.1268 | 5.3383 | 5.5716 | 5.8132 | 6.0166 | 6.253 | 6.594 | 6.6838 | 6.6108 | 6.9209 | 7.3434 | 7.7271 | 8.1233 | 8.3064 | 8.5118 | 8.903 | 9.2162 | 9.4528 | 9.3507 | 9.5777 | 9.9356 | 10.2365 | 10.3543
| MAPP_US | Winter | 5.0472 | 5.3084 | 5.5968 | 5.8183 | 6.0616 | 6.3232 | 6.5566 | 6.803 | 7.154 | 7.2538 | 7.2208 | 7.5309 | 7.9734 | 8.3771 | 8.8033 | 9.0064 | 9.2318 | 9.623 | 9.9562 | 10.2128 | 10.1207 | 10.3677 | 10.7256 | 11.0565 | 11.2043
| MAPP_US | Shoulder | 4.8672 | 5.0684 | 5.2968 | 5.5083 | 5.7416 | 5.9832 | 6.2066 | 6.443 | 6.784 | 6.8738 | 6.8308 | 7.1409 | 7.5634 | 7.9471 | 8.3633 | 8.5564 | 8.7718 | 9.153 | 9.4762 | 9.7228 | 9.6207 | 9.8577 | 10.2156 | 10.5265 | 10.6443
| MISO_IN | Summer | 4.7972 | 4.9784 | 5.3068 | 5.5283 | 5.7816 | 5.9032 | 6.0766 | 6.293 | 6.464 | 6.5138 | 6.4408 | 6.7509 | 7.1834 | 7.5571 | 7.9133 | 8.0964 | 8.3118 | 8.683 | 8.9662 | 9.1928 | 9.0907 | 9.3277 | 9.6856 | 9.9665 | 10.0443
| MISO_IN | Winter | 5.0872 | 5.3784 | 5.7268 | 5.9683 | 6.2316 | 6.3432 | 6.5366 | 6.763 | 6.924 | 6.9838 | 6.9308 | 7.2509 | 7.6934 | 8.0871 | 8.4533 | 8.6664 | 8.8818 | 9.273 | 9.5562 | 9.7928 | 9.7007 | 9.9577 | 10.3156 | 10.6165 | 10.7143
| MISO_IN | Shoulder | 4.8872 | 5.1184 | 5.4468 | 5.6783 | 5.9416 | 6.0532 | 6.2366 | 6.453 | 6.624 | 6.6738 | 6.6108 | 6.9209 | 7.3634 | 7.7371 | 8.0933 | 8.2964 | 8.5118 | 8.883 | 9.1762 | 9.3928 | 9.3007 | 9.5477 | 9.9056 | 10.1965 | 10.2643
| MISO_MI | Summer | 4.6572 | 4.8584 | 5.0768 | 5.2983 | 5.5316 | 5.7532 | 5.9566 | 6.163 | 6.454 | 6.5238 | 6.4408 | 6.7509 | 7.1734 | 7.5471 | 7.9033 | 8.0864 | 8.2918 | 8.683 | 8.9762 | 9.2028 | 9.1007 | 9.3477 | 9.7056 | 9.9965 | 10.0743
| MISO_MI | Winter | 4.7672 | 5.0984 | 5.3768 | 5.6183 | 5.8616 | 6.1032 | 6.3066 | 6.513 | 6.814 | 6.8838 | 6.8208 | 7.1409 | 7.5834 | 7.9571 | 8.3233 | 8.5164 | 8.7418 | 9.133 | 9.4262 | 9.6628 | 9.5707 | 9.8177 | 10.2056 | 10.4965 | 10.5943
| MISO_MI | Shoulder | 4.6972 | 4.9184 | 5.1668 | 5.3883 | 5.6216 | 5.8532 | 6.0566 | 6.273 | 6.554 | 6.6338 | 6.5608 | 6.8709 | 7.3034 | 7.6771 | 8.0233 | 8.2164 | 8.4318 | 8.813 | 9.1062 | 9.3328 | 9.2507 | 9.4877 | 9.8556 | 10.1465 | 10.2243
| MISO_MO_IL | Summer | 4.7472 | 4.9584 | 5.1768 | 5.3883 | 5.6116 | 5.9132 | 6.0866 | 6.263 | 6.564 | 6.5438 | 6.5008 | 6.7509 | 7.1834 | 7.5471 | 7.9633 | 8.1464 | 8.3618 | 8.783 | 9.1162 | 9.3328 | 9.2307 | 9.4777 | 9.8256 | 10.1165 | 10.2043
| MISO_MO_IL | Winter | 5.0872 | 5.3584 | 5.5968 | 5.8283 | 6.0616 | 6.3732 | 6.5566 | 6.743 | 7.064 | 7.0538 | 7.0108 | 7.2809 | 7.7234 | 8.1071 | 8.5433 | 8.7264 | 8.9518 | 9.403 | 9.7362 | 9.9728 | 9.8907 | 10.1377 | 10.5056 | 10.8065 | 10.9243
| MISO_MO_IL | Shoulder | 4.8572 | 5.0984 | 5.3168 | 5.5383 | 5.7716 | 6.0632 | 6.2466 | 6.433 | 6.734 | 6.7238 | 6.6708 | 6.9409 | 7.3734 | 7.7371 | 8.1633 | 8.3564 | 8.5618 | 9.003 | 9.3262 | 9.5528 | 9.4607 | 9.7077 | 10.0656 | 10.3565 | 10.4643
| MISO_W | Summer | 4.6972 | 4.9184 | 5.1368 | 5.3483 | 5.5716 | 5.8232 | 6.0266 | 6.263 | 6.604 | 6.6938 | 6.6308 | 6.9309 | 7.3534 | 7.7371 | 8.1333 | 8.3264 | 8.5318 | 8.913 | 9.2362 | 9.4728 | 9.3707 | 9.5977 | 9.9556 | 10.2465 | 10.3643
| MISO_W | Winter | 5.0572 | 5.3184 | 5.5868 | 5.8183 | 6.0516 | 6.3132 | 6.5366 | 6.793 | 7.144 | 7.2438 | 7.2008 | 7.5209 | 7.9634 | 8.3671 | 8.7833 | 8.9864 | 9.2118 | 9.613 | 9.9462 | 10.1828 | 10.1007 | 10.3377 | 10.7156 | 11.0365 | 11.1743
| MISO_W | Shoulder | 4.8472 | 5.0684 | 5.2968 | 5.5083 | 5.7416 | 5.9932 | 6.2066 | 6.453 | 6.784 | 6.8738 | 6.8308 | 7.1409 | 7.5634 | 7.9571 | 8.3633 | 8.5564 | 8.7618 | 9.163 | 9.4762 | 9.7228 | 9.6307 | 9.8577 | 10.2156 | 10.5265 | 10.6543
| MISO_WUMS | Summer | 4.5872 | 4.7884 | 5.0368 | 5.2583 | 5.4816 | 5.7132 | 5.9166 | 6.113 | 6.404 | 6.4738 | 6.3908 | 6.7009 | 7.1234 | 7.4871 | 7.8433 | 8.0264 | 8.2418 | 8.623 | 8.9162 | 9.1428 | 9.0407 | 9.2777 | 9.6456 | 9.9265 | 10.0043
| MISO_WUMS | Winter | 4.8672 | 5.1684 | 5.4268 | 5.6683 | 5.9016 | 6.1432 | 6.3566 | 6.573 | 6.864 | 6.9438 | 6.8808 | 7.2009 | 7.6334 | 8.0271 | 8.3833 | 8.5864 | 8.8018 | 9.203 | 9.4962 | 9.7328 | 9.6507 | 9.8977 | 10.2756 | 10.5765 | 10.6743
| MISO_WUMS | Shoulder | 4.6772 | 4.9284 | 5.1668 | 5.3983 | 5.6316 | 5.8632 | 6.0666 | 6.273 | 6.564 | 6.6338 | 6.5608 | 6.8709 | 7.3034 | 7.6771 | 8.0333 | 8.2164 | 8.4318 | 8.823 | 9.1162 | 9.3428 | 9.2407 | 9.4877 | 9.8556 | 10.1565 | 10.2343
| NE | Summer | 4.6972 | 4.9184 | 5.1368 | 5.3483 | 5.5816 | 5.8232 | 6.0366 | 6.273 | 6.614 | 6.6938 | 6.6408 | 6.9409 | 7.3634 | 7.7471 | 8.1533 | 8.3364 | 8.5418 | 8.933 | 9.2462 | 9.4828 | 9.3907 | 9.6177 | 9.9656 | 10.2765 | 10.3943
| NE | Winter | 5.0672 | 5.3184 | 5.5768 | 5.8083 | 6.0416 | 6.3032 | 6.5266 | 6.773 | 7.124 | 7.2238 | 7.1908 | 7.5009 | 7.9434 | 8.3371 | 8.7633 | 8.9764 | 9.1918 | 9.583 | 9.9162 | 10.1628 | 10.0807 | 10.3077 | 10.6856 | 11.0065 | 11.1443
| NE | Shoulder | 4.8272 | 5.0684 | 5.2968 | 5.5083 | 5.7416 | 5.9932 | 6.2066 | 6.453 | 6.794 | 6.8838 | 6.8308 | 7.1409 | 7.5634 | 7.9571 | 8.3733 | 8.5564 | 8.7718 | 9.163 | 9.4862 | 9.7228 | 9.6307 | 9.8577 | 10.2256 | 10.5265 | 10.6543
| NEISO | Summer | 4.2272 | 4.9784 | 5.5568 | 5.9383 | 5.9516 | 5.9332 | 6.0266 | 6.173 | 6.404 | 6.3738 | 6.2208 | 6.4709 | 6.8534 | 7.1471 | 7.4833 | 7.5964 | 7.7618 | 8.133 | 8.4362 | 8.6928 | 8.5907 | 8.7977 | 9.1056 | 9.2965 | 9.2043
| NEISO | Winter | 7.0072 | 6.6684 | 7.0768 | 7.5183 | 7.5016 | 7.4232 | 7.5266 | 7.693 | 7.924 | 7.9138 | 7.7608 | 8.0409 | 8.4734 | 8.7971 | 9.1633 | 9.3164 | 9.4918 | 9.903 | 10.2462 | 10.5328 | 10.4707 | 10.7077 | 11.0456 | 11.2565 | 11.1643
| NEISO | Shoulder | 4.5472 | 5.3684 | 5.9168 | 6.3183 | 6.3216 | 6.2932 | 6.3966 | 6.543 | 6.774 | 6.7538 | 6.5908 | 6.8509 | 7.2434 | 7.5571 | 7.8933 | 8.0164 | 8.1818 | 8.563 | 8.8862 | 9.1428 | 9.0507 | 9.2677 | 9.5756 | 9.7765 | 9.6843
| NonRTO_midwest | Summer | 5.2572 | 5.5384 | 5.8268 | 6.0583 | 6.2716 | 6.4832 | 6.6066 | 6.783 | 7.044 | 7.0938 | 7.0508 | 7.3509 | 7.7834 | 8.1771 | 8.5333 | 8.7364 | 8.9418 | 9.283 | 9.5362 | 9.7328 | 9.6507 | 9.8877 | 10.2256 | 10.4965 | 10.6143
| NonRTO_midwest | Winter | 5.5872 | 5.9584 | 6.3068 | 6.5583 | 6.7716 | 6.9832 | 7.1366 | 7.303 | 7.564 | 7.6238 | 7.6008 | 7.9109 | 8.3534 | 8.7671 | 9.1433 | 9.3464 | 9.5718 | 9.913 | 10.1762 | 10.3728 | 10.3007 | 10.5677 | 10.9156 | 11.1965 | 11.3343
| NonRTO_midwest | Shoulder | 5.3472 | 5.6784 | 5.9968 | 6.2383 | 6.4416 | 6.6532 | 6.7966 | 6.973 | 7.224 | 7.2738 | 7.2408 | 7.5409 | 7.9834 | 8.3771 | 8.7433 | 8.9464 | 9.1618 | 9.503 | 9.7562 | 9.9628 | 9.8707 | 10.1277 | 10.4656 | 10.7265 | 10.8543
| NP15 | Summer | 5.3372 | 5.5184 | 5.7468 | 5.9283 | 6.1016 | 6.3032 | 6.5666 | 6.863 | 7.264 | 7.3338 | 7.3308 | 7.7109 | 8.1134 | 8.4971 | 8.8533 | 9.0664 | 9.2818 | 9.693 | 10.0162 | 10.2528 | 10.1407 | 10.3777 | 10.7356 | 11.0265 | 11.1543
| NP15 | Winter | 5.4672 | 5.8384 | 6.1268 | 6.3383 | 6.5116 | 6.7132 | 6.9966 | 7.313 | 7.724 | 7.8038 | 7.8208 | 8.2109 | 8.6334 | 9.0371 | 9.4033 | 9.6264 | 9.8518 | 10.263 | 10.6062 | 10.8428 | 10.7507 | 10.9877 | 11.3656 | 11.6765 | 11.8143
| NP15 | Shoulder | 5.3872 | 5.6084 | 5.8568 | 6.0583 | 6.2216 | 6.4232 | 6.6966 | 7.003 | 7.394 | 7.4738 | 7.4708 | 7.8509 | 8.2634 | 8.6571 | 9.0233 | 9.2364 | 9.4518 | 9.863 | 10.1862 | 10.4228 | 10.3307 | 10.5577 | 10.9256 | 11.2265 | 11.3543
| NWPP_Gas | Summer | 4.6172 | 4.8084 | 5.0268 | 5.1783 | 5.4316 | 5.8632 | 6.1266 | 6.393 | 6.724 | 6.8138 | 6.7608 | 7.1209 | 7.5934 | 7.9571 | 8.2933 | 8.4664 | 8.6718 | 9.073 | 9.4062 | 9.6528 | 9.5607 | 9.7877 | 10.1656 | 10.4965 | 10.6143
| NWPP_Gas | Winter | 5.0272 | 5.3284 | 5.6068 | 5.7583 | 6.0416 | 6.5132 | 6.7966 | 7.083 | 7.444 | 7.5538 | 7.5208 | 7.9209 | 8.4134 | 8.7871 | 9.1533 | 9.3464 | 9.5618 | 9.983 | 10.3362 | 10.6028 | 10.5307 | 10.7777 | 11.1756 | 11.5265 | 11.6843
| NWPP_Gas | Shoulder | 4.7572 | 5.0084 | 5.2568 | 5.3983 | 5.6716 | 6.1132 | 6.3866 | 6.663 | 7.004 | 7.0938 | 7.0508 | 7.4309 | 7.9034 | 8.2771 | 8.6233 | 8.8064 | 9.0118 | 9.423 | 9.7662 | 10.0228 | 9.9307 | 10.1677 | 10.5556 | 10.8865 | 11.0243
| NYISO_A-F | Summer | 5.3272 | 5.7384 | 6.2968 | 6.7783 | 6.8516 | 6.6432 | 6.6766 | 6.763 | 6.944 | 6.8738 | 6.7008 | 6.9409 | 7.3334 | 7.6471 | 8.0333 | 8.1764 | 8.3618 | 8.753 | 9.0562 | 9.3328 | 9.2507 | 9.4777 | 9.7856 | 9.9865 | 9.9143
| NYISO_A-F | Winter | 5.6772 | 6.1884 | 6.8568 | 7.3683 | 7.4316 | 7.1732 | 7.1966 | 7.283 | 7.444 | 7.3638 | 7.1908 | 7.4309 | 7.8334 | 8.1571 | 8.5433 | 8.6864 | 8.8818 | 9.273 | 9.5862 | 9.8728 | 9.8007 | 10.0277 | 10.3556 | 10.5465 | 10.4643
| NYISO_A-F | Shoulder | 5.4572 | 5.8984 | 6.5068 | 6.9983 | 7.0616 | 6.8332 | 6.8566 | 6.953 | 7.124 | 7.0438 | 6.8708 | 7.1209 | 7.5034 | 7.8171 | 8.2033 | 8.3464 | 8.5418 | 8.933 | 9.2362 | 9.5128 | 9.4407 | 9.6577 | 9.9756 | 10.1665 | 10.0943
| NYISO_G-I | Summer | 4.6072 | 5.3384 | 5.9668 | 6.4483 | 6.5216 | 6.3332 | 6.3666 | 6.453 | 6.634 | 6.5538 | 6.3908 | 6.6309 | 7.0134 | 7.3271 | 7.6933 | 7.8264 | 8.0118 | 8.383 | 8.6962 | 8.9528 | 8.8707 | 9.0877 | 9.3956 | 9.5765 | 9.5043
| NYISO_G-I | Winter | 6.9672 | 6.8284 | 7.3768 | 7.9083 | 7.9516 | 7.6632 | 7.6866 | 7.773 | 7.944 | 7.8538 | 7.6808 | 7.9309 | 8.3334 | 8.6671 | 9.0833 | 9.2364 | 9.4418 | 9.843 | 10.1662 | 10.4628 | 10.4007 | 10.6377 | 10.9756 | 11.1865 | 11.1043
| NYISO_G-I | Shoulder | 4.9272 | 5.7184 | 6.3468 | 6.8383 | 6.9116 | 6.6932 | 6.7266 | 6.813 | 6.984 | 6.9138 | 6.7308 | 6.9709 | 7.3634 | 7.6771 | 8.0633 | 8.2064 | 8.3918 | 8.773 | 9.0762 | 9.3628 | 9.2707 | 9.4977 | 9.8056 | 10.0065 | 9.9243
| NYISO_J-K | Summer | 4.3472 | 5.1484 | 5.8068 | 6.2683 | 6.3416 | 6.1632 | 6.1966 | 6.293 | 6.474 | 6.3938 | 6.2208 | 6.4609 | 6.8334 | 7.1371 | 7.5033 | 7.6364 | 7.8118 | 8.193 | 8.4862 | 8.7428 | 8.6507 | 8.8577 | 9.1656 | 9.3565 | 9.2743
| NYISO_J-K | Winter | 7.4972 | 7.1684 | 7.6768 | 8.2383 | 8.2816 | 7.9832 | 7.9966 | 8.073 | 8.244 | 8.1538 | 7.9808 | 8.2309 | 8.6534 | 8.9871 | 9.4233 | 9.5764 | 9.7918 | 10.203 | 10.5262 | 10.8328 | 10.7807 | 11.0277 | 11.3656 | 11.5765 | 11.5043
| NYISO_J-K | Shoulder | 4.6572 | 5.5784 | 6.2168 | 6.6983 | 6.7716 | 6.5632 | 6.5966 | 6.683 | 6.864 | 6.7838 | 6.6108 | 6.8509 | 7.2334 | 7.5471 | 7.9233 | 8.0664 | 8.2518 | 8.623 | 8.9362 | 9.2128 | 9.1207 | 9.3377 | 9.6556 | 9.8465 | 9.7743
| OH | Summer | 5.3172 | 5.7284 | 6.2968 | 6.7783 | 6.8516 | 6.6432 | 6.6766 | 6.783 | 6.964 | 6.8838 | 6.7208 | 6.9609 | 7.3534 | 7.6771 | 8.0633 | 8.2064 | 8.4018 | 8.783 | 9.0962 | 9.3728 | 9.3007 | 9.5177 | 9.8356 | 10.0365 | 9.9643
| OH | Winter | 5.6872 | 6.1984 | 6.8568 | 7.3783 | 7.4316 | 7.1732 | 7.1966 | 7.273 | 7.434 | 7.3438 | 7.1808 | 7.4109 | 7.8134 | 8.1271 | 8.5133 | 8.6564 | 8.8418 | 9.233 | 9.5462 | 9.8328 | 9.7507 | 9.9777 | 10.2956 | 10.4865 | 10.4143
| OH | Shoulder | 5.4472 | 5.8984 | 6.4968 | 6.9883 | 7.0516 | 6.8332 | 6.8566 | 6.943 | 7.114 | 7.0338 | 6.8608 | 7.1009 | 7.4934 | 7.8171 | 8.1933 | 8.3364 | 8.5318 | 8.913 | 9.2262 | 9.5028 | 9.4307 | 9.6477 | 9.9656 | 10.1565 | 10.0843
| PJM_E | Summer | 4.7272 | 5.5084 | 6.1168 | 6.4483 | 6.6216 | 6.5032 | 6.5466 | 6.643 | 6.834 | 6.7838 | 6.6208 | 6.8709 | 7.2634 | 7.5871 | 7.9533 | 8.1064 | 8.2918 | 8.683 | 8.9762 | 9.2328 | 9.1507 | 9.3577 | 9.6756 | 9.8665 | 9.7943
| PJM_E | Winter | 6.9272 | 6.7384 | 7.2368 | 7.5683 | 7.7216 | 7.5532 | 7.5766 | 7.673 | 7.854 | 7.7938 | 7.6408 | 7.8909 | 8.3034 | 8.6571 | 9.0533 | 9.2164 | 9.4218 | 9.833 | 10.1462 | 10.4328 | 10.3507 | 10.5877 | 10.9156 | 11.1165 | 11.0443
| PJM_E | Shoulder | 5.0672 | 5.8584 | 6.4568 | 6.7883 | 6.9516 | 6.8232 | 6.8566 | 6.953 | 7.144 | 7.0838 | 6.9308 | 7.1809 | 7.5734 | 7.9071 | 8.2833 | 8.4364 | 8.6318 | 9.023 | 9.3262 | 9.5928 | 9.5007 | 9.7177 | 10.0456 | 10.2465 | 10.1643
| PJM_ROM | Summer | 4.8472 | 5.5684 | 6.1568 | 6.4983 | 6.6616 | 6.5432 | 6.5766 | 6.683 | 6.874 | 6.8138 | 6.6608 | 6.9009 | 7.3034 | 7.6271 | 7.9933 | 8.1464 | 8.3318 | 8.723 | 9.0262 | 9.2828 | 9.1907 | 9.3977 | 9.7156 | 9.9165 | 9.8343
| PJM_ROM | Winter | 6.7172 | 6.6384 | 7.1768 | 7.4983 | 7.6616 | 7.4932 | 7.5266 | 7.623 | 7.794 | 7.7338 | 7.5808 | 7.8409 | 8.2534 | 8.5971 | 8.9933 | 9.1564 | 9.3618 | 9.763 | 10.0862 | 10.3628 | 10.2907 | 10.5177 | 10.8556 | 11.0565 | 10.9743
| PJM_ROM | Shoulder | 5.1372 | 5.8784 | 6.4668 | 6.8083 | 6.9716 | 6.8432 | 6.8766 | 6.973 | 7.154 | 7.0938 | 6.9408 | 7.1909 | 7.5834 | 7.9171 | 8.3033 | 8.4564 | 8.6418 | 9.033 | 9.3462 | 9.6028 | 9.5207 | 9.7477 | 10.0556 | 10.2565 | 10.1843
| PJM_ROR | Summer | 4.6772 | 4.9484 | 5.2768 | 5.4983 | 5.7516 | 5.8732 | 6.0566 | 6.263 | 6.434 | 6.4838 | 6.4108 | 6.7209 | 7.1534 | 7.5271 | 7.8733 | 8.0664 | 8.2818 | 8.653 | 8.9362 | 9.1528 | 9.0507 | 9.2977 | 9.6456 | 9.9365 | 10.0043
| PJM_ROR | Winter | 5.2972 | 5.4384 | 5.7768 | 6.0083 | 6.2716 | 6.3932 | 6.5866 | 6.813 | 6.974 | 7.0338 | 6.9708 | 7.3009 | 7.7534 | 8.1371 | 8.5033 | 8.7164 | 8.9318 | 9.323 | 9.6162 | 9.8428 | 9.7507 | 10.0077 | 10.3756 | 10.6765 | 10.7743
| PJM_ROR | Shoulder | 4.7972 | 5.0984 | 5.4368 | 5.6683 | 5.9316 | 6.0432 | 6.2266 | 6.443 | 6.614 | 6.6638 | 6.6008 | 6.9109 | 7.3534 | 7.7271 | 8.0833 | 8.2764 | 8.4918 | 8.873 | 9.1562 | 9.3828 | 9.2907 | 9.5277 | 9.8856 | 10.1765 | 10.2543
| RMPA | Summer | 4.9672 | 5.2084 | 5.4468 | 5.6583 | 5.8616 | 6.1032 | 6.3066 | 6.563 | 6.904 | 7.0038 | 6.9608 | 7.3309 | 7.7534 | 8.1171 | 8.4333 | 8.6464 | 8.8918 | 9.313 | 9.6362 | 9.8728 | 9.7707 | 9.9977 | 10.3356 | 10.6365 | 10.7443
| RMPA | Winter | 5.3072 | 5.6484 | 5.9568 | 6.1783 | 6.3816 | 6.6432 | 6.8566 | 7.133 | 7.504 | 7.6138 | 7.5808 | 7.9709 | 8.4134 | 8.7971 | 9.1333 | 9.3664 | 9.6218 | 10.063 | 10.3962 | 10.6428 | 10.5507 | 10.7977 | 11.1556 | 11.4665 | 11.6043
| RMPA | Shoulder | 5.0672 | 5.3584 | 5.6268 | 5.8383 | 6.0316 | 6.2932 | 6.4966 | 6.763 | 7.114 | 7.2138 | 7.1708 | 7.5509 | 7.9834 | 8.3571 | 8.6733 | 8.8964 | 9.1518 | 9.573 | 9.8962 | 10.1428 | 10.0407 | 10.2777 | 10.6256 | 10.9265 | 11.0443
| SOCO | Summer | 5.4472 | 5.6384 | 5.9768 | 6.2283 | 6.4116 | 6.6032 | 6.7066 | 6.873 | 7.114 | 7.1638 | 7.1208 | 7.4209 | 7.8534 | 8.2471 | 8.6133 | 8.7964 | 9.0218 | 9.353 | 9.6262 | 9.8028 | 9.7507 | 9.9977 | 10.3356 | 10.6065 | 10.7243
| SOCO | Winter | 5.6072 | 6.0084 | 6.4268 | 6.6983 | 6.8816 | 7.0832 | 7.1866 | 7.353 | 7.604 | 7.6638 | 7.6208 | 7.9409 | 8.3834 | 8.7871 | 9.1633 | 9.3664 | 9.6018 | 9.943 | 10.2162 | 10.4128 | 10.3707 | 10.6277 | 10.9756 | 11.2565 | 11.3843
| SOCO | Shoulder | 5.5072 | 5.7584 | 6.1268 | 6.3783 | 6.5616 | 6.7632 | 6.8666 | 7.033 | 7.274 | 7.3238 | 7.2908 | 7.5909 | 8.0234 | 8.4271 | 8.7833 | 8.9964 | 9.2018 | 9.553 | 9.8162 | 10.0028 | 9.9507 | 10.2077 | 10.5456 | 10.8165 | 10.9343
| SP15 | Summer | 5.3072 | 5.4884 | 5.7168 | 5.9083 | 6.0816 | 6.2732 | 6.5366 | 6.853 | 7.244 | 7.3138 | 7.3108 | 7.6809 | 8.0834 | 8.4771 | 8.8233 | 9.0364 | 9.2518 | 9.663 | 9.9862 | 10.2228 | 10.1107 | 10.3377 | 10.7056 | 10.9965 | 11.1243
| SP15 | Winter | 5.5172 | 5.8584 | 6.1568 | 6.3683 | 6.5316 | 6.7432 | 7.0166 | 7.333 | 7.744 | 7.8338 | 7.8508 | 8.2409 | 8.6634 | 9.0571 | 9.4333 | 9.6564 | 9.8818 | 10.303 | 10.6362 | 10.8828 | 10.7907 | 11.0277 | 11.3956 | 11.7065 | 11.8543
| SP15 | Shoulder | 5.3772 | 5.6084 | 5.8668 | 6.0583 | 6.2316 | 6.4232 | 6.7066 | 7.003 | 7.404 | 7.4738 | 7.4808 | 7.8609 | 8.2734 | 8.6571 | 9.0233 | 9.2364 | 9.4618 | 9.873 | 10.1962 | 10.4328 | 10.3307 | 10.5577 | 10.9356 | 11.2265 | 11.3543
| SPP_N | Summer | 4.9072 | 5.0984 | 5.2868 | 5.4883 | 5.7116 | 5.9832 | 6.2166 | 6.453 | 6.754 | 6.8438 | 6.7808 | 7.1309 | 7.5734 | 7.9471 | 8.3033 | 8.4864 | 8.6918 | 9.073 | 9.3962 | 9.6228 | 9.5207 | 9.7477 | 10.1056 | 10.4065 | 10.5243
| SPP_N | Winter | 5.1272 | 5.4584 | 5.7068 | 5.9283 | 6.1616 | 6.4532 | 6.7066 | 6.953 | 7.264 | 7.3638 | 7.3208 | 7.6809 | 8.1434 | 8.5371 | 8.9033 | 9.0964 | 9.3118 | 9.713 | 10.0462 | 10.2828 | 10.1907 | 10.4277 | 10.7956 | 11.1065 | 11.2543
| SPP_N | Shoulder | 4.9672 | 5.2084 | 5.4268 | 5.6283 | 5.8516 | 6.1532 | 6.3866 | 6.613 | 6.934 | 7.0238 | 6.9708 | 7.3109 | 7.7634 | 8.1571 | 8.5033 | 8.6964 | 8.9018 | 9.293 | 9.6262 | 9.8528 | 9.7407 | 9.9677 | 10.3356 | 10.6465 | 10.7643
| SPP_S | Summer | 5.0072 | 5.2484 | 5.5268 | 5.7283 | 5.9516 | 6.1732 | 6.3266 | 6.513 | 6.794 | 6.8738 | 6.8208 | 7.1409 | 7.5634 | 7.9471 | 8.2933 | 8.4864 | 8.7018 | 9.053 | 9.3062 | 9.5028 | 9.4307 | 9.6877 | 10.0056 | 10.2765 | 10.3843
| SPP_S | Winter | 5.2372 | 5.6184 | 5.9768 | 6.1983 | 6.4316 | 6.6632 | 6.8266 | 7.023 | 7.314 | 7.3938 | 7.3608 | 7.6909 | 8.1334 | 8.5371 | 8.8933 | 9.0964 | 9.3218 | 9.683 | 9.9462 | 10.1528 | 10.0907 | 10.3577 | 10.6856 | 10.9765 | 11.1043
| SPP_S | Shoulder | 5.0772 | 5.3684 | 5.6768 | 5.8883 | 6.1116 | 6.3432 | 6.4966 | 6.683 | 6.974 | 7.0538 | 7.0008 | 7.3209 | 7.7534 | 8.1471 | 8.4933 | 8.6964 | 8.9118 | 9.263 | 9.5262 | 9.7228 | 9.6507 | 9.9077 | 10.2356 | 10.5165 | 10.6243
| TVA | Summer | 5.2772 | 5.5284 | 5.8268 | 6.0683 | 6.2716 | 6.4832 | 6.6166 | 6.793 | 7.054 | 7.1038 | 7.0608 | 7.3609 | 7.7934 | 8.1871 | 8.5533 | 8.7564 | 8.9618 | 9.303 | 9.5662 | 9.7628 | 9.6707 | 9.9177 | 10.2656 | 10.5265 | 10.6543
| TVA | Winter | 5.5272 | 5.9584 | 6.3068 | 6.5583 | 6.7716 | 6.9832 | 7.1266 | 7.303 | 7.554 | 7.6138 | 7.5808 | 7.8909 | 8.3334 | 8.7471 | 9.1233 | 9.3264 | 9.5518 | 9.893 | 10.1462 | 10.3528 | 10.2707 | 10.5277 | 10.8756 | 11.1465 | 11.2843
| TVA | Shoulder | 5.3772 | 5.6784 | 5.9968 | 6.2283 | 6.4416 | 6.6532 | 6.7966 | 6.963 | 7.224 | 7.2738 | 7.2408 | 7.5409 | 7.9834 | 8.3771 | 8.7333 | 8.9464 | 9.1518 | 9.493 | 9.7562 | 9.9528 | 9.8707 | 10.1177 | 10.4556 | 10.7265 | 10.8543
| VACAR | Summer | 5.6272 | 6.0584 | 6.4068 | 6.4783 | 6.6916 | 6.9132 | 7.0966 | 7.273 | 7.544 | 7.5738 | 7.5008 | 7.7909 | 8.2034 | 8.6071 | 8.9633 | 9.1664 | 9.4018 | 9.783 | 10.0862 | 10.2828 | 10.1807 | 10.3977 | 10.7356 | 10.9765 | 11.0443
| VACAR | Winter | 6.8772 | 6.8684 | 7.1668 | 7.2083 | 7.4416 | 7.6732 | 7.8666 | 8.043 | 8.324 | 8.3838 | 8.3008 | 8.6109 | 9.0634 | 9.4871 | 9.8633 | 10.0864 | 10.3418 | 10.743 | 11.0462 | 11.2528 | 11.1707 | 11.3977 | 11.7456 | 12.0165 | 12.1043
| VACAR | Shoulder | 5.8172 | 6.2984 | 6.6368 | 6.6983 | 6.9216 | 7.1532 | 7.3266 | 7.503 | 7.784 | 7.8238 | 7.7408 | 8.0409 | 8.4734 | 8.8771 | 9.2433 | 9.4464 | 9.6918 | 10.083 | 10.3762 | 10.5928 | 10.4807 | 10.7077 | 11.0456 | 11.2965 | 11.3743
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## F6S4-CES
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/Regional Implementation
Sensitivity | F6S4-CES | Clean Energy Standard
Worksheets Affected | Exh 22
National and Regional CES are applied in this sensitivity. State RPS are also applied (unchanged from their BAU assumptions). CES qualifying resources include: hydro (existing and new, including canadian), wind, solar, biomass, landfill gas, nuclear, natural gas (at 50% value - each MWh of natural gas generation earns .5 CES credits), and clean coal (clean coal counts for the CES in proportion to what percentage of carbon is captured and sequestered). Qualifying resources for state RPS vary (see Appendix C)
| NEEM Regions Covered | Load Covered | ACP | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
National RPS
Eastern Interconnect | All except Ontario | 100 | None | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70% | 0.7 | 0.7 | 0.7 | 0.7 | 0.8
Super Regional RPS
Northeast | NYISO (A-F, G-I, J-K), NEISO | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%
PJM East | PJM_E, PJM_ROM | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%
PJM ROR | PJM_ROR | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%
Midwest | MISO (W, MI, WUMS, MO-IL, IN), MAPP (CA, US), Non-RTO Midwest | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%
Southwest | SPP (N, S), NE, ENT | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%
Southeast | SOCO, TVA, VACAR, FRCC | 100 | 200 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50% | 50% | 50% | 50% | 50% | 60% | 60% | 60% | 60% | 60% | 70%

## F6S6-Increase Cdn hydro
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation | In this sensitivity, MRN-NEEM will be allowed to select pseudo-generators up to their full potential
Sensitivity | F6S6-Increase Cdn hydro | Increased imported Canadian hydro
Worksheets Affected | Exh 19
Existing (Baseline Infrastructure) Flows | Transfer Capacity | Annual Transfer Capacity | Details |  | Reserve Margin Credit
HQ-NE | 2920 | 0.95 | Lines used to 95% capacity (2774) 24 hours a day |  | 100% (2920 MW)
HQ-NY | 1500 | 0.95 | Lines used to 95% capacity (1425) 24 hours a day |  | 80% (1200 MW)
HQ-OH | 3000 | 0.09 | Lines used at 400 MW capacity 16 hours a day and zero capacity 8 hours a day |  | 0
NB-NE | 1400 | 0.95 | Lines used to 95% capacity (1330) 24 hours a day |  | 100% (1400 MW)
|  | HQ/Maritimes Pseudo Generator Definitions |  |  |  | Manitoba and Ontario Hydro are not pseudo generators
Parameter | Source/Definition | HQ/NE Hydro | HQ- New York Hydro | HQ-OH Hydro | Maritime-NE Hydro | Manitoba | Ontario
First Year Available |  | 2020 | 2020 | 2020 | 2020 | 2020 | 2020
Overnight Capital Cost ($/kW) | AEO 2011 (in 2010 dollars) | 3076 | 3076 | 3076 | 3076 | 3076 | 3800 (2010 Canadian $)
Operating Life | hydro asset life time around 100 Years | 100 | 100 | 100 | 100 | 100 | 100
8760 hr gen shape | Use normalized load shapes | 75% Capacity (Pseudo-gen at 0 capacity hours 1-6 and full capacity hours 7-24) | 75% Capacity (Pseudo-gen at 0 capacity hours 1-6 and full capacity hours 7-24) | Based on load shape for OH | 75% Capacity (Pseudo-gen at 0 capacity hours 1-6 and full capacity hours 7-24) | 75% Capacity (Pseudo-gen at 0 capacity hours 1-6 and full capacity hours 7-24) | 75% Capacity (Pseudo-gen at 0 capacity hours 1-6 and full capacity hours 7-24)
FOM ($/kW-year) | AEO 2011 (in 2010 dollars) (table 4) | 14.24 | 14.24 | 14.24 | 14.24 | 14.24 | 14.24
VOM ($/MWh) | AEO 2011 (in 2010 dollars) (table 4) | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | $7 - represent hurdle/wheel cost for transmision between regions | 0 (hurdle/wheel cost already accounted for in NEEM regions) | 0 (hurdle/wheel cost already accounted for in NEEM regions)
Emissions (lb/MMBtu) | AEO 2011 | 0 | 0 | 0 | 0 | 0 | 0
Reserve Margin Contribution | Based on Regional Stakeholder Input | 1 | 0.8 | 0 | 1 | 1 | 1
Resource Potential | provided by regional experts | Total possible HQ-NE by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | Total possible HQ-NE by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | Total possible HQ-OH by 2030 - 2500 MW. Total exports from HQ: 2020 - 3000 MW; 2025 - 4150 MW; 2030 - 5300 MW | 500 MW - available 2020 | 695 (by 2020) +1495 (by2025) +2460 (by 2025) | 250 MW - available 2020
Refurb cost at end of life | EOL refurb cost of 100 year life asset won’t impact EIPC study | 0 | 0 | 0 | 0 | 0 | 0
Fixed Charge Rate | Use average EIPC FCR values for technologies as FCR spread is small | 0.112 | 0.112 | 0.112 | 0.112 | 0.112 | 0.112
Change in Capital Cost over Time | Use AEO 2010 learning rates for hydro | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Electrical Transmission ($/kW) | CRA from Exhibit 9 (based on coal plant) | 21.92 | 21.92 | 21.92 | 21.92 | 21.92 | 21.92
Regional Multiplier | For lack of data in AEO2011 assumed | 1 | 1 | 1 | 1 | 1 | 1

## F6S7_High_PHEV
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation
Sensitivity | F6S7-High PHEV | Modified load block shapes in recognition of increased PHEV levels 37% charging during peak hrs
Worksheets Affected | Exhibit 21 MRN Impacts | PHEV/EV fleet and consequent VMT will be increased over the AEO2011 amounts by 2x in 2015, 4X in 2020, 7x in 2025, and 10x in 2030 and beyond
2040-2050 fleet growth based on AEO sales trend rather than inventory trend
| Exhibit 1 Load Blocks | Load block schedules per 1 million vehicles calculated using heavy charging at peak and light charging at peak. Values multiplied by number of PHEVs (minus BAU amounts) and added to demand and peak demands.
| Table 2 Demands | Next sheet
| Table 3 Peak Demands | Next sheet after
Appendix A, Exhibit 21: Key MRN Parameters
Original BAU Values
|  |  | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| New vehicle stock (millions) | Plug-in 10/40 Gasoline Hybrid | 0 | 0.17 | 0.49 | 1.14 | 2.23 | 3.56 | 5.65 | 9 | 14.32
|  | 100/200 Mile Electric Vehicle | 0.02 | 0.13 | 0.32 | 0.64 | 1.08 | 1.51 | 2.12 | 2.99 | 4.2
| Total VMT for Light-Duty Vehicles (billions of miles) |  | 2733.552 | 2947.1597 | 3199.0596 | 3465.4707 | 3753.7415 | 4043.7061 | 4356.0695 | 4692.562 | 5055.0475
| Alternative Fuel VMT (billions of miles) | Plug-in 10/40 Gasoline Hybrid | 0 | 1.9531 | 5.935 | 14.3818 | 28.6389 | 46.2024 | 74.5372 | 120.2491 | 193.9949
|  | 100/200 Mile Electric Vehicle | 0.2882 | 1.4878 | 3.7443 | 7.776 | 13.2829 | 18.9172 | 26.9413 | 38.369 | 54.6441
|  | Fraction of VMT that are electric | 0.01054% | 0.1168% | 0.3026% | 0.6394% | 1.117% | 1.61% | 2.33% | 3.38% | 4.919%
|  | Millions of PEVs | 0.02 | 0.3 | 0.81 | 1.78 | 3.31 | 5.07 | 7.77 | 11.99 | 18.52
|  |  | Growth Factor | 3 | 6 | 9 | 10 | 10 | 10 | 10 | 10
| High PHEV Values | Only used in Senstivity so not used in MRN
|  |  | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| New vehicle stock (millions) | Electric and Plug-in Electric Vehicles | 0.02 | 0.9 | 4.86 | 16.02 | 33.1 | 50.7 | 69.937 | 89.4 | 112.717
Based on 2030-2035 sales growth rate instead of 2030-2035 inventory growth rate
Exhibit 1 Load Block modifications
Load Blocks for 1 million vehicles (MW)
|  |  | 2010: Summer (May-Sep) |  | Shoulder (Mar-Apr, Oct-Nov) |  |  |  |  | Winter (Dec-Feb)
Hours |  |  | 10 | 25 | 75 | 100 | 200 | 300 | 400 | 500 | 800 | 1262 | 25 | 200 | 600 | 900 | 1203 | 25 | 100 | 400 | 700 | 935
|  |  | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20
| Time Zone | Highest in top 10 hours | [20 empty] | GWh
Peaking | Eastern | 1083.875 | 216.73 | 576.32 | 358.92 | 381.36 | 425.18 | 276.48 | 266.86 | 270.82 | 331.22 | 588.01 | 811.13 | 684.2 | 299.96 | 133.89 | 604.21 | 615.15 | 555.92 | 445.74 | 145.48 | 551.88 | 3550
Peaking | Central | 1083.875 | 0 | 350.63 | 256 | 271.43 | 354.35 | 352.97 | 238.98 | 262.67 | 296.65 | 636.66 | 751.58 | 821.24 | 283.97 | 109.46 | 608.27 | 802.95 | 617.77 | 459.17 | 118.48 | 553.88 | 3550

## F6S7 Table2_Demand
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation
Sensitivity | F6S7-High PHEV | Modified load block shapes in recognition of increased PHEV levels 37% charging during peak hrs
Table 2 - Energy Demand
NEEM Region | AEO Region for 2020+ Growth Rate | 2011 Energy (GWh) | 2011-2020 Growth Rate Before High PHEV | 2020-2050 Growth Rate Before High PHEV | 2011-2020 Growth Rate After High PHEV | 2020-2050 Growth Rate After High PHEV
AZ_NM_SNV_Coal | AZNM | 124203 | 1.88% | 1.31% | 0.0194 | 0.0153
ENT | SRDA | 159507 | 1.37% | 0.53% | 0.014 | 0.0069
ERCOT | ERCT | 316195 | 1.69% | 0.65% | 0.0172 | 0.0081
FRCC | FRCC | 229020 | 1.73% | 1.24% | 0.0178 | 0.0145
MAPP_US | MROW | 29828 | 0.87% | 0.78% | 0.0089 | 0.0083
MISO_IN | RFCW | 97101 | 1.05% | 0.61% | 0.0108 | 0.008
MISO_MI | RFCM | 94678 | 0.8% | 0.79% | 0.0085 | 0.0104
MISO_MO-IL | SRGW | 96157 | 0.87% | 0.82% | 0.0091 | 0.0102
MISO_W | MROW | 137739 | 0.85% | 0.78% | 0.0089 | 0.0094
MISO_WUMS | MROE | 66425 | 1.1% | 0.66% | 0.0114 | 0.0088
NE | MROW | 29481 | 1.81% | 0.78% | 0.0184 | 0.009
NEISO | NEWE | 129768 | 0.02% | 0% | 0.0006 | 0.0037
NonRTO_Midwest | SRCE | 58092 | 1.66% | 0.49% | 0.0169 | 0.0064
NP15 | CAMX | 110014 | 0.94% | 1% | 0.0102 | 0.0144
NWPP_Coal | NWPP | 246983 | 1.3% | 0.94% | 0.0133 | 0.0108
NYISO_A-F (note A) | NYUP | 63281 | 0.2% | 0.51% | 0.0025 | 0.0084
NYISO_G-I (note A) | NYCW | 19524 | 0.14% | 0.85% | 0.002 | 0.0115
NYISO_J-K (note A) | NYLI | 73315 | 0.39% | 0.88% | 0.0044 | 0.0117
PJM_E | RFCE | 135784 | -0.98% | 0.67% | -0.0094 | 0.0088
PJM_ROM | RFCE | 144050 | 0.86% | 0.67% | 0.0092 | 0.0104
PJM_ROR | RFCW | 520031 | 0.4% | 0.61% | 0.0043 | 0.0079
RMPA | RMPA | 72067 | 1.21% | 1.27% | 0.0125 | 0.0147
SOCO | SRSE | 249461 | 1.94% | 0.81% | 0.0196 | 0.0096
SP15 | CAMX | 179898 | 1.31% | 1% | 0.0136 | 0.0127
SPP_N | SPNO | 75955 | 1.22% | 0.91% | 0.0124 | 0.0101
SPP_S | SPSO | 163927 | 1.15% | 0.64% | 0.0116 | 0.0072
TVA | SRCE | 173627 | 0.97% | 0.49% | 0.0098 | 0.0059
VACAR | SRVC | 236109 | 1.62% | 0.96% | 0.0165 | 0.0112
ALB | NA | 64239 | 1.57% | 1.41% | 0.0157 | 0.0141
BC | NA | 63168 | 1.15% | 0.96% | 0.0115 | 0.0096
IESO | NA | 142313 | -0.29% | 0.67% | -0.0024 | 0.0098
MAPP_CA | NA | 48058 | 2% | 0.78% | 0.0201 | 0.0083
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.

## F6S7 Table3_Peak
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation
Sensitivity | F6S7-High PHEV | Modified load block shapes in recognition of increased PHEV levels 37% charging during peak hrs
Table 3 - Peak Demand
NEEM Region | Reserve Margin Region | AEO Region for 2020+ Growth Rate | 2011 Peak (MW) | 2011-2020 Growth Rate | 2020-2050 Growth Rate | 2011-2020 Growth Rate after High PHEV | 2020-2050 Growth Rate after High PHEV
AZ_NM_SNV_Coal | AZ_NM_SNV | AZNM | 27169 | 1.91% | 1.31% | 0.0199 | 0.0161
ENT | ENT | SRDA | 29623 | 1.28% | 0.53% | 0.0132 | 0.0078
ERCOT | ERCOT | ERCT | 64964 | 1.69% | 0.65% | 0.0173 | 0.0089
FRCC | FRCC | FRCC | 46580 | 1.65% | 1.24% | 0.0171 | 0.0156
MAPP_US | MAPP_US | MROW | 5512 | 0.89% | 0.78% | 0.0091 | 0.0087
MISO_IN | MISO | RFCW | 17792 | 1.11% | 0.61% | 0.0116 | 0.0091
MISO_MI | MISO | RFCM | 19930 | 0.79% | 0.79% | 0.0086 | 0.0115
MISO_MO-IL | MISO | SRGW | 18713 | 0.92% | 0.82% | 0.0099 | 0.0113
MISO_W | MISO | MROW | 25929 | 0.93% | 0.78% | 0.0098 | 0.0103
MISO_WUMS | MISO | MROE | 12790 | 1.1% | 0.66% | 0.0116 | 0.0101
NE | SPP | MROW | 5580 | 1.52% | 0.78% | 0.0157 | 0.0097
NEISO | NEISO | NEWE | 27165 | 0.49% | 0.12% | 0.0055 | 0.0061
NonRTO_Midwest | NonRTO_Midwest | SRCE | 10858 | 1.56% | 0.49% | 0.016 | 0.0074
NP15 | CA | CAMX | 24248 | 1.24% | 1% | 0.0135 | 0.0158
NWPP_Coal | NWPP | NWPP | 41760 | 1.01% | 0.94% | 0.0106 | 0.012
NYISO_A-F (Note A) | NYISO | NYUP | 11269 | 0.1% | 0.51% | 0.0019 | 0.0106
NYISO_G-I (Note A) | NYISO | NYCW | 4280 | -0.09% | 0.85% | -0.0001 | 0.0127
NYISO_J-K (Note A) | NYISO | NYLI | 16622 | 0.1% | 0.88% | 0.0017 | 0.0128
PJM_E | PJM | RFCE | 31190 | -0.92% | 0.67% | -0.0088 | 0.0095
PJM_ROM | PJM | RFCE | 25797 | 0.71% | 0.67% | 0.0082 | 0.0128
PJM_ROR | PJM | RFCW | 95148 | 0.42% | 0.61% | 0.0048 | 0.0091
RMPA | RMPA | RMPA | 12556 | 1.34% | 1.27% | 0.0141 | 0.0161
SOCO | SOCO | SRSE | 48104 | 2.18% | 0.81% | 0.0222 | 0.0104
SP15 | CA | CAMX | 35048 | 1.31% | 1% | 0.0139 | 0.0141
SPP_N | SPP | SPNO | 15530 | 2.03% | 0.91% | 0.0206 | 0.0105
SPP_S | SPP | SPSO | 32752 | 1.06% | 0.64% | 0.0108 | 0.0077
TVA | TVA | SRCE | 33073 | 1.62% | 0.49% | 0.0164 | 0.0065
VACAR | VACAR | SRVC | 46538 | 1.53% | 0.96% | 0.0157 | 0.012
ALB | ALB | NA | 9176 | 1.63% | 1.41% | 0.0163 | 0.0141
BC | BC | NA | 11441 | 1.16% | 0.96% | 0.0116 | 0.0096
IESO | IESO | NA | 23625 | -0.29% | 0.68% | -0.0019 | 0.0123
MAPP_CA | MAPP_CA | NA | 8007 | 1.69% | 0.78% | 0.0171 | 0.0088
The input assumptions contained herein reflect a joint assumptions development process between EIPC, EIPC stakeholders and CRA for purposes of EIPC capacity expansion modeling.
As such, these inputs do not necessarily reflect the opinions or views of CRA or any individual EIPC stakeholder.
Note A. NYISO demands are bassed on EE reductions that are half of the state targets. The growth rates for the BAU must be lowered to reflect the additional EE. Preliminary values are shown here. Below are the PA values.
NYISO_A-F | NYISO | NYUP | 11504 | 0.74%
NYISO_G-I | NYISO | NYCW | 4366 | 0.67%
NYISO_J-K | NYISO | NYLI | 17095 | 0.71%

## F6S9-Offshore Wind
| Title | Short Description
Future | F6-Regional RPS | Future 6: National RPS -- State/regional Implementation
Sensitivity | F6S2-High Load Growth | High load growth
Worksheets Affected
Table 2
Table 3
NEEM Region | 2015 | 2020 | 2025 | 2030
VACAR | 0 | 421 | 632 | 947
NYISO_J-K | 0 | 947 | 1421 | 2132
NEISO | 0 | 1158 | 1737 | 2605
PJM_E | 0 | 1184 | 1776 | 2664
PJM_ROR | 0 | 395 | 592 | 888
PJM_ROR (Great Lakes) | 0 | 0 | 0 | 250
MISO_MI (Great Lakes) | 0 | 0 | 0 | 250

## F6S10_Hard TransLimits Ex_17
| Title | Short Description
Future | Regional RPS | Future 6: National RPS - State/regional Implementation
Sensitivity | F6S10-Hardened Transmission Limits | Re-run of base case with hardened transmission limits
Worksheets Affected | Exhibit 17- Transfer Limits | Below
TO BE UPDATED WHEN LIMITS ARE SELECTED FROM F2S1 AND F2S2 RUNS