## Sheet1
| EIPC RESPONSE TO STAKEHOLD Roll-up WORKING GROUP |  | 2010-10-07
Queston # | Asker | Question | Comments
1 | Peter Huang | On page 8, B1: it states SMLFWG is responsible to “create/modify steady-state loadflow models”. What is the process for the comments from this SSC Roll-Up WG and the Scenario WG to be taken into consideration for the development of loadflow models? | The procedure is for the SMLFWG to provide public information describing the model and analysis results through posting and open webex presentations. Stakeholder comments can be provided during comment periods of webex persentations or via email to the SMLFWG chair person. The SMLFWG will review this input and either incorporate appropriate model modifications or explain their preference for not changing the model.
2 | Peter Huang | On Page 11, Section C, there is no mention of how to model future planned generation resource. Do the cases only model existing and approved generation? | This is covered under the Resorce assumption to be included in the Report.
3 | Peter Huang | On page 19, second bullet on the page states “transfer source will be available generation, including off-line, honouring machine limits”. If certain units are modeled as off-line, is there concern it is a de-commissioned unit? Is there a preference to max out the on-line unit first? | The PAs were asked to provide sub files for the transfer. So, retired generators were not inadvertantly included.
4 | Peter Huang | On page 19 and 20, the two tables indicate linear transfer analysis will be performed for transfers between areas (labelled as A, B, C…). will analysis be performed to investigate transfer within a area? If yes, which ones are planned? | As mentioned in the Note below Table 2 in the Manual, control area-level transfers and PA-level transfers may be studied (in addition to the transfers shown in Table 2), if requested by PAs.
5 | Fred Plett | Page 5, last paragraph, 1st sentence – “The EIPC…plans developed each year…” Should this be clarified; 2020, 2030 or 2010-2020? | Because this manual is intended to be used for subsequent EIPC modeling efforts as well. This Manual is intended to be a general procedure manual for this and all future EIPC loadflow model activities.
6 | Fred Plett | Please define all abbreviations and acronyms the first time they are used, or create a glossary (e.g. ERAG MMWG). | Will consider a glossary to be added to the manual
7 | Fred Plett | Page 8, Case Development, 3rd bullet - Please define long-term. | Yearly transactions - Long-term is >=1 year from transmission service perspective
8 | Fred Plett | Page 8, Case Development, 3rd bullet - Are roll-over rights the same as grandfathered rights? | No. Grandfathered rights generally refer to transmission rights that were granted prior to Order 888. Roll-over rights are transmission rights that give the transmission user the option continuing a service beyond the granted service period. Roll-over rights are typically more restrictive than grandfathered rights.
9 | Fred Plett | Page 8, Case Development, last bullet - “Base case generation dispatch … are set to the internal assumption…” There should be some consistency among the dispatch models. PAs should use detailed transmission production cost model with sequential load accounting for minimum down and run times, operating reserves, etc. These models do not have to be the same vendor. The fuel forecast for all PAs should be from a consistent source. The differences of the internal assumptions should be documented and reported. | We agree the questioneer's description is important in market efficiency modeling that accounts for all hours and loads in a year. A peak load single snapshot power flow 10 years in the future generally requires all available generation to be dispatched.
10 | Fred Plett | Page 10, Section III.A, item 7 – Will you please clarify “per series”? | Series refers to a set of MMWG powerflow cases used
11 | Fred Plett | Page 10, Section III.A, items 11 thru 14 – The delineation of the seasons seems illogical. Please justify why the seasons have been divided in such a manner. We recommend that the seasons be adjusted for spring (3/1/xxxx-5/31/xxxx), summer (6/1/xxxx-8/30/xxxx), fall (9/1/xxxx-11/30/xxxx), and winter (12/1/xxxx-2/28/xxxx). This seasonal delineation correlates to the highest three months for cooling degree days and heating degrees day for summer and winter, respectively. The following link contains data to support this recommendation. http://www.ncdc.noaa.gov/oa/documentlibrary/hcs/hcs.html | This delination is not based directly on temperature, but rather refers to general industry practice on what constitutes spring, summer, fall and winter seasons. This is used more as a guide. These are consistent with the MMWG series defintions.
12 | Fred Plett | Page 11, Section III.C, bottom of page – what is current, confirmed transmission service? Please clarify “(B) All future native …..” | There may be LSEs in a PA's control area who have not defined their network resources in future years. Such LSEs will have their loads accounted for (served) in the loadflow models using the PA's procedure to address resource assumptions
13 | Fred Plett | Page 12, Section III.C, (E) – Methods used for generation dispatch and transfer for each PA should be reported. | Addressed in the Report under resource and modeling assimptions
14 | Fred Plett | Page 12, Section III.D, What is “specific status” modeling? | Each PA determines the individual status (in or out of service) of the transmission faciltities considered in the model based on their planning process.
15 | Fred Plett | Page 12, Section III.D, How is an “affected party” identified? | All parties involved in the transmission interconnection - the participating PA's
16 | Fred Plett | Page 12, Section III.E, Light load – What is early morning? Should this be more clearly defined? | It is generally the min load period as determined by each PA. It is not expected to be a coincident low load period across the entire interconnection.
17 | Fred Plett | Page 17, Section III.J, Item 1 – “The EIPC Area Coordinators will review the models and provide corrections…” These corrections should be documented and reported. | Corrections to the models are documented during the model development
18 | Fred Plett | Page 18, Section IV.B. Item 2 – Why was 5000 MW selected as the limit? | The intent is not to transfer 5000 MW per se, but to establish the base transfer capabilities between the various transfer regions. 5000 MW was considered as a large enough transfer such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified.
19 | Fred Plett | For each Planning Authority, please identify: a) Annual energy consumption forecast by year (through 2015 or 2020 as available) b) Annual peak load forecast by year (again, for whatever years are provided) c) Annual percentage growth estimates for (1) energy and (2) peak load through 2015 | a) The energy forecasts are related to the economic model. b) and c) The peak MW forecasts and the growth rates as provided by each PA are included in the roll-up report but based on the year 2020.
20 | Fred Plett | For each Planning Authority, please identify: a) Estimates of energy consumption reductions by year from energy efficiency programs b) Estimates of peak load reductions by year from demand side programs (energy efficiency, demand response, load management) | The annual energy metric is not relevant to snapshot power flows. Information for specific PA's may become a higher priority for idenfitication during the scenario modeling phases of the project. This information is generally avaialble from individual PA's.
21 | Fred Plett | Rollup to 2020, please identify: a) Assumptions used by EIPC for each Planning Authority region in order to “roll up” the Planning Authority forecasts and make estimates regarding future energy consumption, peak loads, and the anticipated impacts of demand side programs on the forecasts. b) Actions taken by EIPC to reconcile, resolve, or smooth out regional forecast variances. | The roll-up process is documented in the roll-up report. A) Each individual PA has provided the estimated load forecast, generation dispatch and topology for the study model. These have been incorporated into the roll-up model. Load forecasting involves complex methods and assumptions and available detailed information should be pursued with individual PA's. B) The forecast provided are PA specific. Load forecasts are generally very sensitive to local economic conditions and load characteristics and so uniform assumptions are not generally desirable.
22 | Ken Lotterhos | Page 10, Master Tie-line Database: Will stakeholder WGs (particularly the RollupWG) have the opportunity to review and comment on the Master Tie-line database and the line modeling assumptions? There have been inadvertent modeling errors in the past on several Merchant Transmission Lines in the Northeast in inter-regional studies that could significantly alter the outcome of planning studies. | A listing of the tie-line information will be made available.
23 | Ken Lotterhos | Page 10, Master Tie-line Database: Will stakeholders be provided a list of tie-lines that were not agreed upon for modeling? | A listing of the tie-line information will be made available.
24 | Ken Lotterhos | Page 10, Master Tie-line Database: Please share the rationale behind the selected in-service and out-of-service assumptions in items 11 through 14 on pages Page 10-11. Has consideration been given to assessing the effect of a major line coming in/out in late July or early August when evaluating peak summer condition issues? | This is general industry practice on what constitutes spring, summer, fall and winter in-service dates. The seasonal terms used in points 11 through 14 refer to general utility construction schedules. The construction schedules for some of these transmission facilities that are included in the models are not defined well enough for the PAs to estimate the month in which the facility will be in-service.The PAs feel that the confidence level in the construction schedules of these future transmission facilities allows for only a seasonal in-service date.
25 | Ken Lotterhos | Page 11, Interchange Schedule Matrices: On Item 7 – Which of the four seasonal models does Light Load correspond to? It states a date of April first but the Spring model has a start date of April 15th. | This is general industry practice on what constitutes spring, summer, fall and winter in-service dates. The seasonal terms used in points 11 through 14 refer to general utility construction schedules. The construction schedules for some of these transmission facilities that are included in the models are not defined well enough for the PAs to estimate the month in which the facility will be in-service.The PAs feel that the confidence level in the construction schedules of these future transmission facilities allows for only a seasonal in-service date.
26 | Ken Lotterhos | Page 11, Interchange Schedule Matrices: Why are the interchange schedule window dates one day off from the Tie-line modeling window dates? | No discrepancy in the day was found in the manual
27 | Ken Lotterhos | Resources (Page 11): The procedure manual states that “All existing, confirmed native load generation and announced retirements of existing native load generation will be modeled.” What is meant by “confirmed native load generation”? Does this include planned resource additions per OATT procedures as stated in item “(c)”? | Generation to meet load obligations that have gone through the respective PA's transmission service process and has been confirmed.
28 | Ken Lotterhos | Model Definitions (Page 12): The Procedural Manual defines Summer Peak Load “as the summer peak demand expected to be served, reflecting load reductions for peak shaving. Topological modeling changes shall be incorporated into the model if they are to go into effect on or before July 15th. Summer interchange schedules should reflect transactions expected to be in place on July 15th.” How does this take into consideration the differing modeling practices of the various RTO/ISO, for example: For PJM, the summer months are June – September for planning purposes (see Manual M-35 – page 73). For NYISO, the “Summer Capability period is from May 1 to October 31 (Footnote 3 on page 11 of the 2010 Gold book). | In the roll-up process, each PA has provided what they expect their summer peak load to be. While, we understand the complexities due to the non-coincident nature of the summer peak load demands in differing geographic regions, this roll-up process is generally the same process that is followed by the MMWG in building their summer peak models. It is important for a roll up of existing regional plans to represent the system on which the regional plans were developed according to the respective tarrif and planning protocols.
29 | Ken Lotterhos | Preparation and Transmittal of Power Flow Models (Page 14): While the objective stated in item 5 is a good goal to ensure a robust base case “These must be solvable in not more than 20 iterations from a flat start with a mismatch tolerance of 1 MW or 1 MVAR per bus and a zero impedance cutoff setting of 0.0001 p.u.” It is sometimes difficult to get models to solve with the stated tolerances for certain N-1 conditions. Would EIPC consider exceptions to this rule for specific instances where the case solves but may require more iterations or a looser solution tolerance or would a failure to solve within the stated limits be deemed a divergent case? | The solution paramenters quoted refer to base case (no contingency) conditions. For AC contingency analysis involving these models, adjustments (such as increasing the iteration limit) may have to be made. Failure to solve within the stated limits (with the excpetion of the mismatch tolerance) will not cause a case to be deemed divergent.
30 | Ken Lotterhos | Transfer Specific Subsystem Description File Examples (Page 22): If the intent is to include off line source generators in the transfers as stated on page 18 “Transfer sources will be available generation, including off-line, honoring machine limits,” the PSS/MUST sub-system files may need to specifically include the “include offline” statement if indicating Areas instead of particular busses for shift participation. For example, SUBSYSTEM 'MY COMPANY', AREA 145, AREA 205, AREA 209, AREA 215, SCALE ALL FOR EXPORT INCLUDE OFFLINE, END When a transfer limit is found using linear DC analysis, will a confirming AC loadflow analysis be performed at that transfer level for the specific limiting contingency identified? | Agree with comment about the off-line statement in the sub file. The purpose of the linear transfer analysis is to establish high-level base transfer capabilities between the various transfer regions. The test transfer was intentionally chosen to be large enough such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified. An AC verfication is not intended.
31 | Terron Hill | Section III.D (pg 12) : If a proposed transmission facility is already in an individual PAs model, does it count as an approved facility? We need further clarification on the guidelines for defining and clarification of what is a proposed and an approved transmission facility. | No, could be proposed or conceptual. More information is provided in the roll-up report.
32 | Terron Hill | Section III.E (pg 12) : Which year are these dates referring to? For example does the Summer Peak Load refer to before July 15, 2020? | The year being refered to is the year for which the roll-up model has been developed - 2020. The summer designation is based on on each PA's individual interpretation as to what constitutes the summer season.
33 | Terron Hill | Pg 14: Why limit this to 20 iterations for convergence? | It is a generally accepted industry practice for base case models
34 | Terron Hill | Section III.J (pg 17): Where are we with Finalizing Power Flow models? | We are complete to the point where transfer analysis has been performed. In the event errors are found the model will be corrected.
35 | Terron Hill | Section IV.B (pg 18): why is a 5000MW transfer value assumed? What is the purpose of fixing transfers to 5000MW? | The intent is not to transfer 5000 MW per se, but to establish the base transfer capabilities between the various transfer regions. 5000 MW was considered as a large enough transfer such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified.
36 | Denis Bergeron | Implications of flow based vs. contract path based AC analysis in linear transfer analysis, p.8 a) Is it intended by this that the model will allow a production cost dispatch of the entire system to dictate how power moves across the system using the path of least resistance to get from source to sink? b) Does this approach misrepresent regions in which the system is dispatched to preserve the ability to flow power along the contract path? Does this approach misrepresent regions in which the system is dispatched to preserve the ability to flow power along the contract path? c) If so, could the model overestimate Eastern Interconnect dispatch efficiency, for example due to ignoring seams between markets and ignoring seams between market and non-market areas? | The basic purpose of the transfer analysis is to provide a very rough guide to the physical system capability to transfer power within reliability limits. These are only rough guides that provide a relative benchmark of system capability and are only indicative in nature. They provide useful guides with which to test the effects of varying system configurations or conditions. a) The intent is not to transfer 5000 MW per se, but to establish the base transfer capabilities between the various transfer regions. 5000 MW was considered as a large enough transfer such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified. Establishing these base transfer capabilitites will aid in the development of the economic transfer scenarios. Establishing these base transfer capabilities helps in forming an expectation of the existing transfer capability between two transfer regions and the investment that will be involved in increasing this transfer capbility. The subsystem files (which define the generators or control areas that are to participate in these linear transfers) were provided by the PAs and, therefore, reflect their preferred method of studying the linear transfers b) Since the transfer subsystem files were provided by each individual PA, such contract path obligations were taken into account while developing the subsystem files. c) Please see answer to part a) regarding the purpose of the linear transfers. Seams issues such as inefficiencies between markets or between market and non-market areas will have to be addressed in the economic model
37 | Denis Bergeron | Page 9 lists “Each PA coordinates their respective, approved expansion plans with neighboring PAs for possible, mutual benefit ‘enhancements’ based on the EIPC analysis of the approved plans… (this may include one 3-5 day in person meeting). This will result in the EIPC base plan consistent with currently approved plans.” EISPC requests notification of the date, time and invitees to these meetings. | This possible meeting has not yet occurred since the need for an in person meeting has not yet been determined
38 | Denis Bergeron | Linear Transfer Analysis p.9. “The intent of this analysis is not to identify constraints such that the transmission projects can be identified and transfer capability increased.” This sentence is confusing. Is the analysis intended to examine existing system capability assuming larger markets or coordinated EI dispatch? | The intent is not to transfer 5000 MW per se, but to establish the base transfer capabilities between the various transfer regions. 5000 MW was considered as a large enough transfer such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified. The analysis does not assume larger markets
39 | Denis Bergeron | Compile analysis into reports p. 9 bullet 2 a) The bullet specifies this is not applicable to the roll up, so I think it refers to facilities that may be identified through scenario analysis. B) According to the Association for the Advancement of Cost Engineering, a “Planning Estimate” is possible when a project is between 40% and 70% defined, and it is within plus or minus 25% accuracy. Shouldn’t we make sure this is what EIPC means? If not, let’s at least make sure they all use the same plus or minus accuracy parameters for the values expressed – do you all agree? c) Is the NPV going to be the cost of the transmission infrastructure anticipated by itself, or is it going to include any economies created by more efficient system dispatch? d) What is the appropriate discount rate to use in the analysis? A societal discount rate? The ROE required of the Transmission owner in question? Or something else? Ideas? | a) Yes b) A definition of planning estimate may be included in the glossary of the Manual c) Transmission cost. Production cost benefits will not be known until the economic models are runs. d) Carrying cost and associated financial parameters will be provided by each PA responsible for the improvement.
40 | Denis Bergeron | Tie line database p. 10: The EIPC coordinator is to maintain a master list of all inter area tie lines. EISPC Roll up working group requests this list be made available for our review as soon as possible. | A listing of the tie-line information will be made available but not the actual database that may include proprietary coding.
41 | Denis Bergeron | Interchange Schedule Matrices p. 11: Item 1 says only “Firm full path schedules” will be modeled. This seems counter to what was mentioned in item 1 above i.e. “flow based v. contract path.” Please explain | The two issues are unrelated. The quoted passages from page 11 refer to modeling assumption. The quotes passage from page 8 refer to the linear transfer analysis methodology.
42 | Denis Bergeron | Topology p.12: “each PA may include proposed transmission facilities that …” a) Why is this elective? If there are facilities that have been proposed and agreed upon, should ALL be included, or should ALL not be included – will elective nomination of this sort could create difficulties interpreting results? b) Is there a difference in certainty of facility construction among the different PA ten year plans? For example, the RTO tariff in New England requires member TOs to pursue the construction of facilities that are included in the plan if the facilities are located within their service territories. c) Is there a difference in certainty of facility construction among the different PA ten year plans? For example, the RTO tariff in New England requires member TOs to pursue the construction of facilities that are included in the plan if the facilities are located within their service territories. d) What if regulators who may have citing authority in communities through which such facilities will pass believe they will not receive permits? | Not all facilities in the roll up are of the same level of certainty by the vary nature of the relationship between facilities with varying in-service dates throughout the 10 year projection. Based on their best judgements, the PAs have provided their best estimate of which facilities are to be included in the model basd on their expectations and degree of confidence. Permitting issues don't enter into the process until later stages of system development.
43 | Denis Bergeron | Model Definition p.12: The manual states that Demand side management should be modeled in accordance with the standards/modeling practices of each PA. a) Does the EIPC believe such variability could create confusion when comparing between areas in future modeling efforts? b) Would adoption of a standard protocol for 20 year scenarios avoid confusion? | a) The PAs have provided their best estimate of which facilities are to be included in the model basd on their expectations and degree of confidence. b) A standard protocol may be in conflict with the working practices of some of the PAs and would be inconsistent with the basis for the roll up system. Instead, the PAs will provide their best estimate of load levels and transmission facility assumptions to be included in the model based on their expectations and degree of confidence.
44 | Denis Bergeron | Loads pp.12 & 13: a) It was our impression that the load flow studies would be conducted for a particular year. Is this correct? If so, why does this section not state which year is the study year? | Because this manual is intended to be used for subsequent EIPC modeling efforts as well. This Manual is intended to be a general procedure manual for this and all future EIPC loadflow model activities.
45 | Denis Bergeron | Power Flow Model Merging p.15: a) “TVA Brown’s Ferry is the “swing machine” for each EIPC model” Please explain the term “swing machine” and also the significance to Brown’s Ferry? b) What is meant by “tie line discrepancies,” and should EISPC have some say in toss ups about these? c) Please explain provision #4 “non-convergent models.” . weren’t PAs supposed to submit their 10 year plans that (presumably) solve? Does “convergent” mean the same as “solving” here? | a) Swing machine is a loadflow term used to designate a generating unit in a loadflow model that is used to balance out any imbalances in generation, load and interchange levels in the loadflow case. It is a mathematical requirement. The unit at Brown's Ferry has been the industry standard swing machine for the MMWG cases for decads. b) This is a model checking procedure to correct inadvertant errors and is not subject to discretion . The final list of tie-lines can be provided to the EISPC. c) Yes, that’s true. Convergent means solving the loadflow case to the specified tolerance level.
46 | Denis Bergeron | Linear transfer analysis p.18: A 5,000 MW injection is a large source that can require expensive provisions to guard againstr loss of source problems. Do the operating and security analyses contemplate including LOS analyses and remedies in the final work and in the Net Present Value estimates of any final configurations? | The 5000 MW injection doesn't refer to a single source injection but only refers to a dispatch adjustment of modeled units. The intent is not to transfer 5000 MW per se, but to establish the base transfer capabilities between the various transfer regions. 5000 MW was considered as a large enough transfer such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified.
47 | Denis Bergeron | Transfer amounts allocated amongst the sink on a load ratio share. a) how could this be arranged without actually transferring power from point to point? b) Would using this assumption mask any loss of source problems inquired about above? c) Are transfers going to be based on production costing models? If so see concerns expressed above regarding contract path vs economic dispatch. d) Sources – it will be important to states that have entered into the Regional Greenhouse Gas Initiative to know which particular units will be ramped up in any power flow analysis and whether the ramp up indicates a greater output of carbon emissions when the transfers are permitted. e) Why are nuclear units not allowed to back down? In some regions with resources that have zero fuel cost available at low load times, would these resources not be selected while nuclear units (which do have fuel costs) be dispatched? | a) and b) The purpose of the linear transfer analysis in page 18 is to establish high-level base transfer capabilities between the various transfer regions. The test transfer amount was chosen such that most flowgates limiting transfer capability (between the transfer regions defined in table 1 on page 19) would be expected to be identified. Establishing these base transfer capabilitites will aid in the development of the economic transfer scenarios. Establishing these base transfer capabilities helps in forming an expectation of the existing transfer capability between two transfer regions and the investment that will be involved in increasing this transfer capbility c) The final transfers evaluated will be a result of the three scenarios selected by the SSC and a transmission overlay will be developed to accomododate those specific transfers. d) The PAs provided the sub files for the transfer. So,such consideration will be taken into account in developing the transfer subsystem files e) It is extremely unlikely that nuclear and other base load units will be allowed to run back to allow intermittent energy sources to be dispatched. Each PA has provided their best estimate of generation dispatch to be included in the model based on their expectations and degree of confidence
48 | Denis Bergeron | Table 1 page 19: a) What is the logic used for giving PJM and SPP their own columns in this table? b) In column “C” why are NY and New England grouped with two Canadian provincial utilities? c) Why has Hydro-Quebec been left out of this table? d) Is it intended that the 5,000 MW injection discussed above will be split load ratio share between these regions? (e.g. PJM absorbs 5,000, but it is split among the 3 areas in column A. e) Do the PAs in each of these groups then need to assess whether their region can absorb such an influx w/o other modifications? | a) PJM is a single control area and transfers to and from PJM indeed are correctly modeled with PJM as a single region. The transfers to and from the control areas in SPP are correctly modeled by treating them as a single region. Others and combinations of various PAs represent larger geographical regions. b) basically they represent large geographical regions. c) Hydro Quebec is a separate asynchronous Interconnection only linked to the US by DC ties. Its transfer capability is the ratings of its ties and interregional agreements for their operatons. d) There is no subsystem A to Subsystem D (PJM) transfer contemplated in the linear transfer analysis. Subsystem files determning distribution of sources and sinks are determined by each PA. e) The PAs provide sub files for the transfer. So,such consideration will be taken into account in developing the transfer subsystem files
49 | Denis Bergeron | NITC, FCTIC and FCTTC p. 28 Please explain what is meant by the term, “First Contingency Incremental Transfer Capability (FCITC). | The incremental power, limited by the worst case single contingency, that can be transferred (above and beyond base transfer capabilitiy) across an interface or to a region
50 | Denis Bergeron | Table p. 29 Please provide a simple illustrative, numeric example of the LODF table showing how the sign conventions work would clarify this section. | See attached tab for example
51 | Denis Bergeron | “interface” and “flowgate” p. 32. Are these terms interchangeable or do they mean something that is separate and distinct?. | No, they are not interchangeable. An interface is defined as a collection of transmission elements, usually connecting different areas. A flowgate, on the other hand, is a mathematical construct, comprised of one or more monitored transmission elements and optionally one or more contingency elements, used to analyze the impact of power flows upon the system.
52 | NGOs | For each planning authority load forecast projection, please explain how each applicable state’s policies on demand side resources and renewable energy policy are reflected in the forecasts provided. | Each PA has provided their load forecast for their roll-up model. These forecasts include any demand-side and renewable resources that the PAs may have decided to include.
53 | NGOs | For each planning authority forecast, please explain if, and how, the effect of the current economic recession has been (in the April 2010 values provided) or will be accounted for in the forecast. If not, please explain why the current trends have not been considered. | Each PA has provided their load forecast for their roll-up model. These load growth forecasts incorporate the effect of macro-economic activity in the PAs service footprint.
54 | NGOs | For each Planning Authority, please identify: a. Annual energy consumption forecast by year (through 2015 or 2020 as available) b. Annual peak load forecast by year (again, for whatever years are provided) c. Annual percentage growth estimates for (1) energy and (2) peak load through 2015 | Peak MW forecasts are in the Report. Energy forecasts have to be addressed by the economic working group.
55 | NGOs | For each Planning Authority, please identify: d. Estimates of energy consumption reductions by year from energy efficiency programs e. Estimates of peak load reductions by year from demand side programs (energy efficiency, demand response, load management) | Information for all PA's has not been compiled as of today. Will consider the request.
56 | NGOs | Rollup to 2020, please identify: f. Assumptions used by EIPC for each Planning Authority region in order to “roll up” the Planning Authority forecasts and make estimates regarding future energy consumption, peak loads, and the anticipated impacts of demand side programs on the forecasts. g. Actions taken by EIPC to reconcile, resolve, or smooth out regional forecast variances. | The forecast provided are PA specific. No consideration has been given to attempt to develop a "uniform" forecast.
57 | NGOs | For each planning authority, please provide a year-by-year schedule out to 2020 of any supply resource addition and any supply resource retirement or mothballing to be considered as part of the rolled-up plan. Please include actual unit-specific information for any retirement/mothball, and include the size, type, location, fuel source, anticipated cost, and rationale for any expected addition. Please provide this information in spreadsheet format files. | Expected generation additons are listed in the roll-up reported. Information associated with retirements are commercially sensitive.
58 | NGOs | Have the regional aggregate load forecasts provided by PJM, MISO, and SPP among others been adjusted to account for coincidence or are they the sum of the non-coincident LSE load forecasts? | The load forecast are non-coincident among the regions mentioned, however, diversity may be applied internal to the regions, depending on regional practice. See the the individual PA references for details on load forecast.
59 | NGOs | Has any thought been given to creating either regional coincident load forecasts or an interconnection wide coincident load forecasts? | The load forecast are non-coincident, consistent with the planning basis and protocol for the roll up plans assembled.
60 | NGOs | Will the treatment of DSM as either an adjustment to load or a resource be standardized across the interconnection? | Effect of DSM has been incorporated in the load forecast as described by each PA in the roll-up report. This is consistent with the planning basis and protocol for the roll up plans assembled.
61 | NGOs | How will firm transmission capacity reserved through Transmission Service Requests but not currently associated with firm capacity obligations be addressed in the power flow models or in the analysis? | Only long term firm transmission service is incorporated in the model.
62 | NGOs | Will RPS requirements be modeled concurrently or will coincidence and diversity be included? | Each PA has taken into account RPS requirements as reflected in their respective resource plans.
63 | NGOs | How will the natural diversity of un-dispatchable variable resources be included in the power flow modeling? | It is taken into account in the generation dispatch provided by each respective PA in the roll-up or scneario models.
64 | NGOs | Will transmission requirements be moderated to address variable energy requirements vs. traditional capacity? a. Will fixed transfer capability to deliver 100% of the capacity 100% of the time be the target? b. If RPS are driven by energy requirements will any adjustment be made to the transmission capability deliver enough of the power enough of the time to meet the RPS? | Will be determined based on the final scenarios selected by the SSC
65 | NGOs | How will merchant or other potentially speculative transmission upgrades be selected for inclusion in the 2020 model? In the +20 year model? | Each PA has provided their expected transmission expansion plans based on their planning process. Any such potential upgrades are included in the roll-up model as determined by the PAs. 20+ expansions will determined based on the needs identified in the economic scenario portion of the study.
66 | NGOs | Will there be any consideration given to local transmission upgrades driven by generation retirements, derating, or repowering which may be required to enable the importation of renewable or other resources from remote sources? | Will be dependent on the outcome of the economic scenario analyis.
67 | NGOs | Please have each PA list what, if any, changes were made to the modeling assumptions used in developing the EIPC roll-up model compared to those used in the ERAG MMWG model building effort. | General assumptions for the EIPC are listed in the report
68 | NGOs | Please identify the differences between the plans being stitched together in the roll-up and the ERAG/MMWG plan, including significant changes in the assumptions, load forecasts, use of DSM, DR or EE, generation additions and retirements (100 MW or more), large transmission additions (200 kV or more), etc. | General assumptions for the EIPC are listed in the report
69 | NGOs | Several PA indicated that demand side adjustments were “in” their load forecasts but they did not indicate the magnitude. For each PA, please indicate how much demand side adjustments are “in” their forecast, what types of demand side adjustments are included in their forecast, for what transmission modeling tests that forecast is used, whether a different forecast is used for other modeling runs or NERC tests (and if so describe the differences). | Information for all PA's has not been compiled as of today. Will consider the request.
70 | NGOs | Please have each PA indicate the total amount of new generation modeled in their footprint and provide a list of all unit additions or upgrades greater than or equal to 100 MW. | In report
71 | NGOs | Please have each PA indicate any new external capacity purchases greater than 100 MW modeled to meet future capacity adequacy requirements. | Each PA's generation assumption and scheduled transfers are accounted for and listed in the report
72 | NGOs | Please have each PA indicate the total amount of generation within their footprint which has been assumed to have been retired, mothballed, or derated and provide a list of all reductions greater than or equal to 100 MW. | This information is considered to be market sensitive
73 | NGOs | Please have each PA provide a list of all transmission additions greater than 200 kV modeled in their footprint and the facilities status; proposed, planned, or under construction, their current in service date, and the need driver; reliability, generation interconnection, transmission service request, merchant, or economics. | In roll-up report
74 | NGOs | Please provide a list of any transmission additions greater than or equal to 200 kV which traverse multiple PA and can be considered regional transmission upgrades. Please include the in service date, all PA associated with the upgrade, and the need driver associated with the upgrade. | In roll-up report
75 | NGOs | Please identify the differences between the plans being stitched together in the roll-up and the base cases that the PAs are currently using for planning, including any significant changes in the assumptions, load forecasts, load forecast areas, use of DSM, DR or EE, generation additions and retirements (100 MW or more), large transmission additions (200 kV or more), etc. | General assumptions for the EIPC are listed in the report
76 | NGOs | Please identify the base case years currently being used by each of the PAs for transmission planning, i.e. which PAs use 5 year base cases, 10 year, or other lengths. | In narrative provided by each PA

## eg for Q 50
FCITC | N | FCITC | L: Limiting constraint | Shift | MW | TDF |  | PTDF = | BaseCaseFlow =
|  |  | C: Contingency description | Flow | Rating |  | LODF |  | Init | Final
2400 | 97 | 2442 | L: 333 PETER 161 337 MIKE 161 1 | -315.4 | -461 | 0.05963 |  | 0.02535 | -129.4 | -191.3
|  |  | C:331 JACK 500 515 SMITH 500 1 19 | 35
|  |  | Open 331 JACK 500 515 SMITH 500 1 |  |  |  | 0.24196 | 0.14168 | 768.5 | 1114.5
In the above example, the polatity (or sign) of the TDF is positive and that of the LODF is positive. This implies that the direction of contingency and limiting branches assumed in the transfer report above is accurate and does not have to be changed. In other words, for this transfer, at transfer level of 2442 MW, the direction of power flow for this constraint to be binding is from bus PETER to bus MIKE in the limiting element and from bus JACK to bus SMITH in the contingency element. The LODF and the TDF will be reported in the roll-up report unchaged, as shown above.
FCITC | N | FCITC | L: Limiting constraint | Shift | MW | TDF |  | PTDF = | BaseCaseFlow =
|  |  | C: Contingency description | Flow | Rating |  | LODF |  | Init | Final
2650 | 97 | 2650 | L: 333 PETER 161 337 MIKE 161 1 | -315.4 | -461 | 0.021923 |  | 0.02535 | -129.4 | -191.3
|  |  | C:331 JACK 500 515 SMITH 500 1 19 | 35
|  |  | Open 331 JACK 500 515 SMITH 500 1 |  |  |  | -0.02419 | 0.14168 | 768.5 | 1114.5
In the above example, the polatity (or sign) of the TDF is positive and that of the LODF is negative. This implies that the direction of the contingency branch assumed in the transfer report above has to be changed. In other words, for this transfer, at transfer level of 2650 MW, the direction of power flow for this constraint to be binding is from bus PETER to bus MIKE in the limiting element, but is from bus SMITH to bus JACK in the contingency element, rather than as shown in the report above. So, in the roll-up report, the contingency element will be reported as "C:515 SMITH 500 331 JACK 500 1" and the LODF will then be displayed as "0.02419", rather than as shown above
FCITC | N | FCITC | L: Limiting constraint | Shift | MW | TDF |  | PTDF = | BaseCaseFlow =
|  |  | C: Contingency description | Flow | Rating |  | LODF |  | Init | Final
2400 | 97 | 2442 | L: 333 PETER 161 337 MIKE 161 1 | -315.4 | -461 | -0.021923 |  | -0.02535 | -129.4 | -191.3
|  |  | C:331 JACK 500 515 SMITH 500 1 19 | 35
|  |  | Open 331 JACK 500 515 SMITH 500 1 |  |  |  | 0.02419 | 0.14168 | 768.5 | 1114.5
In the above example, the polatity (or sign) of the TDF is negative and that of the LODF is positive. This implies that the directions of the limiting branch and the contingency branch assumed in the transfer report above have to be both changed. In other words, for this transfer, at transfer level of 2442 MW, the direction of power flow for this constraint to be binding is from bus MIKE to bus PETER in the limiting element and is from bus SMITH to bus JACK in the contingency element, rather than as shown in the report above. So, in the roll-up report, the limiting element will be reported as "L:337 MIKE 161 333 PETER 161 1" and the contingency element will be reported as "C:515 SMITH 500 331 JACK 500 1" . The TDF will be then displayed as "0.05963", rather than as shown above
FCITC | N | FCITC | L: Limiting constraint | Shift | MW | TDF |  | PTDF = | BaseCaseFlow =
|  |  | C: Contingency description | Flow | Rating |  | LODF |  | Init | Final
2400 | 97 | 2442 | L: 333 PETER 161 337 MIKE 161 1 | -315.4 | -461 | -0.028777 |  | -0.02535 | -129.4 | -191.3
|  |  | C:331 JACK 500 515 SMITH 500 1 19 | 35
|  |  | Open 331 JACK 500 515 SMITH 500 1 |  |  |  | -0.02419 | 0.14168 | 768.5 | 1114.5
In the above example, the polatity (or sign) of the TDF is negative and that of the LODF is negative. This implies that the direction of the limiting branch assumed in the transfer report above has to be changed. In other words, for this transfer, at transfer level of 2442 MW, the direction of power flow for this constraint to be binding is from bus MIKE to bus PETER in the limiting element and is from bus JACK to bus SMITH in the contingency element, rather than as shown in the report above. So, in the roll-up report, the limiting element will be reported as "L:337 MIKE 161 333 PETER 161 1". The LODF will then be displayed as "0.02419" and the TDF will be displayed as "0.05963", rather than as shown above