## Transfers from A
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem A (FRCC)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
A to E | 1738.7 | DEF | 403528 MARTIN WEST 230 407120 SLV_SP_N 230 1 | 385 | -0.08308 | DEF | 403522 CRYST RVR PL 230 403526 KINGROAD PEF 230 1 3883 | Y* | Operating Guide increased the limit from 950 to 1600 MW
| 1828.8 | DEF | 403159 ARCHER 230 403171 HAILE TAP 230 1 | 319 | 0.09526 | DEF | 403522 CRYST RVR PL 230 403526 KINGROAD PEF 230 1 3883
| 2144.5 | DEF | 403171 HAILE TAP 230 403174 GINNIE 230 1 | 319 | 0.09526 | DEF | 403522 CRYST RVR PL 230 403526 KINGROAD PEF 230 1 3883
| 2467.8 | SCEG | 371308 6SRS2 230 371380 3SRS2 115 2 | 336 | 0.03735 | SCEG | 370308 6SRS1 230 371308 6SRS2 230 Z1 2402
| 2741.6 | DEF | 403159 ARCHER 230 403528 MARTIN WEST 230 1 | 438 | -0.0857 | DEF | 403522 CRYST RVR PL 230 403526 KINGROAD PEF 230 1 3883
| 2864.9 | SOCO | 380009 8W MCINTOSH 500 381424 6W MCINTOSH2 230 1 | 1350 | 0.13501 | SOCO | 380009 8W MCINTOSH 500 381421 6W MCINTOSH1 230 1 2501
| 2871.4 | SOCO | 380009 8W MCINTOSH 500 381421 6W MCINTOSH1 230 1 | 1344 | 0.13433 | SOCO | 380009 8W MCINTOSH 500 381424 6W MCINTOSH2 230 1 2502

## Transfers from B
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem B (MISO)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
B to C | 702.6 | PENELEC | 200674 26TOWANDA 115 200675 26E.TWANDA 230 4 | 226 | -0.04489 | NYISO/PENELEC | R:C398/NWES | R | B-->C: 1800 Base Transfer
| 2125.2 | FE | 238915 02LRN Q2 138 239728 02BLKRVR 138 1 | 270 | -0.03082 | FE | 238551 02AVON 345 238850 02JUNIPE 345 1 | R
| 2297.6 | PENELEC | 200674 26TOWANDA 115 200676 26E.SAYRE 115 1 | 191 | 0.11321 | NYISO/PENELEC | SB:HILL_B312 | Y
| 2302.7 | NYISO/PENELEC | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 128 | -0.11321 | NYISO/PENELEC | SB:HILL_B312 | Y
| 2760.8 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.07262 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2820.5 | NYISO | 131018 LOUNS115 115 131850 CNYOG115 115 1 | 131 | 0.07262 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2849.1 | NYISO | 130848 S.OWE115 115 131850 CNYOG115 115 1 | 131 | -0.07262 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2900.6 | AP | 235152 01BUTLER 138 235197 01KARNSC 138 1 | 179 | 0.03047 | PENELEC/AP | 200769 26HOMER CY 345 235129 01ARMSTRONG 345 1F | R
| 2907.4 | NYISO | 126294 PLTVLLEY 345 137451 LEEDS 3 345 2 | 1538 | -0.10135 | NYISO | 126294 PLTVLLEY 345 137455 ATHENS 345 1 | Y
| 2988.9 | PENELEC | 200678 26LENOX 115 200936 26WILLMS 115 1F | 162 | 0.08544 | NYISO/PENELEC | R:C398/NWES | R
| 3038.1 | NYISO | 126294 PLTVLLEY 345 137455 ATHENS 345 1 | 1538 | -0.09999 | NYISO | 126294 PLTVLLEY 345 137451 LEEDS 3 345 2 | Y
| 3071.9 | NYISO/PENELEC | 135277 FALCONER 115 200579 26WARREN 115 1 | 118 | -0.09316 | NYISO/PENELEC | 135398 SW345 345 200942 FARM_V_345 345 1 | Y
| 3104.6 | PENELEC | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 189 | 0.08933 | NYISO/PENELEC | R:C398/NWES
| 3170.4 | PENELEC | 200679 26TIFFANY 115 200936 26WILLMS 115 1F | 162 | -0.08544 | NYISO/PENELEC | R:C398/NWES
| 3263.3 | NYISO/PENELEC | 130807 WESTOVER115 115 200680 26LAUREL L 115 1 | 150 | -0.08933 | NYISO/PENELEC | R:C398/NWES
| 3323.3 | PENELEC | 200679 26TIFFANY 115 200680 26LAUREL L 115 1 | 160 | 0.08933 | NYISO/PENELEC | R:C398/NWES
| 3339.4 | NYISO | 130836 N.WAV115 115 131162 CHEMU115 115 1 | 176 | 0.06013 | NYISO/PENELEC | SB:HILL_B312
| 3363.8 | NYISO/PENELEC | 130763 HILSD230 230 200675 26E.TWANDA 230 1 | 531 | -0.24903 | NYISO/PENELEC | 130757 WATRC345 345 200930 26MAINESBURG 345 1
| 3375.9 | NYISO | 130814 HILSD115 115 131162 CHEMU115 115 1 | 176 | -0.06013 | NYISO/PENELEC | SB:HILL_B312
B to D | NO LIMIT
B to E | NO LIMIT
B to F | 693 | EES | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | 446 | -0.06532 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 726.2 | EES-SWPA | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 396 | 0.06532 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 895.4 | EES | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 446 | -0.0426 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 1703.6 | EES | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 521 | -0.0426 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 4184.1 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 1299 | 0.1128 | N/A | No Contingency
| 2877.4 | SWPA | 504440 BUFORD 5 161 505448 NORFORK5 161 1 | 175 | -0.03291 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 3527.7 | SWPA | 504440 BUFORD 5 161 505460 BULL SH5 161 1 | 189 | 0.03291 | EES-OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1

## Transfers from C
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem C (NPCC)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
C to B | 574 | METED/PL | 204515 27YORKANA 230 207922 BRIS 230 1 | 624 | -0.03376 | PJM | 200004 CNASTONE 500 200013 PEACHBTM 500 1 | R | C-->B: 1800 Base Transfer
| 1136.1 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 717 | -0.19241 | NYISO | T:61&64 | Y
| 1251.7 | NYISO | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | -0.05114 | NYISO | T:77&78 | Y
| 1378.6 | NYISO | 126272 E13ST 45 345 126645 FARRAGUT EAS 345 1 | 922 | -0.06066 | NYISO | 126273 E13ST 46 345 126644 FARRAGUT WES 345 1 | Y
| 1410.2 | NYISO | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 275 | -0.03826 | NYISO | T:61&191 | Y
| 1414.7 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 717 | -0.24145 | NYISO | T:62&BP76 | Y
| 1475.7 | NYISO | 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | -0.04874 | NYISO | T:77&78 | Y
| 1566.9 | NYISO | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | 0.04961 | NYISO | T:77&78 | Y
| 1584.2 | NYISO | 135449 GR.I-182 115 135538 LONG-182 115 1 | 208 | -0.04961 | NYISO | T:77&78 | Y
| 1671.2 | NYISO | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | 654 | -0.17786 | NYISO | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | Y
| 1683.4 | NYISO | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | -0.20234 | NYISO | 135303 SAWYER77 230 135415 PACKARD2 230 1 | Y
| 1689.6 | NYISO | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | -0.20202 | NYISO | 135304 SAWYER78 230 135415 PACKARD2 230 2 | Y
| 1769.9 | NYISO | 135450 GRDNVL1 115 135475 S139-141 115 1 | 101 | 0.03073 | NYISO | SB:DUNK230_R1312 | Y
| 1780.6 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 841 | -0.19241 | NYISO | T:61&64
C to D | -381.6 | NYISO | 126272 E13ST 45 345 126645 FARRAGUT EAS 345 1 | 922 | -0.06077 | NYISO | 126273 E13ST 46 345 126644 FARRAGUT WES 345 1 | Y | C-->D: 2000 Base Transfer
| 567 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 717 | -0.18905 | NYISO | T:61&64 | Y
| 611.2 | NYISO | 126273 E13ST 46 345 126644 FARRAGUT WES 345 1 | 982 | -0.06072 | NYISO | 126272 E13ST 45 345 126645 FARRAGUT EAS 345 1 | Y
| 664.3 | NYISO | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | -0.05032 | NYISO | T:77&78 | Y
| 714.2 | NYISO | 126561 8E DUM 138 126643 RAINEY EAST 345 8 | 305 | 0.04513 | NYISO | SB:RAIN345_9W | Y
| 762 | NYISO | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 275 | -0.03741 | NYISO | T:61&191 | Y
| 894.7 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 717 | -0.23756 | NYISO | T:62&BP76 | Y
| 899.1 | NYISO | 136150 CLAY 345 136156 VOLNEY 345 1 | 1344 | -0.05811 | NYISO | SB:OSWE_R985 | Y
| 924.1 | NYISO | 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | -0.04784 | NYISO | T:77&78 | Y
| 971.8 | NYISO | 126561 8E DUM 138 126643 RAINEY EAST 345 8 | 252 | 0.03592 | N/A | No Contingency | Y
| 1012.1 | NYISO | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | 0.04871 | NYISO | T:77&78 | Y
| 1035.5 | NYISO | 135449 GR.I-182 115 135538 LONG-182 115 1 | 208 | -0.04871 | NYISO | T:77&78 | Y
| 1188.6 | NYISO | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | -0.19884 | NYISO | 135303 SAWYER77 230 135415 PACKARD2 230 1 | Y
| 1189.8 | NYISO | 135450 GRDNVL1 115 135475 S139-141 115 1 | 101 | 0.03004 | NYISO | SB:DUNK230_R1312 | Y
| 1195 | NYISO | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | -0.19852 | NYISO | 135304 SAWYER78 230 135415 PACKARD2 230 2 | Y
| 1196.4 | NYISO | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | 654 | -0.17467 | NYISO | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | Y
| 1222.9 | NYISO | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 841 | -0.18905 | NYISO | T:61&64

## Transfers from D
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem D (PJM)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
D to B | 2.1 | CE-ALTW | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | 1153 | 0.03725 | CE-MEC | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | Y
| 1018.3 | PJM | 200004 CNASTONE 500 200013 PEACHBTM 500 1 | 2815 | -0.09462 | PJM | 200004 CNASTONE 500 200026 HUNTERTN 500 1 | R
| 1188.8 | CE/ALTW | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | 999 | 0.03066 | N/A | No Contingency | Y
| 1668.7 | ALTW | 631140 SALEM 3 345 631141 ROCK CK3 345 1 | 890 | -0.03037 | CE/ALTW | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1
| 2610.5 | PJM | 200004 CNASTONE 500 200013 PEACHBTM 500 1 | 2338 | -0.10609 | N/A | No Contingency | R
| 3994.3 | CE | 270730 ELECT JCT; B 345 270846 PLANO ; B 345 1 | 1341 | -0.03606 | CE | 270733 ELECT JCT;3R 345 270847 PLANO ; R 345 1 | INVALID
| 3999.1 | CE | 270781 ITASCA ; R 345 270813 LOMBARD ; R 345 1 | 1341 | -0.03124 | CE | 270713 DES PL 46; R 345 270813 LOMBARD ; R 345 1
D to C | 803.5 | PENELEC | 200674 26TOWANDA 115 200675 26E.TWANDA 230 4 | 226 | -0.04975 | NYISO/PENELEC | R:C398/NWES | Y | D-->C: 3000 Base Transfer
| 1823.3 | PENELEC | 200674 26TOWANDA 115 200676 26E.SAYRE 115 1 | 191 | 0.1183 | NYISO/PENELEC | SB:HILL_B312 | Y
| 1866.2 | NYISO/PENELEC | 135277 FALCONER 115 200579 26WARREN 115 1 | 118 | -0.0916 | NYISO/PENELEC | 135398 SW345 345 200942 FARM_V_345 345 1 | Y
| 1873.4 | NYISO/PENELEC | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 128 | -0.1183 | NYISO/PENELEC | SB:HILL_B312 | Y
| 2249.4 | NYISO/PENELEC | 135277 FALCONER 115 200579 26WARREN 115 1 | 80 | -0.05499 | N/A | No Contingency | Y
| 2372.8 | NYISO | 130836 N.WAV115 115 131162 CHEMU115 115 1 | 176 | 0.06295 | NYISO/PENELEC | SB:HILL_B312 | Y
| 2409.5 | NYISO | 130814 HILSD115 115 131162 CHEMU115 115 1 | 176 | -0.06295 | NYISO/PENELEC | SB:HILL_B312 | Y
| 2682.6 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.07457 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2688.7 | PENELEC | 200674 26TOWANDA 115 200676 26E.SAYRE 115 1 | 158 | 0.06949 | N/A | No Contingency | R
| 2755.1 | NYISO | 131018 LOUNS115 115 131850 CNYOG115 115 1 | 131 | 0.07457 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2785.8 | NYISO | 130848 S.OWE115 115 131850 CNYOG115 115 1 | 131 | -0.07457 | NYISO | SB:Oakd345_36-3122_no-sps | Y
| 2786.6 | PENELEC | 200678 26LENOX 115 200936 26WILLMS 115 1F | 162 | 0.09024 | NYISO/PENELEC | R:C398/NWES | R
| 2822.8 | NYISO/PENELEC | 130763 HILSD230 230 200675 26E.TWANDA 230 1 | 531 | -0.25829 | NYISO/PENELEC | 130757 WATRC345 345 200930 26MAINESBURG 345 1 | Y
| 2862.6 | PENELEC | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 189 | 0.09435 | NYISO/PENELEC | R:C398/NWES | R
| 2893 | PENELEC | 200769 26HOMER CY 345 200942 FARM_V_345 345 1F | 605 | 0.14785 | N/A | No Contingency
| 2901.9 | PENELEC | 200820 26ERIE SE 115 200927 26FOURMILE 115 1F | 228 | 0.11276 | PENELEC | 200819 26ERIE SE 230 200928 26FOURMILE 230 1F
D to E | 957.3 | PJM | 200004 CNASTONE 500 200013 PEACHBTM 500 1 | 2815 | -0.10065 | PJM | 200004 CNASTONE 500 200026 HUNTERTN 500 1 | R
NO ADDITIONAL LIMIT

## Transfers from E
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem E (SERC)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
E to A | 612 | FPL | 400398 HUDSONFL 230 407119 SEMINOLE 230 1 | 637 | -0.05497 | FPL | 400462 RICE 230 401099 RICEBYPASS 230 1 | Y
| 1485 | FPL | 400468 PUTNAM 230 401099 RICEBYPASS 230 1 | 588 | -0.07449 | FPL | 400398 HUDSONFL 230 407119 SEMINOLE 230 1 | Y
| 1638.7 | FPL | 400398 HUDSONFL 230 400468 PUTNAM 230 1 | 637 | 0.05497 | FPL | 400462 RICE 230 401099 RICEBYPASS 230 1 | Y
| 1817.8 | PEF | 403085 FT WHITE B 69.0 403162 FT WHITE N 230 1 | 112 | -0.03198 | PEF | 403162 FT WHITE N 230 403163 FT WHITE S 230 1 | Y
| 1944 | SBA/FRCC | Voltage Security Limit | N/A | N/A | N/A | No Contingency
| 2289.3 | SOCO-FPL | 380015 8THALMANN 500 400356 DUVAL 500 1 | 2598 | 0.66055 | SOCO-FPL | 380014 8HATCH 500 400356 DUVAL 500 1
| 2429.4 | SOCO | 382148 3HOMELAND 115 382149 3STGEORGE 115 1 | 124 | 0.03169 | SOCO-FPL | 380015 8THALMANN 500 400356 DUVAL 500 1
E to B | 5790.1 | AMIL/EEI | 347325 7JOPPA TS 345 351003 5JOPPA TS 161 1 | 600 | -0.03327 | TVA | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
E to D | 4840.9 | DVP | 314902 8CARSON 500 314936 8RAWLINGS 500 1 | 2598 | -0.12857 | DVP | 314902 8CARSON 500 314935 8BRUNSWICK 500 1
E to F | 521.8 | SWPA-SPP | 505508 DARDANE5 161 505514 CLARKSV5 161 1 | 223 | 0.03516 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 574.1 | EES-MISO | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | 446 | -0.07885 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 601.6 | EES-MISO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 396 | 0.07885 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 749 | EES-MISO | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 446 | -0.05093 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
| 1425 | EES-MISO | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 521 | -0.05093 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1

## Transfers from F
Appendix H: Summary of Incremental Transfer Capabilities
Transfers from Subsystem F (SPP)
Transfer | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
F to B | 836.3 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 896 | -0.04154 | WERE | 532766 JEC N 7 345 532767 GEARY 7 345 1
| 3457.5 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1 | 956 | -0.05662 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1
| 4191.6 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1 | 1073 | -0.05119 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1
| 4715.4 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 896 | -0.04337 | N/A | No Contingency
F to E | 949.9 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 896 | -0.03657 | WERE | 532766 JEC N 7 345 532767 GEARY 7 345 1

## Summary
|  |  |  | Previous |  | New
Source |  | Sink |  | FCITC (MW) | Lim. PA | FCITC (MW) | Lim. PA | Delta
A | FRCC | E | SERC | 1600 | DEF | 1700 | DEF | 100
B | MISO | C | NPCC | 3400 | PENELEC-PJM | 3100 | PENELEC | -300
B | MISO | D | PJM | >5000 | N/A | >5000 | N/A | 0
B | MISO | E | SERC | >5000 | N/A | >5000 | N/A | 0
B | MISO | F | SPP | 650 | EES | 650 | EES | 0
C | NPCC | B | MISO | 1800 | NYISO | 1750 | NYISO | -50
C | NPCC | D | PJM | 1500 | NYISO | 1200 | NYISO | -300
D | PJM | B | MISO | 1600 | ALTW-MISO | 1650 | ALTW | 50
D | PJM | C | NPCC | 2100 | PENELEC-PJM | 2850 | PENELEC | 750
D | PJM | E | SERC | >5000 | N/A | >5000 | N/A | 0
E | SERC | A | FRCC | 1900 | SBA/FRCC | 1900 | SBA/FRCC | 0
E | SERC | B | MISO | >5000 | N/A | >5000 | N/A | 0 | Last years MUST files had an error in the SUB file, causing an erroneous error to show up.
E | SERC | D | PJM | 1900 | BREC-MISO | 4800 | DVP | 2900 | During the update of the roll-up cases, MISO submitted a correction to transmission facilities between BREC and TVA. A previous upgrade modeled in the original roll-up cases had incorrect bus numbers causing isolated facilities to be tied together and show overloads in the case. Subsequent transmission fixes were submitted to address the overloads in the original roll-up cases. During the update, the correction included backing out the transmission fixes and correcting the bus numbers to the original update. The erroneous, lower transfer limit is not present with the correct modeling
E | SERC | F | SPP | 550 | SWPA-SPP | 500 | SWPA-SPP | -50
F | SPP | B | MISO | 850 | WERE-SPP | 800 | WERE | -50
F | SPP | E | SERC | 950 | WERE-SPP | 950 | WERE | 0