## S1
Addition to base SSI model
Region | Load Block | Pass | Name | Mileage | Bus# | Bus# | Ckt ID | Reason/Need | If added for a loading or voltage Issue, what was the driver
EIPC | B1/B13 | 1 | Sooner (SPP-S) - Jackson Ferry (PJM Rest of RTO) | 899 | 514804 | 242514 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
EIPC | B1/B13 | 1 | Iatan (SPP-N) - Hanging Rock (PJM Rest of RTO) | 657 | 543003 | 242924 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
EIPC | B1/B13 | 1 | Minnesota I (MISO W) - Marysville (PJM Rest of RTO) | 667 | 700527 | 242928 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
EIPC | B1/B13 | 1 | Iowa G (MISO W) - Sullivan (PJM Rest of RTO) | 546 | 700541 | 243210 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
EIPC | B1/B13 | 1 | Lakeville Junction (MISO W) - Greentown (PJM Rest of RTO) | 626 | 700530 | 243207 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
EIPC | B1/B13 | 1 | Brookings County (MISO W) - Collins (PJM Rest of RTO) | 558 | 700529 | 270607 | 1 | Loading >100% of System Emergency | Needed for Large West to East Transfer
ENTERGY | B1/B13 | 3 | New Addis to Tiger 230 kV Ckt 2 | 5.78 | 335536 | 335665 | 2 | Loading >100% of System Emergency | Addis - Cohen 230 kV Ckt 1 overloads FTLO Addis - Tiger 230 kV Ckt 1 Addis - Tiger 230 kV Ckt 1 overloads FTLO Dow meter - Air Liquid Tap 230 kV Ckt 1 Dow Meter - Air Liquid Tap 230 kV Ckt 1 overloads FTLO Addis - Tiger 230 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Chisolm Road to Sabine 230 kV Ckt 2 | 10.36 | 334429 | 334434 | 2 | Loading >100% of System Emergency | Chisolm Road - Sabine 230 kV Ckt 2 overloads FTLO Hartburg - Nelson 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Cleveland to Silver City 138 kV Ckt 2 | 21.82 | 300138 | 300140 | 2 | Loading >100% of System Normal | Base overload on Cleveland - Silver City 138 kV Ckt 1
ENTERGY | B1/B13 | 3 | New W Memphis to Bham Steel 500 kV Ckt 2 | 6 | 338162 | 360075 | 2 | Loading >100% of System Emergency | W Memphis to Bham Steel 500 kV Ckt 1 overloads FTLO W. Memphis - Cordova 765 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Sorrento 138/115 kV auto | NA | 336050 | 336051 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload for the loss of 500 kV line
ENTERGY | B1/B13 | 3 | UpgradeGonzales to Sorrento 138 kV | 4.65 | 335625 | 336050 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload for the loss of 500 kV line
ENTERGY | B1/B13 | 3 | New Sterlington to Eldorado 500 KV Ckt 2 | 50.09 | 337420 | 337561 | 2 | Loading >100% of System Emergency | Sterlington - Eldorado 500 kV Ckt 1 overloads FTLO Mt. Olive - Eldorado 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Standard to Sterlington 500 kV | 64.99 | 337888 | 337420 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | New Standard to Natchez 500 kV | 55.06 | 337888 | 337887 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | New Natchez to McKnight 500 kV | 75.14 | 337887 | 337836 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | New Standard to Richard 500 kV | 110.13 | 337888 | 337367 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | New Standard to NQ Texarkana | 180 | 337888 | 511900 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | Natchez 500/115 kV auto | NA | 336500 | 337887 | 1 | Loading >100% of System Emergency | Needed to relieve the overloads on the 500 kV system and underlying 115 kV system in the Lousiana are during various contingency events
ENTERGY | B1/B13 | 3 | Replace Lewis Creek 500/230 kv auto with 500/138 kV | NA | 334999 | 334069 | 1 | Loading >100% of System Emergency | Needed in association with the Cypress to Lewis Creek 500 kV solution to address transformer loadings at Lewis Creek
ENTERGY | B1/B13 | 3 | New Lewis Creek to West Conroe SS 230 kV | 12 | 334069 | 334088 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1/B13 | 3 | New West Conroe SS to Grimes 230 kV | 38 | 334088 | 334990 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1/B13 | 3 | New 345/230 kV auto at Grimes | NA | 334990 | 334028 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1/B13 | 3 | New 230/138/13/8 kV three winding transformer at Conroe SS | NA | 334088 | 334099 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1/B13 | 3 | New Cypress to Lewis Creek 500 kV | 80 | 334320 | 334999 | 1 | Loading >100% of System Emergency | Lewis Creek 500/230 kV Auto 1, Lewis Creek - Peach Creek 230 kV Ckt 1, Peach Creek - Jacinto 230 kV Ckt 1 overloads FTLO Harburg - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New 500/230 kV Lewis Creek auto | NA | 334999 | 334069 | 1 | Loading >100% of System Emergency | Lewis Creek 500/230 kV Auto 1, Lewis Creek - Peach Creek 230 kV Ckt 1, Peach Creek - Jacinto 230 kV Ckt 1 overloads FTLO Harburg - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New 230/138 kV Lewis Creek second auto | NA | 334069 | 334072 | 2 | Loading >100% of System Emergency | Lewis Creek 500/230 kV Auto 1, Lewis Creek - Peach Creek 230 kV Ckt 1, Peach Creek - Jacinto 230 kV Ckt 1 overloads FTLO Harburg - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Carville to Conway 230 kV | 9 | 335569 | 335580 | 1 | Loading >100% of System Emergency | Address 230 kV overload due to loss of Willow Glen to Conway 230 kV line
ENTERGY | B1/B13 | 3 | New Danville to Winfield 230 kV | 20 | 337348 | 337341 | 1 | Loading >100% of System Emergency | Winnfield - Jeld Wen - Dodson - Danville 115 kV section Base overload
ENTERGY | B1/B13 | 3 | Loop Daniel to McKnight into Bogalusa | NA | 335836 | 336130 | 1 | Loading >100% of System Emergency | Address various 230 kV overloads north of Lake Pontchartrain for loss of Franklin to Bogalusa 500 kV or Bogalusa 500/230 kV autotransformer
ENTERGY | B1/B13 | 3 | Loop Daniel to McKnight into Bogalusa | NA | 336130 | 338700 | 1 | Loading >100% of System Emergency | Address various 230 kV overloads north of Lake Pontchartrain for loss of Franklin to Bogalusa 500 kV or Bogalusa 500/230 kV autotransformer
ENTERGY | B1/B13 | 3 | New 500/230 kV Nelson second auto | NA | 335190 | 335192 | 2 | Loading >100% of System Emergency | Nelson 500/230 kV auto Ckt 1 overloads FTLO Nelson - Richard 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Madrid 345/161 kV third auto | NA | 300046 | 300103 | 3 | Loading >100% of System Emergency | New Madrid 500/161 kV auto Ckt 1 Overloads FTLO New Madrid 500/161 kV auto Ckt 2
ENTERGY | B1/B13 | 3 | Remove Daniel Phase Shifter | NA | 388700 | 388702 | 1 | Loading >100% of System Emergency | Address various 230 kV overloads north of Lake Pontchartrain for loss of Franklin to Bogalusa 500 kV or Bogalusa 500/230 kV autotransformer
ENTERGY | B1/B13 | 3 | New Richard 230/138 kV auto | NA | 335366 | 500765 | 1 | Loading >100% of System Emergency | Address 500-138 kV autotransformer contingency loadings at Richard
ENTERGY | B1/B13 | 3 | New Sportman 345/161 kV third auto | NA | 300740 | 300741 | 3 | Loading >100% of System Emergency | Sportsman 345/161 kV auto Ckt 1 overloads FTLO Sportsman 345/161 kV Ckt 2
ENTERGY | B1/B13 | 3 | Upgrade West Conroe SS to Conroe 138 kV | 2.6 | 334099 | 334104 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload for loss of various 138 kV lines in Conroe area
ENTERGY | B1/B13 | 3 | Upgrade Dumas to Reed 115 kV | 13.4 | 337600 | 337602 | 1 | Loading >100% of System Normal | Base overload on Dumas - Reed 115 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Reed to McGhee 115 kV | 4.55 | 337602 | 337599 | 1 | Loading >100% of System Emergency | Reed - McGhee 115 kV Ckt 1 overloads under several N-1 contingencies
ENTERGY | B1/B13 | 3 | Upgrade Lewis to Patmos 115 kV | 10.38 | 338874 | 338875 | 1 | Loading >100% of System Emergency | Lewis - Patmos 115 kV Ckt 1 overloads FTLO Hartburg - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Patmos to Fulton 115 kV | 14.95 | 338875 | 503912 | 1 | Loading >100% of System Emergency | Patmos - Fulton 115 kV Ckt 1 overloads FTLO Hartburg - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Morilton East to Gleason 161 kV | 3.06 | 337921 | 337927 | 1 | Loading >100% of System Emergency | Morilton - Gleason 161 kV Ckt 1 overloads FTLO Pleasant Hill - Mayflower 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Gleason to Tyler 161 kV | 0.9 | 337927 | 338424 | 1 | Loading >100% of System Emergency | Gleason - Tyler 161 kV Ckt 1 overloads FTLO Pleasant Hill - Mayflower 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Star to Mendenhall 115 kV | 15.12 | 336763 | 336762 | 1 | Loading >100% of System Normal | Base overload
ENTERGY | B1/B13 | 3 | Upgrade Mendenhall to Magee 115 kV | 10.04 | 336762 | 336760 | 1 | Loading >100% of System Normal | Base overload
ENTERGY | B1/B13 | 3 | New Wells 500/230 kV third auto | NA | 335368 | 500950 | 3 | Loading >100% of System Emergency | Address Wells area autotransformer contingency loadings
ENTERGY | B1/B13 | 3 | New Bogalusa 500/230 kV second auto | NA | 336130 | 336131 | 2 | Loading >100% of System Emergency | Associated with loop in of Daniel to McKnight 500 kV line into Bogalusa
ENTERGY | B1/B13 | 3 | New Mt. Olive 500/230 kV auto | NA | 337368 | 337369 | 2 | Loading >100% of System Emergency | Mt. Olive 500/230 kV Auto 1 overloads FTLO Sterlington - Eldorado 500 kV Ckt 1 Mt. Olive 500/230 kV Auto 1 overloads FTLO Hartburg - Mt. Olive 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Adams Creek to Hattiesburg 230 kV | 53.8 | 336131 | 388270 | 1 | Loading >100% of System Emergency | Angie - Adams Creek 230 kV Ckt 1 and Angie - Hattiesburg 230 kV Ckt 1 overloads FTLO French Branch - Slidell 230 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Essex to Stoddard 161 kV | 0.7 | 300075 | 345790 | 1 | Loading >100% of System Emergency | Essex - Stoddard 161 kV Ckt 1 overloads FTLO Kelso - Lutesville 345 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade HS Village to Hollis 115 kV | 15.37 | 337707 | 338743 | 1 | Loading >100% of System Emergency | HS Village - Hollis 115kV Ckt 1 overloads FTLO Magnet Cove - Sheridan 500 kV Ckt 1 or FTLO Sheridan - Hot Springs 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Hollis to Olla 115 kV | 14.61 | 338743 | 337900 | 1 | Loading >100% of System Emergency | HS Hollis - Olla 115kV Ckt 1 overloads FTLO Magnet Cove - Sheridan 500 kV Ckt 1 or FTLO Sheridan - Hot Springs 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade ` Olla to Danville 115 kV | 8.6 | 337900 | 337901 | 1 | Loading >100% of System Emergency | Olla - Danville 115kV Ckt 1 overloads FTLO Magnet Cove - Sheridan 500 kV Ckt 1 or FTLO Sheridan - Hot Springs 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Lewisville to Couch 115 kV | 9.07 | 337502 | 338874 | 1 | Loading >100% of System Emergency | Couch - Lewis 115 kV Ckt 1 overloads FTLO Standard - NW Texarkana 500 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Novelty to Adair 161 kV | 22 | 300106 | 344001 | 1 | Loading >100% of System Emergency | Novelty - Adair 161 kV Ckt 1 overloads FTLO WADAIRTP to PALMYRA 345 kV
ENTERGY | B1/B13 | 3 | Upgrade Viney to Hergett 161 kV Ckt 1 | 4 | 338157 | 505420 | 1 | Loading >100% of System Emergency | Viney - Hergett 161 kV Ckt 1 overloads FTLO Viney - Hergett 161 kV Ckt 2
ENTERGY | B1/B13 | 3 | Upgrade Viney to Hergett 161 kV Ckt 2 | 4 | 338157 | 505420 | 2 | Loading >100% of System Emergency | Viney - Hergett 161 kV Ckt 2 overloads FTLO Viney - Hergett 161 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Fredtn to Wedekn T 161 kV | 31.18 | 300079 | 345976 | 1 | Loading >100% of System Emergency | Fredtn to Wedekn T 161 kV Ckt 1 overloads FTLO Lutesville - St Francois 345 kV Ckt 1
ENTERGY | B1/B13 | 3 | Upgrade Fredtn to Fredtown 161 kV | 14.18 | 300079 | 344586 | 1 | Loading >100% of System Emergency | Fredtn - Fredtown 161 kV Ckt 1 overloads FTLO Lutesville - St Francois 345 kV Ckt 1
ENTERGY | B1/B13 | 3 | New Swartz to Oakridge 230 kV Ckt 1 | 13 | 337390 | 337449 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Tap Oakridge to Carson, add new Dunn 115 kV substation | NA | 337449 | 337452 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Rebuild Dunn to Carson Ckt 1 | 1.11 | 337452 | 337450 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Move Swartz - Oakridge to Swartz - Oakridge2 | NA | 337390 | 3374491 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Construct new Dunn to Oakridge2 | 13.75 | 337454 | 337542 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Reconductor existing Oakridge to Dunn | 13.75 | 337449 | 337452 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Reconductor Sterlington to Oakridge 115 kV | 19.3 | 337415 | 337449 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Reconductor Carson to Delhi 115 kV | 3.36 | 337450 | 337453 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Construct new Sacksonia to Winnsboro | 23 | 337330 | 337451 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 3 | Replace existing Sacksonia - Carson with Dunn - Sacksonia 115 kV | 3.5 | 337452 | 337451 | 1 | Loading >100% of System Emergency | Address various 115 kV contingency overloads in the Monroe/Delhi/Winnsboro as a result of increased flows across North Louisiana
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 1 from ANO to Ft Smith | 95 | 337914 | 515304 | 1 | Loading >100% of System Normal | ANO to Ft. Smith 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 2 from ANO to Ft Smith | 95 | 337914 | 515304 | 2 | Loading >100% of System Normal | ANO to Ft. Smith 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at ANO | NA | 337914 | 337909 | 1 | Loading >100% of System Normal | ANO to Ft. Smith 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at ANO | NA | 337914 | 337909 | 2 | Loading >100% of System Normal | ANO to Ft. Smith 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 1 from ANO to Mabelvale | 90 | 337811 | 337914 | 1 | Loading >100% of System Normal | ANO to Mabelvale 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 2 from ANO to Mabelvale | 90 | 337811 | 337914 | 2 | Loading >100% of System Normal | ANO to Mabelvale 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at Mabelvale | NA | 337811 | 337808 | 1 | Loading >100% of System Normal | ANO to Mabelvale 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at Mabelvale | NA | 337811 | 337808 | 2 | Loading >100% of System Normal | ANO to Mabelvale 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 1 from Mabelvale to KEO | 25 | 337811 | 337959 | 1 | Loading >100% of System Normal | Mabelvale to Wrightsville to KEO 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 2 from Mabelvale to KEO | 25 | 337811 | 337959 | 2 | Loading >100% of System Normal | Mabelvale to Wrightsville to KEO 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at KEO | NA | 337959 | 337957 | 1 | Loading >100% of System Normal | Mabelvale to Wrightsville to KEO 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at KEO | NA | 337959 | 337957 | 2 | Loading >100% of System Normal | Mabelvale to Wrightsville to KEO 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 1 from KEO to Dell | 160 | 337959 | 338190 | 1 | Loading >100% of System Normal | KEO to Holland Bottoms to ISES to Viney to Dell 500 kV overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at Dell | NA | 338190 | 338187 | 1 | Loading >100% of System Normal | KEO to Holland Bottoms to ISES to Viney to Dell 500 kV overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at Dell | NA | 338190 | 338187 | 2 | Loading >100% of System Normal | KEO to Holland Bottoms to ISES to Viney to Dell 500 kV overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit 1 from KEO to West Memphis | 115 | 337959 | 338163 | 1 | Loading >100% of System Normal | KEO to West Memphis 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at West Memphis | NA | 338163 | 338162 | 1 | Loading >100% of System Normal | KEO to West Memphis 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at West Memphis | NA | 338163 | 338162 | 2 | Loading >100% of System Normal | KEO to West Memphis 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit from West Memphis to Cordova | 40 | 338163 | 360020 | 1 | Loading >100% of System Normal | Freeport to Birmingham Steel to Cordova 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 765 kV circuit from Dell to Cordova | 50 | 338190 | 360020 | 1 | Loading >100% of System Normal | Freeport to Birmingham Steel to Cordova 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at Cordova | NA | 360020 | 360025 | 1 | Loading >100% of System Normal | Freeport to Birmingham Steel to Cordova 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at Cordova | NA | 360020 | 360025 | 2 | Loading >100% of System Normal | Freeport to Birmingham Steel to Cordova 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct new 500 kV line from NW Texarkana to Hartburg | 225 | 334325 | 511900 | 1 | Loading >100% of System Normal | Hartburg to Mt.Olive 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 1 at NW Texarkana | NA | 511544 | 511900 | 1 | Loading >100% of System Normal | Hartburg to Mt.Olive 500 kV line overload
ENTERGY | B1/B13 | 2 | Install 765/500 kV Auto 2 at NW Texarkana | NA | 511544 | 511900 | 2 | Loading >100% of System Normal | Hartburg to Mt.Olive 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct new 500 kV line from NW Texarkana to Lewis Creek | 240 | 334999 | 511900 | 1 | Loading >100% of System Normal | Grimes to Crockett 345 kV line overload
ENTERGY | B1/B13 | 2 | Install 500/230 kV Auto at Lewis Creek | NA | 334999 | 334069 | 1 | Loading >100% of System Normal | Grimes to Crockett 345 kV line overload
ENTERGY | B1/B13 | 2 | Construct 500 kV circuit 2 from Baxter Wilson to Ray Braswell | 35.68 | 336830 | 336839 | 2 | Loading >100% of System Emergency | Baxterwilson to Ray Braswell 500 kV line overload
ENTERGY | B1/B13 | 2 | Construct 345 kV line from Neosho to Flint Creek | 80 | 532793 | 506935 | 1 | Loading >100% of System Emergency | Address Neosho to Blackberry 345 kV line overload
ENTERGY | B1/B13 | 2 | Construct 345 kV line from Brookline to Huben | 45 | 549984 | 300042 | 1 | Loading >100% of System Emergency | Morgan to Huben 345 kV line overload FTLO Morgan to Brookline 345 kV
ENTERGY | B1/B13 | 2 | Reconductor Morgan to Blackberry 345kV line | 62 | 300045 | 300739 | 1 | Loading >100% of System Emergency | Morgan to Blackberry 345 kV line overload
ENTERGY | B1/B13 | 2 | Construct 500 kV line from Fort Smith to Sheridan | 150 | 515305 | 337643 | 1 | Loading >100% of System Normal | Mabelvale to Sheridan 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Hartburg to Mt.Olive 500 kV line | NA | 334325 | 337368 | 1 | Loading >100% of System Emergency | Hartburg to Mt.Olive 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Hartburg to Nelson 500 kV line | NA | 334325 | 335192 | 1 | Loading >100% of System Emergency | Hartburg to Nelson 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on ANO to Fort Smith 500 kV line | NA | 337909 | 515305 | 1 | Loading >100% of System Emergency | ANO to Fort Smith 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on ANO to Pleasant Hill 500 kV line | NA | 337909 | 337922 | 1 | Loading >100% of System Emergency | ANO to Pleasant Hill 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Baxter Wilson to Perryville 500kV line | NA | 336830 | 337427 | 1 | Loading >100% of System Emergency | Baxter Wilson to Perryville 500kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Franklin to Ray Braswell 500kV line | NA | 336562 | 336839 | 1 | Loading >100% of System Emergency | Franklin to Ray Braswell 500kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Nelson to Richard 500 kV | NA | 335192 | 335367 | 1 | Loading >100% of System Emergency | Nelson to Richard 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Sterlington to Eldorado 500 kV cricuit 1 | NA | 337420 | 337561 | 1 | Loading >100% of System Emergency | Sterlington to Eldorado 500 kV line overload
ENTERGY | B1/B13 | 2 | Upgrade terminal equipment on Baxter Wilson to Ray Braswell 500 kV circuit 1 | NA | 336830 | 336831 | 1 | Loading >100% of System Emergency | Baxter Wilson to Ray Braswell 500 kV line overload
IESO | B1/B13 | 3 | Lambton - St Clair 230 kV to 345 kV TL | 1.8 | 160059 | 264656 | 2 | Loading >100% of System Normal | Accommodate the NEEM interchange of 3125 MW with MISO MI
IESO | B1/B13 | 3 | Lambton - St Clair 230 kV to 345 kV TL | 2.4 | 160059 | 264656 | 2 | Loading >100% of System Emergency | Accommodate the NEEM interchange of 3125 MW with MISO MI
IESO | B1/B13 | 3 | Lambton 230/230 kV PAR | NA | 160059 | 150004 | 1 | Loading >100% of System Normal | Addition of Lambton - St Clair 230/345 TL - New Tieline
IESO | B1/B13 | 3 | Lambton 230/230 kV PAR | NA | 160069 | 150006 | 1 | Loading >100% of System Emergency | Addition of Lambton - St Clair 230/345 TL - New Tieline
IESO | B1/B13 | 3 | Lambton 230/345 kV XFRM | NA | 150004 | 150007 | 2 | Loading >100% of System Normal | Addition of Lambton - St Clair 230/345 TL - New Tieline
IESO | B1/B13 | 3 | Lambton 230/345 kV XFRM | NA | 150006 | 150009 | 2 | Loading >100% of System Emergency | Addition of Lambton - St Clair 230/345 TL - New Tieline
IESO | B1/B13 | 3 | Fort Frances - International Falls 115 kV TL | 1.7 | 151203 | 608752 | 1 | Loading >100% of System Normal | Accommodate the NEEM interchange of 195 MW with MISO W
IESO | B1/B13 | 3 | Fort Frances - International Falls 115 kV TL | 1.7 | 151203 | 608752 | 2 | Loading >100% of System Emergency | Accommodate the NEEM interchange of 195 MW with MISO W
IESO | B1/B13 | 3 | Fort Frances 115/115 kV PAR | NA | 151203 | 608752 | 1 | Loading >100% of System Normal | Addition of Fort Frances - International Falls 115 kV TL - New Tieline
IESO | B1/B13 | 3 | Fort Frances 115/115 kV PAR | NA | 151203 | 608752 | 2 | Loading >100% of System Emergency | Addition of Fort Frances - International Falls 115 kV TL - New Tieline
IESO | B1/B13 | 3 | Longwood - Lambton 230 kV TL | 43.6 | 160062 | 160059 | 2 | Loading >100% of System Normal | Accommodate the NEEM interchange of 3125 MW with MISO MI
IESO | B1/B13 | 3 | Longwood - Lambton 230 kV TL | 43.6 | 160062 | 160060 | 2 | Loading >100% of System Emergency | Accommodate the NEEM interchange of 3125 MW with MISO MI
MAPP_US | B1/B13 | 0 | BELFELD - CHAR.CK 345kV TL | 43.6 | 652424 | 659183 | 2,3 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | CHAR.CK - ANTELOP 345kV TL | 75 | 659183 | 659101 | 2,3 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | ANTELOP - LELANDO 345kV TL | 30 | 659101 | 659105 | 3 | Interconnect New Generation | New single ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | ANTELOP - MAPPCOR_COLB 345kV TL | 75 | 659101 | 652002 | 1,2 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | MAPPCOR_COLB - BELFELD 345kV TL | 25 | 652002 | 652424 | 1,2 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | BELFELD - MAPPCOR_COLA 345kV TL | 50 | 652424 | 652001 | 1,2 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | MAPPCOR_COLA - ANTELOP 345kV TL | 50 | 652001 | 659101 | 1,2 | Interconnect New Generation | new double ckt line, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | MAPPCOR_COLB -DICKNSN 345/230kV XFMR | NA | 652002 | 652417 | 1 | Interconnect New Generation | new transformer, North Dakota wind collecotor
MAPP_US | B1/B13 | 0 | WATERTOWN - BRDLAND 345kV TL | 75 | 652529 | 659120 | 1,2 | Interconnect New Generation | new double ckt line, South Dakota wind collecotor
MAPP_US | B1/B13 | 0 | MAPPCOR_COLC - WATERTOWN 345kV TL | 60 | 652012 | 652529 | 1,2 | Interconnect New Generation | new double ckt lineSouth Dakota wind collecotor
MAPP_US | B1/B13 | 0 | MAPPCOR_COLC - BRDLAND 345kV TL | 60 | 652012 | 659120 | 1,2 | Interconnect New Generation | new double ckt lineSouth Dakota wind collecotor
MAPP_US | B1/B13 | 2 | WATERTOWN - WHITE 345kV TL | 44.4 | 652529 | 652537 | 3,4 | Loading >100% of System Normal | Base case overload. Solved by replacing the single ckt with a higher rated double ckt
MAPP_US | B1/B13 | 2 | WHITE 345/115kV XFMR | NA | 652537 | 652538 | 1 | Loading >100% of System Normal | add a second transformer with higher rating
MAPP_US | B1/B13 | 2 | LELND 345/230kV XFMR | NA | 659106 | 659105 | 2 | Loading >100% of System Emergency | overloads for the outage of the parallel transformer. double existing transformer
MAPP_CA | B1/B13 | 3 | HENDAY - LIMEST54 | 0.95 | 667001 | 667002 | 6 | Loading >100% of System Emergency | double ckt existing single ckt line
MAPP_CA | B1/B13 | 3 | HENDAY - LIMEST44 | 0.95 | 667001 | 667003 | 5 | Loading >100% of System Emergency | double ckt existing single ckt line
MAPP_CA | B1/B13 | 3 | HENDAY - LIMEST34 | 0.95 | 667001 | 667004 | 4 | Loading >100% of System Emergency | double ckt existing single ckt line
MAPP_CA | B1/B13 | 3 | HENDAY - LIMEST24 | 0.95 | 667001 | 667005 | 3 | Loading >100% of System Emergency | double ckt existing single ckt line
MAPP_CA | B1/B13 | 3 | HENDAY - LIMEST14 | 0.95 | 667001 | 667006 | 2 | Loading >100% of System Emergency | double ckt existing single ckt line
MAPP_CA | B1/B13 | 3 | HENDAY - LONGSPR 230kV TL | 15.65 | 667001 | 667012 | 4,5,6 | Loading >100% of System Emergency | overload caused by deferent outages. Solved by reconductoring
MAPP_CA | B1 | 3 | LONGSPR - RADL43 230kV TL | 12.51 | 667012 | 667013 | 1 | Loading >100% of System Emergency | for any outage of Long Spruce - Radison lines. Solved by reconductoring
MAPP_CA | B1 | 3 | LONGSPR - RADL42 230kV TL | 12.51 | 667012 | 667014 | 1 | Loading >100% of System Emergency | for any outage of Long Spruce - Radison lines. Solved by reconductoring
MAPP_CA | B1 | 3 | LONGSPR - RADL41 230kV TL | 12.51 | 667012 | 667015 | 2 | Loading >100% of System Emergency | for any outage of Long Spruce - Radison lines. Solved by reconductoring
MAPP_CA | B1/B13 | 2 | ASHERN - VERMIL 230kV TL | 80.6 | 667029 | 667062 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | DORSE - PORTSOU 230kV TL | 39.36 | 667035 | 667053 | 3,4 | Loading >100% of System Emergency | overload caused by one of the ckt outage. Solved by reconductoring
MAPP_CA | B1/B13 | 3 | RIEL - RIELMID 230kV TL | 100ft jumper | 667041 | 667042 | 2,3 | Loading >100% of System Emergency | overload caused by outage of Dorsey - Riel 500kV. Solved by adding double ckt (total is 3ckts)
MAPP_CA | B13 | 3 | RIEL - STVITAL 230kV TL | 4.66 | 667041 | 667043 | 3,4 | Loading >100% of System Emergency | for one ckt outage, the other overloads. Solution is reconductoring
MAPP_CA | B1/B13 | 3 | RIEL 500/230kV XFMR | NA | 667501 | 667042 | 2 | Loading >100% of System Emergency | overload caused by outage of Dorsey - Riel. Solved by adding a second transformer
MAPP_CA | B1/B13 | 2 | PORTSOU - CORNWLS 230kV TL | 74.16 | 667053 | 667070 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B13 | 3 | RALL - EBCAMPB 230kV TL | 104.76 | 667059 | 672630 | 2,3 | Loading >100% of System Normal | overloads for outage of William River - Ponton. single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | VERMIL - ROBLIN 230kV TL | 55.1 | 667062 | 667063 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | YORKTON - ROBLIN 230kV TL | 49.7 | 672615 | 667063 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | RESTON - SOURSTP 230kV TL | 48.4 | 667067 | 667069 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | RESTON - AUBURNT 230kV TL | 46.5 | 667067 | 672613 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | CORNWLS - SOURSTP 230kV TL | 19.33 | 667070 | 667069 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 0 | RADSNDC - KEEYASK 138kV TL | 21.7 | 667231 | 667232 | 1,2,3 | Interconnect New Generation
MAPP_CA | B1/B13 | 2 | QE 230/138kV XFMR | NA | 672640 | 672540 | 2 | Loading >100% of System Normal | add a second transformer
MAPP_CA | B1/B13 | 2 | QE 230/138kV XFMR | NA | 672641 | 672540 | 2 | Loading >100% of System Normal | add a second transformer
MAPP_CA | B1/B13 | 2 | BD - AUBURNT 230kV TL | 66 | 672601 | 672613 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 2 | TANTALL - YORKTON 230kV TL | 50 | 672614 | 672615 | 1,2 | Loading >100% of System Normal | new double ckt line added to solve the 138kV line overloads
MAPP_CA | B1/B13 | 2 | EBCAMPB - CODETTE 230kV TL | 55 | 672630 | 672649 | 2 | Loading >100% of System Emergency | overloaded for outaage of E.B. Campbell to Beatty. Solved by double ckting existing single ckt line
MAPP_CA | B1/B13 | 2 | EBCAMPB - BEATTY 230kV TL | 100 | 672630 | 672638 | 2 | Loading >100% of System Emergency | overloaded for outaage of E.B. Campbell to Codette. Solved by double ckting existing single ckt line
MAPP_CA | B1/B13 | 2 | BEATTY - STOON 230kV TL | 88 | 672638 | 672639 | 3,4 | Loading >100% of System Normal | reconductoring
MAPP_CA | B1/B13 | 2 | BEATTY - WOLVERI 230kV TL | 100 | 672638 | 672643 | 1,2 | Loading >100% of System Normal | base case overload Beatty - Humbold and various contingent overloads. Solved by building new double ckt line
MAPP_CA | B1/B13 | 2 | BEATTY - CODETTE 230kV TL | 56 | 672638 | 672649 | 3,4 | Loading >100% of System Emergency | overloaded for outage of one of the two ckts. Solved by reconductoring
MAPP_CA | B1/B13 | 2 | STOON - QE 230kV TL | 25 | 672639 | 672640 | 2 | Loading >100% of System Normal | reconductoring
MAPP_CA | B1/B13 | 2 | STOON - QE 230kV TL | 25 | 672639 | 672641 | 2 | Loading >100% of System Normal | reconductoring
MAPP_CA | B1/B13 | 2 | CODETTE -NIPAWIN 230kV TL | 3 | 672649 | 672650 | 2,3 | Loading >100% of System Normal | single ckt replaced by higher rated double ckt
MAPP_CA | B1/B13 | 0 | CONAWAP-MAPPCOR_HYSO 230kV TL | 33.91 | 667000 | 667424 | 1,2 | Interconnect New Generation | new double ckt line
MAPP_CA | B1/B13 | 0 | RADSNDC6-MAPPCOR_HYS2 138kV TL | 21.7 | 667231 | 667425 | 1,2,3 | Interconnect New Generation | new 3ckt line
MAPP_CA | B1/B13 | 0 | HENDAY-MAPPCOR_HYS3 230kV TL | 0.95 | 667001 | 667426 | 1,2 | Interconnect New Generation | new double ckt line
MAPP_CA | B1/B13 | 3 | ROSEAUN2 - RIEL 500kV TL | 109.5 | 601012 | 667501 | 2 | Loading >100% of System Normal | double ckt existing single ckt line
MAPP_CA | B1/B13 | 0 | CONAWAP4 - RIEL bipole DC line | 850 | 667000 | 667041 | 39,40 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP - HENDAY 230kV TL | 19.04 | 667000 | 667001 | 1,2,3,4 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP -LONGSPR 230kV TL | 33.91 | 667000 | 667012 | 1 | Interconnect New Generation
MISO_IN | B1/B13 | 0 | Reynolds - Greentown 765 | 66 | 700555 | 243207 | 1 | Interconnect New Generation | Wind Integration
MISO_IN | B1/B13 | 0 | Reynolds-Meadow Lk - Sullivan 765 | 126 | 700555 | 243210 | 1 | Interconnect New Generation | Wind Integration
MISO_IN | B1/B13 | 3 | 05BREED 345 - 16WHEAT 345 Reconductor | 30 | 243213 | 254539 | 1 | Loading >100% of System Emergency | Loss of Jefferson - Rockport 765
MISO_IN | B1/B13 | 3 | 08HORTVL 345 - 08NOBLSV 345 Reconductor | 11.46 | 249513 | 249515 | 1 | Loading >100% of System Emergency | Loss of Whitestown - Guion 345
MISO_IN | B1/B13 | 3 | 08NUCOR 345 - 08WHITST 345 Reconductor | 27.99 | 249516 | 249529 | 1 | Loading >100% of System Emergency | Loss of Amo - Edwardsport 345
MISO_IN | B1/B13 | 3 | 08WHITST 345 - 16GUION 345 Reconductor | 10 | 249529 | 254523 | 1 | Loading >100% of System Emergency | Loss of Hortonville - Noblesville 345
MISO_IN | B1/B13 | 3 | 16PETE 345 - 16WHEAT 345 Reconductor | 10.7 | 254529 | 254539 | 6 | Loading >100% of System Emergency | Loss of Jefferson - Rockport 765
MISO_IN | B1/B13 | 4 | 08CAYUGA 345 - 08NUCOR 345 Reconductor | 32.29 | 249505 | 249516 | 1 | Loading >100% of System Emergency | Loss of Amo - Edwardsport 345
MISO_IN | B1/B13 | 4 | 08GIBSON 345 - 08FRNCSC 345 Reconductor | 21.83 | 249510 | 249531 | 1 | Loading >100% of System Emergency | Loss of Gibson - AB Brown 345
MISO_IN | B1/B13 | 4 | 7WILSON 345 - 7REID 345 Reconductor | 25 | 340561 | 340562 | 1 | Loading >100% of System Emergency | Loss of Reid 345/161 Xfmr
MISO_MI | B1/B13 | 3 | 18MCV 345 - 18TITBAW 345 Reconductor | 2.47 | 256016 | 256027 | 1 | Loading >100% of System Emergency | Loss of MCV - Tittabawasee 345
MISO_MI | B1/B13 | 3 | 19PONTC 345 - 19WIXOM 345 Reconductor | 24.7 | 264635 | 264697 | 1 | Loading >100% of System Emergency | Loss of Pontiac - Placid 345
MISO_MI | B1/B13 | 3 | 19STEPH 345 - 19CANIF 345 Reconductor | 7.29 | 264664 | 264752 | 1 | Loading >100% of System Normal | Base Case
MISO_MI | B1/B13 | 4 | 18COVERT 345 - 18PALISD 345 Reconductor | 0.6 | 256018 | 256019 | 1 | Loading >100% of System Emergency | Loss of Covert - Palisades 345 Ckt 2
MISO_MI | B1/B13 | 4 | 18COVERT 345 - 18PALISD 345 Reconductor | 0.6 | 256018 | 256019 | 2 | Loading >100% of System Emergency | Loss of Covert - Palisades 345 Ckt 1
MISO_MO_IL | B1/B13 | 0 | Fairport - West AdairTap 345 | 101.13 | 300039 | 344002 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Thomas Hill - West AdairTap 345 | 47.25 | 300049 | 344002 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | West AdairTap - Ottumwa 345 | 57.75 | 344002 | 631143 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | West AdairTap - Palmyra 345 | 61.71 | 344002 | 345436 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Sidney - Rising 345 | 28 | 348887 | 348882 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Oak Grove - Galesburg 345 | 32 | 636635 | 348940 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Galesburg - Fargo 345 | 45 | 348940 | 349730 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Galesburg 345/138 Xfmr | NA | 348940 | 348915 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Palmyra - Quincy 345 | 15 | 345435 | 348060 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Quincy - Meredosia 345 | 45 | 348060 | 347679 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Quincy 345/138 Xfmr | NA | 348060 | 348061 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Meredosia - Ipava 345 | 35 | 347679 | 347288 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Meredosia - Pawnee 345 | 63 | 347679 | 347962 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Meredosia 345/138 Xfmr | NA | 347679 | 347680 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Pawnee - Pana 345 | 22 | 347962 | 347945 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Pawnee 345/138 Xfmr | NA | 347962 | 347963 | 2 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Pana - Mt Zion 345 | 30 | 347945 | 348961 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Pana 345/138 Xfmr | NA | 347945 | 347946 | 2 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Mt Zion - Kansas 345 | 52 | 348961 | 347340 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Mt Zion 345/138 Xfmr | NA | 348961 | 348872 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Kansas - Sugar Creek 345 | 35 | 347340 | 249521 | 1 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 0 | Kansas 345/138 Xfmr | NA | 347340 | 347341 | 2 | Interconnect New Generation | Wind Integration
MISO_MO_IL | B1/B13 | 3 | 7MONTGMRY 345 - 7SPENCER 345 Reconductor | 28.2 | 345230 | 345992 | 1 | Loading >100% of System Emergency | Loss of Callaway Generator
MISO_MO_IL | B1/B13 | 3 | 7GOOS_CRK 345 - 7RISING 345 Reconductor | 14.71 | 348770 | 348882 | 1 | Loading >100% of System Emergency | Loss of Pontiac - Brokaw 345
MISO_MO_IL | B1/B13 | 4 | 7KELSO 345 - 7LUTESVIL 345 Reconductor | 17.6 | 344849 | 344974 | 1 | Loading >100% of System Emergency | Loss of E W Frankfort - Shawnee 345
MISO_MO_IL | B1/B13 | 4 | 7E W FKFT 345 - 7SHAWNEE FP 345 Reconductor | 60 | 346992 | 360002 | 1 | Loading >100% of System Emergency | Loss of Lutesville - St Francis 345
MISO_MO_IL | B1/B13 | 4 | 6JOPPA 230 - 6W.FRKFT 230 Reconductor | 47.62 | 347330 | 348424 | 1 | Loading >100% of System Emergency | Loss of E W Frankfort - Shawnee 345
MISO_MO_IL | B1/B13 | 4 | 7GOOS_CRK 345 - 7MAROA E JCT345 Reconductor | 16.43 | 348770 | 348850 | 1 | Loading >100% of System Emergency | Loss of Pontiac - Brokaw 345
MISO_W | B1/B13 | 0 | Lakefield - Winnebago 345 | 55 | 631138 | 777000 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Winnebago - Winnco 345 | 38 | 777000 | 777001 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Winnebago 345/161 Xfmr | NA | 777000 | 631043 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Winnco - WZ_IA-J 345 | 2.73 | 777001 | 700003 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Winnco - Lime Creek 345 | 50 | 777001 | 777002 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Webster - WZ_IA-J 345 | 36.27 | 636000 | 700003 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-F - WZ_IA-J 345 | 56.8 | 777005 | 700003 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Sheldon - IA-F 345 | 14.2 | 635368 | 777005 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Lime Creek - Emery 345 | 11 | 777002 | 777003 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Lime Creek 345/161 Xfmr | NA | 777002 | 631047 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Emery - Blackhawk 345 | 73 | 777003 | 777004 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Emery 345/161 Xfmr | NA | 777003 | 631048 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Blackhawk - Hazelton 345 | 29 | 777004 | 631139 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Blackhawk 345/161 Xfmr | NA | 777004 | 636200 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Ellendale - Big Stone 345 | 145 | 661025 | 620313 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Brookings County - Big Stone 345 | 100 | 601031 | 620313 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BISON3 345 - PRAIRIE3 345 | 73 | 601055 | 657946 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BISON3 345 - PRAIRIE3 345 | 73 | 601055 | 657946 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BISON3 345 - HANKSON 345 | 55 | 601055 | 700353 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BRKNGCO3 345 - SD-H STA 345 | 63.58 | 601031 | 700343 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BRKNGCO3 345 - SD-J STA 345 | 67 | 601031 | 700344 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | ALEXSS3 345 - HANKSON 345 | 91.11 | 601046 | 700353 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | LAKEFLD3 345 - IA-B STA 345 | 46.76 | 631138 | 700356 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | HAZLTON3 345 - WEBSTER3 345 | 111.5 | 631139 | 636000 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | OTTUMWA3 345 - MO-C STA 345 | 19.58 | 631143 | 700399 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | GRIMES 3 345 - GU CTR 5 345 | 34.88 | 635600 | 700355 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | GRIMES 3 345 - GU CTR 5 345 | 34.88 | 635600 | 700355 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | WEBSTER3 345 - IA-G STA 345 | 70 | 636000 | 700358 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | WEBSTER3 345 - IA-J STA 34 | 15.05 | 636000 | 700397 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | CENTER 3 345 - MCHENRY 345 | 79.98 | 657791 | 700350 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | CENTER 3 345 - TTNKPOI4 345 | 130 | 657791 | 700392 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | PRAIRIE3 345 - ND-NWSTA 345 | 63 | 657946 | 700351 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | PRAIRIE3 345 - ND-NWSTA 345 | 63 | 657946 | 700351 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MN-K STA 345 - IA-J STA 345 | 15.05 | 700341 | 700397 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | SD-H STA 345 - SD-J STA 345 | 68.16 | 700343 | 700344 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | SD-H STA 345 - TTNKPOI4 345 | 125 | 700343 | 700392 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MCHENRY 345 - ND-NWSTA 345 | 141.2 | 700350 | 700351 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | HANKSON 345 - FORMAN 345 | 34 | 700353 | 700396 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | HANKSON 345 - FORMAN 345 | 34 | 700353 | 700396 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | GU CTR 5 345 - IA-H STA 345 | 48.41 | 700355 | 700359 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-B STA 345 - IA-F STA 345 | 29 | 700356 | 700357 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-F STA 345 - IA-G STA 345 | 44.17 | 700357 | 700358 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-G STA 345 - IA-H STA 345 | 46.51 | 700358 | 700359 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | ELLENDL4 345 - TTNKPOI4 345 | 20 | 700368 | 700392 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | ELLENDL4 345 - TTNKPOI4 345 | 20 | 700368 | 700392 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | ELLENDL4 345 - OAKES 345 | 24 | 700368 | 700395 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | ELLENDL4 345 - OAKES 345 | 24 | 700368 | 700395 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | OAKES 345 - FORMAN 345 | 22 | 700395 | 700396 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | OAKES 345 - FORMAN 345 | 22 | 700395 | 700396 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MITCHLCO 765 - MN-K STA 765 | 56.51 | 700528 | 700531 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MITCHLCO 7657 - HMPT CNR 765 | 80 | 700528 | 700536 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MITCHLCO 765 - HILLS 3 765 | 153.75 | 700528 | 700543 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MITCHLCO 765 - NLAX 3 765 | 91 | 700528 | 700560 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BRKNGCO 765 - HMPT CNR 765 | 181 | 700529 | 700536 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BRKNGCO 765 - BL2_F2 765 | 21.35 | 700529 | 700550 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | LKFLDXL3 765 - MN-K STA 765 | 71.66 | 700530 | 700531 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | LKFLDXL3 765 - IA-G STA 765 | 94 | 700530 | 700541 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | LKFLDXL3 765 - BL1_F1 765 | 60.98 | 700530 | 700549 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-G STA 765 - GRIMES 3 765 | 118.68 | 700541 | 700542 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | GRIMES 3 765 - HILLS 3 765 | 124.09 | 700542 | 700543 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | BL1_F1 765 - BL2_F2 765 | 30.54 | 700549 | 700550 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Brookings Co 765/345 Xfmr | NA | 601031 | 700529 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Brookings Co 765/345 Xfmr | NA | 601031 | 700529 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | N LaCrosse 765/345 Xfmr | NA | 601044 | 700560 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Hampton Corner 765/345 Xfmr | NA | 601051 | 700536 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Buffalo Ridge 765/115 Xfmr | NA | 603134 | 700550 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Buffalo Ridge 765/115 Xfmr | NA | 603134 | 700550 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Chanarambie 765/115 Xfmr | NA | 603180 | 700549 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Chanarambie 765/115 Xfmr | NA | 603180 | 700549 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Hankinson 345/230 Xfmr | NA | 620327 | 700353 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Hankinson 345/230 Xfmr | NA | 620327 | 700353 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Oakes 345/230 Xfmr | NA | 620362 | 700395 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Foreman 345/230 Xfmr | NA | 620363 | 700396 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Lakefield 765/345 Xfmr | NA | 631138 | 700530 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Mitchell Co 765/345 Xfmr | NA | 631144 | 700528 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Grimes 765/345 Xfmr | NA | 635600 | 700542 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Hills 765/345 Xfmr | NA | 636400 | 700543 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Ellendale 345/115 Xfmr | NA | 661027 | 700368 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Tatanka 345/230 Xfmr | NA | 661096 | 700392 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Tatanka 345/230 Xfmr | NA | 661096 | 700392 | N2 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | MN-K 765/345 Xfmr | NA | 700341 | 700531 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | IA-G 765/345 Xfmr | NA | 700358 | 700541 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | McHenry 230/115 Xfmr | NA | 615348 | 615347 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Panther 230/69 Xfmr | NA | 615530 | 615529 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 0 | Panther 230/69 Xfmr | NA | 619977 | 619975 | N1 | Interconnect New Generation | Wind Integration
MISO_W | B1/B13 | 2 | MN-I - Marysville 400 | 666.68 | 700527 | 242928 | DC | Loading >100% of System Normal | Many severe overloads delivering power per NEEM specifications
MISO_W | B1/B13 | 2 | IA-G - Sullivan 400 | 546.27 | 700541 | 243210 | DC | Loading >100% of System Normal | Many severe overloads delivering power per NEEM specifications
MISO_W | B1/B13 | 2 | Lakefield - Greentown 400 | 626.27 | 700530 | 243207 | DC | Loading >100% of System Normal | Many severe overloads delivering power per NEEM specifications
MISO_W | B1/B13 | 2 | Brookings County - Collins 400 | 558.25 | 700529 | 270607 | DC | Loading >100% of System Normal | Many severe overloads delivering power per NEEM specifications
MISO_W | B1/B13 | 3 | ATCHSNT3 345 - BOONVIL3 345 Reconductor | 103.34 | 635017 | 635630 | 1 | Loading >100% of System Emergency | Loss of Atchison - Cooper 345
MISO_W | B1/B13 | 3 | ATCHSNT3 345 - COOPER 3 345 Reconductor | 17.54 | 635017 | 640139 | 1 | Loading >100% of System Emergency | Loss of Atchison - Boonville 345
MISO_W | B1/B13 | 3 | HILLS 3 345 - SUB 92 3 345 Reconductor | 16.32 | 636400 | 636630 | 1 | Loading >100% of System Emergency | Loss of Hills - Sub T 345
MISO_W | B1/B13 | 4 | ADAMS 3 345 - GRE-PL VLLY3345 Reconductor | 17 | 601002 | 615306 | 1 | Loading >100% of System Emergency | Loss of MN-I - Hampton Corner 765
MISO_W | B1/B13 | 4 | ADAMS 3 345 - MITCHLCO3 345 Reconductor | 8.04 | 601002 | 631144 | 1 | Loading >100% of System Emergency | Loss of MN-I - Hampton Corner 765
MISO_W | B1/B13 | 4 | OAKGROV3 345 - LOUISA 3 345 Reconductor | 27.59 | 636635 | 636640 | 1 | Loading >100% of System Emergency | Loss of Walcott - Sub 92 345
MISO_W | B1/B13 | 6 | BRKNGCO3 345 - SD-H STA 345 Conductor size increase | 63.58 | 601031 | 700343 | N1 | Loading >100% of System Emergency | Loss of Brookings Co - SD-J 345
MISO_W | B1/B13 | 6 | LAKEFLD3 345 - IA-B STA 345 Conductor size increase | 46.76 | 631138 | 700356 | N1 | Loading >100% of System Emergency | Loss of IA-F - IA-G 345
MISO_W | B1/B13 | 6 | IA-F STA 345 - IA-G STA 345 Conductor size increase | 44.17 | 700357 | 700358 | N1 | Loading >100% of System Emergency | Loss of Lakefield - IA-B 345
MISO_WUMS | B1/B13 | 2 | Branch River 345kV 8x50MVAR Reactors | NA | 693636 |  |  | High Voltage | Voltage at Pt Beach Nuclear exceeds IA level
MISO_WUMS | B1/B13 | 2 | La Crosse - North Madison 345kV TL | 136.3 | 601044 | 699818 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | North Madison - Cardinal 345kV TL | 20.6 | 699818 | 699829 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | Cardinal - Eden 345kV TL | 48.4 | 699829 | 693863 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | Eden - Dubuque Co 345kV TL | 70.5 | 693863 | 631180 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | Cardinal 345/138kV XFMR | NA | 699829 | 699820 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | Cardinal 345/138kV XFMR | NA | 699829 | 699820 | 2 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1/B13 | 2 | Eden 345/138kV XFMR | NA | 693863 | 699034 | 1 | Loading >100% of System Emergency | Overload of Arpin-Rocky Run-Werner West-N Appleton 345kV Overload of Forest Jct-Cypress-Arcadian 345kV Overload of Stone Lake-Gardner Park 345kV
MISO_WUMS | B1 | 3 | Oak Creek-Elm Rd 230-345kV XFMR Replacement | NA | 698857 | 699367 | 1 | Loading >100% of System Emergency | Overload of Oak Creek-Elm Rd 230-345-kV Xfmr
MISO_WUMS | B1/B13 | 3 | Granville- Bluemound 345kV TL | 10 | 698871 | 694080 | 1 | Loading >100% of System Emergency | Overload of Butler-Granville-Tosa 138kV Overload of Granville-Rangeline 138kV Overload of Granville 345/138kV XFMR #3
MISO_WUMS | B1/B13 | 3 | Bluemound 345/230kV XFMR | NA | 694080 | 698862 | 1 | Loading >100% of System Emergency | Overload of Butler-Granville-Tosa 138kV Overload of Granville-Rangeline 138kV Overload of Granville 345/138kV XFMR #3
Nebraska | B1/B13 | 0 | Hooker - Columbus East 765kV |  | 640444 | 640501 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Columbus East - Sarpy 765kV |  | 640501 | 645460 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Sarpy - Iatan 765kV |  | 645460 | 543003 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Sarpy - Moore 765kV |  | 645460 | 640502 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Moore - Grand Island |  | 640502 | 640500 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Grand Island - Iatan 765kV |  | 640500 | 543003 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Grand Island - Gentleman 765kV |  | 640500 | 640186 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Gentleman - Hooker 765kV |  | 640186 | 640444 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Gentleman - Pauline 765kV |  | 640186 | 640354 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Pauline - Iatan 765kV |  | 640354 | 543003 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Gentleman 765/345kV XFMR |  | 640183 | 640186 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Pauline 765/345kV XFMR |  | 640312 | 640354 | 1 | Interconnect New Generation
Nebraska | B1/B13 | 0 | Mingo - Grand Island 765kV |  | 531453 | 640500 | 1 | Interconnect New Generation
New England ISO | B1/B13 | 1 | Scobie - Tewksbury 345 kV TL |  | 104143 | 113951 | 1 | Loading >100% of System Emergency | Loss of NU_394_SBK - NU_394_NGR 345 kV TL - New Line
New England ISO | B1/B13 | 1 | Tewksbury - Woburn 345 kV TL |  | 113951 | 110756 | 2 | Loading >100% of System Emergency | Loss of NU_394_SBK - NU_394_NGR 345 kV TL - New Line
New England ISO | B1/B13 | 1 | Woburn - N. Cambridge 345 kV TL |  | 110756 | 110758 | 3 | Loading >100% of System Emergency | Loss of NU_394_SBK - NU_394_NGR 345 kV TL - New Line
New England ISO | B1/B13 | 1 | Ward Hill - Wakefield JCT 345 kV TL |  | 113952 | 114476 | 1 | Loading >100% of System Emergency | Loss of NU_394_SBK - NU_394_NGR 345 kV TL - New Line
New England ISO | B1 | 0 | CT LAKES - SEA STRATTON115 kV TL |  | 90115 | 100169 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | PITTSTON ME - PITTSTN CLR1 115 kV TL |  | 90117 | 90118 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | PITTSTON ME - HARRIS HYDRO 115 kV TL |  | 90117 | 100111 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | MARTHAS VYND - FALMOUTH TAP 115 kV TL |  | 90130 | 111206 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | ASHLAND ME - ASHLAND 115 kV TL |  | 90135 | 104396 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | CANAL - HATCHVILLE 115 kV TL |  | 90140 | 111209 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | SEA STRATTON - PITTSTON ME 345 kV TL |  | 90305 | 90317 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | SEA STRATTON - ORRINGTON 345 kV TL |  | 90305 | 100002 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | DRACTU MA - ORRINGTON 345 kV TL |  | 90308 | 100002 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | DRACTU MA - MILLBURY 345 kV TL |  | 90308 | 113264 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | PITTSTON ME - ASHLAND ME 345 kV TL |  | 90317 | 90335 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | WHITTING ME - HARRINGTON 345 kV TL |  | 90321 | 90322 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | WHITTING ME -ORRINGTON 345 kV TL |  | 90321 | 100002 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | HARRINGTON - TRENTON 345 kV TL |  | 90322 | 90323 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | TRENTON - ORRINGTON 345 Kv TL |  | 90323 | 100002 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BARNSTABLE - LONG TRM LSM 345 kV TL |  | 90326 | 111134 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | ASHLAND ME - ORRINGTON 345 kV TL |  | 90335 | 100002 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | STURTEVANT - LIVERMORE FL 115 kV TL |  | 100116 | 100117 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BEEBE RIVER - WEBSTER 115 kV TL |  | 104374 | 104418 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | WEBSTER - DEERFIELD 115 kV TL |  | 104418 | 104506 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BARNSTABLE - HATCHVILLE 115 kV TL |  | 111202 | 111209 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BARNSTABLE - HARWICH MCGR 115 kV TL |  | 111202 | 111218 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | FALMOUTH TAP - HATCHVILLE 115 kV TL |  | 111206 | 111209 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | WELLFLEET - ORLEANS 115 Kv TL |  | 111216 | 111221 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | HARWICH MCGR - ORLEANS 115 Kv TL |  | 111218 | 111221 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | MILLBURY - MANCHESTER 345 kV TL |  | 113264 | 119077 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | KENYON - KENT COUNTY 115 kV TL |  | 117305 | 117332 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BELFAST - HIGHLAND 345 kV TL |  | 90324 | 90325 | C1 | Interconnect New Generation
New England ISO | B1 | 0 | BELFAST - ORRINGTON 345 kV TL |  | 90324 | 100002 | C1 | Interconnect New Generation
NYISO__A-F | B1/B13 | 0 | MASS 765 765.00 - CHA-NY 765.00 |  | 147828 | 180819 | 2 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Moses - Adirondack B1 345 kV |  | 999840 | 999835 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Moses - Adirondack B2 345 kV |  | 999840 | 999836 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Adirondack B1 - Chases Lake 345 kV |  | 999835 | 999841 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Adirondack B2 - Edic 345 kV |  | 999836 | 137200 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Chases Lake - Marcy 345 kV |  | 999841 | 147833 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Marcy - Jordanville 345 kV |  | 147833 | 999837 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Jordanville - Princetown 345 kV |  | 999837 | 137728 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Princetown - New Scotland 345 kV |  | 137728 | 137754 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | New Scotland - Leeds 345 |  | 137754 | 137451 | 3 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Leeds - Pleasant Valley 345 kV |  | 137451 | 126296 | 3 | Loading >100% of System Emergency | L/O parrallel Leeds-Athens/Pleasant Valley Line(s)
NYISO__A-F | B1/B13 | 0 | Princetown - Rotterdam 230 kV |  | 137729 | 137730 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Princetown - Rotterdam 230 kV |  | 137729 | 137730 | 2 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 3 | Princetown - Rotterdam 230 kV |  | 137729 | 137730 | 3 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Rock Tavern - Ramapo 345 kV |  | 125001 | 126297 | 2 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 0 | Fraser - Oakdale 345 kV |  | 130753 | 130755 | 2 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1/B13 | 3 | Fraser - Coopers Corners 345 kV (reconductor) |  | 130753 | 130750 | 1 | Loading >100% of System Emergency | Large HQ -> NYISO_A-F Transfer
NYISO__A-F | B1 | 3 | Marcy 765 kV - 200 MVAr Cap Bank |  | 147827 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Adinrondack B1 345 kV - 150 MVAr Cap Bank |  | 999835 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Chases Lake 345 kV - 150 MVAr Cap Bank |  | 999841 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Adinrondack B2 345 kV - 150 MVAr Cap Bank |  | 999836 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Marcy 345 kV - 150 MVAr Cap Bank |  | 147833 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Edic 345 kV - 150 MVAr Cap Bank |  | 137200 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Jordanville 345 kV - 150 MVAr Cap Bank |  | 999837 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Princetown 345 kV - 150 MVAr Cap Bank |  | 137728 |  |  | Low Voltage | Low Voltage along Massena-Marcy-New Scotland path
NYISO__A-F | B1 | 3 | Coopers Corners 345 kV - 150 MVAr Cap Bank |  | 130750 |  |  | Low Voltage | Low Voltage at Coopers Corners
NYISO_GHI | B13 | 0 | Pleasant Valley - Long Mountain 345 kV |  | 126296 | 119259 | 2 | Loading >100% of System Emergency | Added to wheel-through from ISO-NE to NYISO_JK via NYISO_GHI
PJM_Eastern_MAAC | B1/B13 | 0 | Peach Bottom - Cooper 230kV TL (double ckt or rebuild) |  | 213869 | 214089 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1/B13 | 0 | Cooper - Graceton 230kV TL (double ckt or rebuild) |  | 214089 | 220964 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1/B13 | 0 | Essex - Kearny 4-6 230kV TL (double ckt or rebuild) |  | 217079 | 217061 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1/B13 | 0 | Peach Bottom - Conastone 500kV TL (terminal equip. uprate) |  | 200013 | 200004 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1/B13 | 0 | Cedar Grove - Athenia 230kV TL |  | 216916 | 216900 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | Safe Harbor - Graceton 230kV TL (double ckt or rebuild) |  | 208071 | 220964 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Graceton - Bagley 230kV TL (double ckt or rebuild) |  | 220964 | 221000 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | North Temple - Lyons 230kV TL (double ckt or rebuild) |  | 204508 | 204503 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Otter Creek - Conastone 230kV TL (double ckt or rebuild) |  | 208048 | 220963 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Dickerson - Station H - Dickerson 230kV TL (double ckt or rebuild) |  | 223938 | 223937 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Ironwood - South Lebanon 230kV TL (double ckt or rebuild) |  | 204518 | 204511 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Graceton - Bagley 230kV TL (terminal equip. uprate) |  | 220964 | 220999 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | North Temple - Hosensack 230kV TL (terminal equip. uprate) |  | 204508 | 207983 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | North Temple - North Kill 230kV TL (terminal equip. uprate) |  | 204508 | 204875 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Raphael Road - Northeast 2315 & 2317 230kV TL (terminal equip. uprate) |  | 220980 | 220979 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1/B13 | 0 | Graceton - Bagley 230kV TL (terminal equip. uprate) |  | 220964 | 220999 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | Bagley - Raphael Road 230kV TL (terminal equip. uprate) |  | 221000 | 220980 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | Bagley - Raphael Road 230kV TL (terminal equip. uprate) |  | 220999 | 220980 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | Raphael Road - Northeast 2315 & 2317 230kV TL (terminal equip. uprate) |  | 220980 | 220979 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | Raphael Road - Northeast 2337 & 2339 230kV TL (terminal equip. uprate) |  | 220980 | 220965 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 0 | New Yorkana - Graceton 230kV TL |  | 204515 | 220964 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_MAAC | B1/B13 | 3 | Brighton - Kemptown 500kV TL (PATH) |  | 200003 | 235632 | 1 | Loading >100% of System Emergency | PATH project to address many overloads around Krammer 765kV and provide for an additional path to offload the 765kV system to the east part of PJM
PJM_Rest_of_MAAC | B1/B13 | 3 | Brighton - Kemptown 500kV TL (PATH) |  | 200003 | 235632 | 2 | Loading >100% of System Emergency
PJM_Rest_of_MAAC | B1/B13 | 3 | Conastone - Kemptown 500kV TL (PATH) |  | 200004 | 235632 | 1 | Loading >100% of System Emergency
PJM_Rest_of_MAAC | B1/B13 | 3 | Keystone 765/500kV XFMR |  | 980000 | 200011 | 1 | Loading >100% of System Emergency
PJM_Rest_of_MAAC | B1/B13 | 3 | Keystone 765/500kV XFMR |  | 980000 | 200011 | 2 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 0 | Lightfoot - Waller 230kV TL (double ckt or rebuild) |  | 314391 | 314415 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Gainesville - Loudoun 230kV TL (double ckt or rebuild) |  | 314037 | 314061 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Bermuda - Chesterfield 230kV TL (double ckt or rebuild) |  | 314278 | 314286 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Edwards Ferry - Dickerson 230kV TL (double ckt or rebuild) |  | 314290 | 223937 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Messer Rd - Charles City Road 230kV TL (double ckt or rebuild) |  | 314228 | 314225 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Chesterfield - Messer Rd 230kV TL (double ckt or rebuild) |  | 314287 | 314228 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Louisa CT - Gordonsville 230kV TL (double ckt or rebuild) |  | 314745 | 314758 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Hopewell - Bermuda 230kV TL (double ckt or rebuild) |  | 314303 | 314278 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | East Frankfort - Goodings Grove 345kV TL (terminal equip. uprate) |  | 270729 | 270767 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Kincaid - Pawnee West 345kV TL (terminal equip. uprate) |  | 270796 | 347962 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Braidwood - East Frankfort 345kV TL (terminal equip. uprate) |  | 270670 | 270728 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Lasalle - Braidwood 345kV TL (terminal equip. uprate) |  | 270802 | 270670 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Elmont - Ladysmith 500kV TL (terminal equip. uprate) |  | 314908 | 314911 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Pleasant View - Edwards Ferry 230kV TL (terminal equip. uprate) |  | 314072 | 314290 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Blue Mound - Pontiac Mid-Point 345kV TL (terminal equip. uprate) |  | 270668 | 270852 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | North Anna - Morrisville 500kV TL (terminal equip. uprate) |  | 314918 | 314916 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Bristers - Ox 500kV TL (terminal equip. uprate) |  | 314900 | 314919 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Mountaineer - Belmont 765kV TL (terminal equip. uprate) |  | 242516 | 242920 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Fredericksburg - Cranes Corner 230kV TL (terminal equip. uprate) |  | 314137 | 314134 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Byron - Cherry Valley 345kV TL (PJM West Overlay) |  | 270678 | 270694 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Cherry Valley - Silver Lake 345kV TL (PJM West Overlay) |  | 270694 | 270883 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Edwardsport - Rockport 765kV TL (PJM West Overlay) |  | 249533 | 243209 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Edwardsport - Sullivan 765kV TL (PJM West Overlay) |  | 249533 | 243210 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Byron - Nelson 765kV TL (PJM West Overlay) |  | 970020 | 970050 | S7 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Nelson - Kewanee 765 kV TL (PJM West Overlay) |  | 970050 | 970041 | S7 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Kewanee - Collins 765 kV TL (PJM West Overlay) |  | 970041 | 270607 | S7 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Kewanee - Pontiac 765 kV TL (PJM West Overlay) |  | 970041 | 970200 | S7 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Pontiac - Meadow Lake 765 kV TL (PJM West Overlay) |  | 970200 | 970048 | S7 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Meadow Lake - Sullivan 765 kV TL (PJM West Overlay) |  | 970048 | 243210 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | 2nd Marysville - Hyatt 345 kV TL (PJM West Overlay) |  | 242939 | 243458 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | 2nd Cloverdale - Lexington 500 kV TL (PJM West Overlay) |  | 242519 | 314912 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | 2nd Belmont 765/500 kV XFMR (PJM West Overlay) |  | 235102 | 242920 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | 3rd Meadow Lake - Dequin 345 kV TL (PJM West Overlay) |  | 243217 | 243878 | 3 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | 2nd Robison Park - Convoy 345 kV TL (PJM West Overlay) |  | 242933 | 243231 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1/B13 | 0 | Pleasant View - Edwards Ferry 230kV TL (terminal equip. uprate) |  | 314072 | 314290 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_RTO | B1/B13 | 0 | 4th Meadow Lake - Dequine 345kV TL |  | 243217 | 243878 | 4 | Interconnect New Generation | PJM Interconnection Analysis (Light)
PJM_Rest_of_RTO | B1 | 1 | Jacksons Ferry - Antioch 500kV TL (terminal equip. uprate) |  | 242520 | 306100 | 1 | Loading >100% of System Normal | Base case overload due to DC line injection
PJM_Rest_of_RTO | B1 | 1 | Mountaineer - Belmont 765kV TL (terminal equip. uprate) |  | 242516 | 242920 | 1 | Loading >100% of System Emergency | Loss of Kammer - Maliszewski 765kV TL
PJM_Rest_of_RTO | B1 | 1 | Maliszewski - Marysville 765kV TL (terminal equip. uprate) |  | 242926 | 242928 | 1 | Loading >100% of System Emergency | Loss of Mountaineer - Belmont 765kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Jackson Ferry 765/500 kV XFMR |  | 242514 | 242520 | 2 | Loading >100% of System Normal | Base case overload due to DC line injection
PJM_Rest_of_RTO | B1 | 1 | 2nd Marysville 765/345 kV XFMR |  | 242928 | 242939 | 2 | Loading >100% of System Emergency | Loss of Maliszewski - Marysville 765kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Jefferson-Clifty 765/345 kV XFMR |  | 243208 | 248000 | 2 | Loading >100% of System Emergency | Loss of Hanging Rock - Jefferson 765kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Bath County - Valley 500 kV TL |  | 314901 | 314926 | 2 | Loading >100% of System Emergency | Loss of Dooms - Lexington 500kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Dooms - Lexington 500 kV TL |  | 314907 | 314912 | 2 | Loading >100% of System Emergency | Loss of Bath County - Valley 500 kV TL
PJM_Rest_of_RTO | B13 | 1 | Cloverdale - Clover 500 kV TL |  | 242519 | 314906 | 1 | Loading >100% of System Emergency | Multiple thermal overloads around Cloverdale (outlet of DC lines at Hanging Rock and Jacksons Ferry)
PJM_Rest_of_RTO | B13 | 3 | Cloverdale 765/500 kV XFMR |  | 242519 | 242512 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B13 | 3 | Cloverdale 765/500 kV XFMR |  | 242519 | 242512 | 2 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B13 | 3 | Cloverdale 765/500 kV XFMR |  | 242519 | 242512 | 3 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B13 | 3 | 2nd Valley - Dooms 500kV TL |  | 314907 | 314926 | 2 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B13 | 3 | Cloverdale - Cunningham 500kV TL |  | 242519 | 314910 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B13 | 3 | Cloverdale - Cunningham 500kV TL |  | 242519 | 314910 | 2 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 3 | Don Marquis - Flatlick 765kV TL |  | 242927 | 242922 | 1 | Loading >100% of System Emergency | Loss of Hanging Rock - North Proctorville 765kV TL
PJM_Rest_of_RTO | B1/B13 | 3 | Doubs - Kemptown 500kV TL (PATH) |  | 235105 | 235632 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | Meadow Brook - Welton Springs 500kV TL (PATH) |  | 235110 | 235637 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | Welton Springs - Kemptown 765kV TL (PATH) |  | 235632 | 237045 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | Welton Springs - John Amos 765kV TL (PATH) |  | 235634 | 242508 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | Welton Springs - Mt Storm 500kV TL (PATH) |  | 235637 | 314917 | 2 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | Greentown - Marysville 765kV TL |  | 243207 | 242928 | 1 | Loading >100% of System Emergency | Additional path to offload the 765kV system as well as fix thermal overloads due to the outage of Greentown - Jefferson 765kV.
PJM_Rest_of_RTO | B1/B13 | 3 | Marysville - South Canton 765kV TL |  | 242928 | 242930 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1/B13 | 3 | South Canton - Keystone 765kV TL |  | 242930 | 980000 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 3 | 3rd Jacksons Ferry 765/500kV XFMR |  | 242514 | 242520 | 3 | Loading >100% of System Emergency | Loss of Jacksons Ferry 765/500 XFMR
PJM_Rest_of_RTO | B1 | 3 | 3rd Jefferson - Clifty 765/345 XFMR |  | 243208 | 248000 | 3 | Loading >100% of System Emergency | Loss of Jefferson - Clifty 765/500 XFMR
PJM_Rest_of_RTO | B1 | 3 | 2nd Reynolds - Meadow Lake 345kV TL |  | 243230 | 243878 | 2 | Loading >100% of System Emergency | Loss of Reynolds - Meadow Lake 765kV TL
PJM_Rest_of_RTO | B13 | 3 | 2nd Charlottesville - Holly Tap 230kV TL |  | 314749 | 314761 | 2 | Loading >100% of System Emergency | Loss of Elmont - Cunningham 500kV TL
PJM_Rest_of_RTO | B13 | 3 | 2nd Gordonville - Holly Tap 230kV TL |  | 314758 | 314761 | 2 | Loading >100% of System Emergency | Loss of Elmont - Cunningham 500kV TL
PJM_Rest_of_RTO | B13 | 4 | Re-conductor Kincaid - Pawnee 345kV TL |  | 270796 | 347962 | 1 | Loading >100% of System Emergency | Loss of Pana - Pawnee 345kV TL
PJM_Rest_of_RTO | B13 | 4 | Re-conductor Cordoba - Nelson 345kV TL |  | 270700 | 270828 | 1 | Loading >100% of System Emergency | Loss of Quad Cities - H471 345kV TL
PJM_Rest_of_RTO | B13 | 4 | Re-conductor Nelson - H471 345kV TL |  | 270828 | 270890 | 1 | Loading >100% of System Emergency | Loss of Cordoba - Nelson 345kV TL
PJM_Rest_of_RTO | B13 | 4 | Re-conductor Quad Cities - H471 345kV TL |  | 270864 | 270890 | 1 | Loading >100% of System Emergency | Loss of Cordoba - Nelson 345kV TL
SOCO | B1/B13 | 0 | Farley - Shoal River 500kV TL | 102 | 384600 | 389999 | 1 | Interconnect New Generation | 2 New Units @ Farley
SOCO | B1/B13 | 0 | Shoal River 500/230kV XFMR | NA | 389999 | 387310 | 1 | Interconnect New Generation | 2 New Units @ Farley
SOCO | B1/B13 | 0 | Farley - N. Americus 500kV TL | 88 | 384600 | 389996 | 1 | Interconnect New Generation | 2 New Units @ Farley
SOCO | B1/B13 | 0 | SOCO_NC - Billingsley 500kV TL | 50 | 389990 | 385123 | 1 | Interconnect New Generation | 4 New Units @ SOCO_NC
SOCO | B1/B13 | 0 | SOCO_NC - N. Brewton 500kV TL | 75 | 389990 | 389989 | 1 | Interconnect New Generation | 4 New Units @ SOCO_NC
SOCO | B1/B13 | 0 | SOCO_NC - Snowdoun 500kV TL | 50 | 389990 | 384512 | 1 | Interconnect New Generation | 4 New Units @ SOCO_NC
SOCO | B1/B13 | 0 | N. Brewton 500/230kV XFMR | NA | 389989 | 384623 | 1 | Interconnect New Generation | 4 New Units @ SOCO_NC
SOCO | B1/B13 | 3 | Miller 500/230kV XFMR | NA | 384157 | 384156 | 2 | Loading >100% of System Emergency | Loss of the Miller 500/230kV XFMR #1 - New XFMR
SOCO | B1/B13 | 3 | Billingsley - Wansley 500kV TL | 100 | 385123 | 380023 | 1 | Loading >100% of System Emergency | Loss of the S. Bessemer - Billinglsey 500kv TL - New Line
SOCO | B1/B13 | 3 | Rockville - East Walton 500kV TL (East Walton Project) | 47 | 380317 | 380017 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New Line
SOCO | B1/B13 | 3 | S. Hall - East Walton 500kV TL (East Walton Project) | 35 | 380011 | 380017 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New Line
SOCO | B1/B13 | 3 | East Walton 500/230kV XFMR (East Walton Project) | NA | 380017 | 382098 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New XFMR
SOCO | B1/B13 | 3 | East Walton - Bostwick 230kV TL (East Walton Project) | 5 | 382098 | 382059 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New Line
SOCO | B1/B13 | 3 | East Walton - Jacks Creek 230kV TL (East Walton Project) | 13 | 382098 | 382799 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New Line
SOCO | B1/B13 | 3 | East Walton - Bethabara 230kV TL (East Walton Project) | 10 | 382098 | 382055 | 1 | Loading >100% of System Emergency | Loss of the Oconee - Middlefork 500kV TL and Low Voltage - New Line
SOCO | B1/B13 | 3 | Bellefonte - Rocky Mountain 500kV TL | 55 | 360062 | 389900 | 1 | Loading >100% of System Emergency | Loss of the Conasauga - Conasauga CC 500kV TL - New Line
SOCO | B1/B13 | 3 | Russell - Athena 230kV TL | 50 | 339100 | 381311 | 1 | Loading >100% of System Emergency | Loss of the Russell - VACAR 230kV TL - New Line
SOCO | B1/B13 | 3 | Bellefonte - Rocky Mountain 500kV TL | 55 | 360062 | 380020 | 2 | Loading >100% of System Emergency | Loss of the Conasauga - Conasauga CC 500kV TL - New Line
SOCO | B1/B13 | 3 | Rocky Mountain - Mostellar 500kV TL | 30 | 389900 | 380021 | 1 | Loading >100% of System Emergency | For the removal of the SPP - TVA DC Line - New Line
SOCO | B1/B13 | 3 | Daniel - Ellicott 500kV TL | 50 | 388700 | 389901 | 1 | Loading >100% of System Emergency | For the removal of the SPP - TVA DC Line - New Line
SOCO | B1/B13 | 3 | Ellicott - N. Brewton 500kv TL | 60 | 389901 | 389989 | 1 | Loading >100% of System Emergency | For the removal of the SPP - TVA DC Line - New Line
SOCO | B1/B13 | 3 | N. Brewton - Shoal River 500kV TL | 50 | 389989 | 389999 | 1 | Loading >100% of System Emergency | Gulf Constraints - New Line
SOCO | B1/B13 | 3 | McGrau Ford - Hopewell 230kV TL | 12 | 380088 | 380209 | 2 | Loading >100% of System Emergency | Loss of Big Shanty - Bull Sluice 500kV TL - New Line
SOCO | B1/B13 | 3 | Hopewell 230kV/115kV TL | NA | 380209 | 380363 | 1 | Loading >100% of System Emergency | Addition of McFrau Ford - Hopewell 230kV TL - Upgrade XFMR
SOCO | B1/B13 | 3 | Rocky Mountain - Bowen 500kV TL | 30 | 389900 | 380020 | 1 | Loading >100% of System Emergency | Loss of the Conasauga - Conasauga CC 500kV TL - New Line
SOCO | B1/B13 | 3 | Daniel - Moss Point Elders Ferry 230kV TL | 9 | 388702 | 388705 | 1 | Loading >100% of System Emergency | For the removal of the SPP - TVA DC Line - Upgrade Line
SOCO | B1/B13 | 3 | Moss Point Elders Fery - Moss Point East 230kV TL | 2 | 388705 | 388710 | 1 | Loading >100% of System Emergency | For the removal of the SPP - TVA DC Line - Upgrade Line
SPP_N | B1/B13 | 0 | Iatan - Lang 765kV |  | 543003 | 532776 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Lang - RoseHill 765kV |  | 532776 | 532795 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | RoseHill - Sooner 765kV |  | 532795 | 514804 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Holcomb - Mingo 765kV |  | 531455 | 531453 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Holcomb - Medicine Lodge 765kV |  | 531455 | 765343 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Mingo - Gentleman 765kV |  | 531453 | 640186 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Mingo - PostRock 765kV |  | 531453 | 530610 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | PostRock - RoseHill 765kV |  | 530610 | 532795 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | PostRock - Medicine Lodge 765kV |  | 530610 | 765343 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Iatan 765/345kV XFMR |  | 542982 | 543003 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Lang 765/345kV XFMR |  | 532769 | 532776 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | RoseHill 765/345kV XFMR |  | 532794 | 532795 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Holcomb 765/345kV XFMR |  | 531449 | 531455 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | Mingo 765/345kV XFMR |  | 531451 | 531453 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 0 | PostRock 765/345kV XFMR |  | 530583 | 530610 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 3 | RoseHill - Iatan 765kV |  | 532795 | 543003 | 1 | Interconnect New Generation
SPP_N | B1/B13 | 3 | RoseHill - Iatan 765kV |  | 532795 | 543003 | 2 | Interconnect New Generation
SPP_N | B1/B13 | 3 | Iatan 765/345kV XFMR |  | 542982 | 543003 | 2 | Loading >100% of System Normal | Overload of Iatan 765/345kV Xfmr
SPP_N | B1/B13 | 3 | Iatan 765/345kV XFMR |  | 542982 | 543003 | 3 | Loading >100% of System Normal | Overload of Iatan 765/345kV Xfmr
SPP_N | B1/B13 | 3 | Lang - West Gardner 345kV |  | 532769 | 542965 | 1 | Loading >100% of System Normal | Overload of EMPEC - Swissvale - West Gardner 345kV line
SPP_N | B1/B13 | 3 | Lang - West Gardner 345kV |  | 532769 | 542965 | 2 | Loading >100% of System Normal | Overload of EMPEC - Swissvale - West Gardner 345kV line
SPP_N | B1/B13 | 3 | RoseHill 765/345kV XFMR |  | 532794 | 532795 | 2 | Loading >100% of System Normal | Overload of Rose Hill 765/345kV Xfmr
SPP_N | B1/B13 | 3 | EMPEC - Lang 345kV |  | 532768 | 532769 | 1 | Loading >100% of System Normal | Overload of EMPEC - Swissvale - West Gardner 345kV line
SPP_N | B1/B13 | 3 | EMPEC - Swissvale 345kV |  | 532768 | 532774 | 1 | Loading >100% of System Normal | Overload of EMPEC - Swissvale - West Gardner 345kV line
SPP_N | B1/B13 | 3 | Iatan - Stranger Creek 345kV |  | 532772 | 542982 | 2 | Loading >100% of System Normal | Overload of Stranger Creek - 87th 345kV line
SPP_N | B1/B13 | 3 | West Gardner - Stilwell 345kV |  | 542965 | 542968 | 2 | Loading >100% of System Emergency | Overload of West Gardner - Stilwell 345kV
SPP_N | B1/B13 | 3 | Wolf Creek - LaCygne 345kV |  | 532797 | 542981 | 2 | Loading >100% of System Normal | Overload of Wolf Creek - LaCygne 345kV
SPP_N | B1/B13 | 3 | Wolf Creek - Neosho 345kV |  | 532797 | 532793 | 1 | Loading >100% of System Normal | Overload of Wolf Creek - LaCygne 345kV
SPP_N | B1/B13 | 3 | Wichita - Medicine Lodge 345kV |  | 532796 | 765342 | 3 | Loading >100% of System Emergency | Overload of Wichita - Medicine Lodge 345kV
SPP_N | B1/B13 | 3 | Hawthorn - Nashua 345kV |  | 542972 | 542980 | 2 | Loading >100% of System Normal | Overload of Hawthorn - Nashua 345kV
SPP_N | B1/B13 | 3 | Holcomb - Medicine Lodge 765kV |  | 531455 | 765343 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Sooner - L.E.S 765kV |  | 514804 | 511543 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | L.E.S - Tuco 765kV |  | 511543 | 525833 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Tuco - Potter 765kV |  | 525833 | 523962 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Potter - Hitchland 765kV |  | 523962 | 523098 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Hitchland - Holcomb 765kV |  | 523098 | 531455 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Hitchland - Kelton 765kV |  | 523098 | 523080 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Medicine Lodge - Sooner 765kV |  | 765343 | 514804 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Kelton - Sooner 765kV |  | 523080 | 514804 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Kelton - L.E.S. 765kV |  | 523080 | 511543 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Kelton - Briscoe 765kV |  | 523080 | 526825 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Briscoe - Tuco 765kV |  | 526825 | 525833 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Sooner 765/345kV XFMR |  | 514803 | 514804 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | L.E.S. 765/345kV XFMR |  | 511468 | 511543 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Tuco 765/345kV XFMR |  | 525832 | 525833 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Potter 765/345kV XFMR |  | 523961 | 523962 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Hitchland 765/345kV XFMR |  | 523097 | 523098 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 0 | Medicine Lodge 765/345kV XFMR |  | 765342 | 765343 | 1 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Tuco Xfmr 765/345kV |  | 525832 | 525833 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Tuco Xfmr 765/345kV |  | 525832 | 525833 | 3 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Hitchland 765/345kV XFMR |  | 523097 | 523098 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Sooner - Kelton 765kV |  | 514804 | 523080 | 3 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Sooner - Medicine Lodge 765kV |  | 514804 | 765343 | 3 | Interconnect New Generation
SPP_S | B1/B13 | 3 | L.E.S. - Kelton 765kV |  | 511543 | 523080 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 3 | L.E.S. - Kelton 765kV |  | 511543 | 523080 | 3 | Interconnect New Generation
SPP_S | B1/B13 | 3 | L.E.S. 765/345kV XFMR |  | 511468 | 511543 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 3 | L.E.S. 765/345kV XFMR |  | 511468 | 511543 | 3 | Interconnect New Generation
SPP_S | B1/B13 | 3 | NW Texarkana - SW Shreveport 345kV |  | 508072 | 507760 | 1 | Loading >100% of System Normal | Overload of Welsh - Lydia - Valiant 345kV
SPP_S | B1/B13 | 3 | NW Texarkana - Welsh 345kV |  | 508072 | 508359 | 3 | Loading >100% of System Normal | Overload of Welsh - Lydia - Valiant 345kV
SPP_S | B1/B13 | 3 | NW Texarkana 765/345kV Xfmr |  | 508072 | 511544 | 4 | Interconnect New Generation
SPP_S | B1/B13 | 3 | L.E.S. - Sunnyside 345kV |  | 511468 | 515136 | 1 | Loading >100% of System Normal | Overload of Sunnyside - L.E.S. - Gracemount 345kV line
SPP_S | B1/B13 | 3 | L.E.S. - Gracemount 345kV |  | 511468 | 515800 | 1 | Loading >100% of System Normal | Overload of Sunnyside - L.E.S. - Gracemount 345kV line
SPP_S | B1/B13 | 3 | Kelson - Briscoe 765kV |  | 523080 | 526825 | 2 | Interconnect New Generation
SPP_S | B1/B13 | 3 | Tulsa North - Sooner 345kV |  | 509852 | 514803 | 1 | Loading >100% of System Normal | Overload of Cleveland - Tulsa North 345kV line
SPP_S | B1/B13 | 3 | Tulsa North - Sooner 345kV |  | 509852 | 514803 | 2 | Loading >100% of System Normal | Overload of Cleveland - Tulsa North 345kV line
SPP_S | B1/B13 | 3 | Sooner - Cleveland 345kV |  | 514803 | 512694 | 2 | Loading >100% of System Normal | Overload of Cleveland - Tulsa North 345kV line
TVA | B1/B13 | 3 | Jackson-Haywood 500 kV uprate | 26 | 360019 | 360542 | 1 | Loading >100% of System Emergency | This uprate helped relieve constraints on the Jackson-Haywood 500kV TL caused by the loss of the Weakley-Lagoon Creek 500kV TL
TVA | B1/B13 | 3 | Freeport-Bham Steel 500 kV uprate | 10 | 360023 | 360025 | 1 | Loading >100% of System Emergency | This uprate helped relieve constraints on the Freeport-Bham Steel 500kV TL caused by the loss of the WMEHV-Cordova 765kV TL
TVA | B1/B13 | 3 | Jackson-Lagoon Creek 500 kV TL | 37 | 360019 | 360568 | 1 | Loading >100% of System Emergency | Adding this 500 kV TL helped unload the Lagoon Creek-Weakley 500 kV TL- which when taken as a contingency caused several constraints at the 161 kV level
TVA | B1/B13 | 3 | Shawnee 500/345 kV Tr. | NA | 360001 | 360002 | 2 | Loading >100% of System Emergency | The addition of this transformer alleviated the overloaded condition of the Shawnee 500/345 kV Tr. #1
TVA | B1/B13 | 3 | Freeport 500/161 kV Tr. | NA | 360023 | 360024 | 2 | Loading >100% of System Emergency | The addition of this transformer alleviated the overloaded condition of the Freeport 500/161 kV Tr. #1
TVA | B1/B13 | 3 | Cordova-Haywood 500 kV uprate | 40 | 360025 | 360542 | 1 | Loading >100% of System Emergency | This uprate helped relieve constraints on the Cordova-Haywood 500kV TL caused by the loss of the Weakley-Lagoon Creek 500kV TL
VACAR | B1/B13 | 0 | LNS2-Newport 500 kV TL | 28 | 306104 | 309601 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | LNS2-Oconee 500 kV TL | 86 | 306105 | 309601 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | LNS1-Catawba 230 kV TL | 29 | 306121 | 309600 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | LNS1-Catawba 230 kV TL | 29 | 306121 | 309600 | 2 | Interconnect New Generation
VACAR | B1/B13 | 0 | LNS1-Pacolet 230 kV TL | 22 | 306147 | 309600 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | LNS1-Pacolet 230 kV TL | 22 | 306147 | 309600 | 2 | Interconnect New Generation
VACAR | B1/B13 | 3 | Antioch 500/230 kV XFMR | N/A | 306100 | 306112 | 1 | Loading >100% of System Emergency | For loss of the parallel bank - increase capacity
VACAR | B1/B13 | 3 | Antioch 500/230 kV XFMR | N/A | 306100 | 306112 | 2 | Loading >100% of System Emergency | For loss of the parallel bank - increase capacity
VACAR | B1/B13 | 3 | Antioch - Mitchell River 230 kV TL | 21 | 306140 | 306112 | 1 | Loading >100% of System Emergency | For loss of the parallel line - bundle conductor
VACAR | B1/B13 | 3 | Antioch - Mitchell River 230 kV TL | 21 | 306140 | 306112 | 2 | Loading >100% of System Emergency | For loss of the parallel line - bundle conductor
VACAR | B1/B13 | 3 | Allen - Catawba Nuclear 230 kV TL | N/A | 306110 | 306121 | 1 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1/B13 | 3 | Allen - Catawba Nuclear 230 kV TL | N/A | 306110 | 306121 | 2 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1/B13 | 3 | Morningstar - Newport 230 kV TL | 34 | 306144 | 306141 | 2 | Loading >100% of System Emergency | For loss of 500 kV line - install 2nd circuit
VACAR | B1/B13 | 3 | McGuire - Riverbend 230 kV TL | N/A | 306139 | 306154 | 1 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1/B13 | 3 | McGuire - Riverbend 230 kV TL | N/A | 306139 | 306154 | 2 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1/B13 | 0 | Wake-Wommack 500kV TL |  | 304183 | 305998 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | Harris#3-Wake 230kV TL |  | 304190 | 305997 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | Harris#3-Erwin 230kV TL |  | 304196 | 305997 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | Cumberland-Wommack 500kV TL |  | 304391 | 305998 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | Harris#3-FtBrWoodruff 230kV TL |  | 304398 | 305997 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | New Bern 500/230kV XFMR |  | 304465 | 305999 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | New Bern 500/230kV XFMR |  | 304465 | 305999 | 2 | Interconnect New Generation
VACAR | B1/B13 | 0 | New Bern-Wommack 500kV TL |  | 305998 | 305999 | 1 | Interconnect New Generation
VACAR | B1/B13 | 0 | New Bern-Wommack 500kV TL |  | 305998 | 305999 | 2 | Interconnect New Generation

## S2
Addition to base SSI model
Region | Load Block | Pass | Name | Mileage | Bus# | Bus# | Ckt ID | Reason/Need | If added for a loading or voltage Issue, what was the driver
MAPP_US | B1/B13 | 0 | BELFELD - CHAR.CK 345kV TL |  | 652424 | 659183 | 2,3 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | CHAR.CK - ANTELOP 345kV TL |  | 659183 | 659101 | 2,3 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | ANTELOP - LELANDO 345kV TL |  | 659101 | 659105 | 3 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | ANTELOP - MAPPCOR_COLB 345kV TL |  | 659101 | 652002 | 1,2 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | MAPPCOR_COLB - BELFELD 345kV TL |  | 652002 | 652424 | 1,2 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | BELFELD - MAPPCOR_COLA 345kV TL |  | 652424 | 652001 | 1,2 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | MAPPCOR_COLA - ANTELOP 345kV TL |  | 652001 | 659101 | 1,2 | Interconnect New Generation
MAPP_US | B1/B13 | 0 | MAPPCOR_COLB -DICKNSN 345/230kV XFMR | NA | 652002 | 652417 | 1 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP-MAPPCOR_HYSO 230kV TL |  | 667000 | 667424 | 1,2 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | RADSNDC6-MAPPCOR_HYS2 138kV TL |  | 667231 | 667425 | 1,2,3 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | HENDAY-MAPPCOR_HYS3 230kV TL |  | 667001 | 667426 | 1,2 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | RADSNDC - KEEYASK 138kV TL |  | 667231 | 667232 | 1,2,3 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP4 - RIEL bipole DC line |  | 667000 | 667041 | 39,40 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP - HENDAY 230kV TL |  | 667000 | 667001 | 1,2,3,4 | Interconnect New Generation
MAPP_CA | B1/B13 | 0 | CONAWAP -LONGSPR 230kV TL |  | 667000 | 667012 | 1 | Interconnect New Generation

## S3
Addition to base SSI model
Region | Load Block | Pass | Name | Mileage | Bus# | Bus# | Ckt ID | Reason/Need | If added for a loading or voltage Issue, what was the driver
ENTERGY | B1 | 1 | Construct Addis - Tiger 230 kV Ckt 2 | 5.73 | 335536 | 335665 | 2 | Loading >100% of System Emergency | Addis - Tiger 230 kV Ckt 1 overloads for the loss of (FTLO) Dow meter to Air Liquid Tap 230 kV Ckt 1
ENTERGY | B1 | 3 | Rexbrown upgrade station equipment | NA | 336938 | 339939 | 1 | Loading >100% of System Emergency | Address 115 kV thermal overload FTLO Ray Braswell 500/115 kV auto
ENTERGY | B1 | 3 | Upgrade Dumas to Lock and Dam 115 kV line | 15.31 | 337602 | 338514 | 1 | Loading >100% of System Emergency | Address 115kV thermal overload FTLO Gillette to Lock and Dam 115 kV line
ENTERGY | B1 | 3 | Upgrade Ray Braswell to West Jackson 115kV line | 6.41 | 336880 | 336882 | 1 | Loading >100% of System Emergency | Address 115kV thermal overload FTLO South Jackson 230/115 kV auto
ENTERGY | B1 | 3 | Upgrade Ray Braswell to Jackson Forest Hill 115kV line | 5.24 | 336871 | 336880 | 1 | Loading >100% of System Emergency | Address 115kV thermal overload FTLO South Jackson 230/115 kV auto
ENTERGY | B1 | 3 | Upgrade Conroe West to Conroe 138 kV line | 2.6 | 334099 | 334104 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload FTLO Porter 230/138 kV auto
ENTERGY | B1 | 3 | Upgrade Sorrento 138/115 kV auto | NA | 336050 | 336051 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload FTLO Wynadotte-Conway 138kV
ENTERGY | B1 | 3 | UpgradeGonzales to Sorrento 138 kV line | 4.65 | 335625 | 336050 | 1 | Loading >100% of System Emergency | Address 138 kV contingency overload FTLO Wynadotte-Conway 138kV
ENTERGY | B1 | 3 | Upgrade Wyandotte to Conway 138 kV line | 4.79 | 335589 | 335590 | 1 | Loading >100% of System Emergency | Address 138 kV thermal overload FTLO Willow Glen to Oak Grove 138 kV line
ENTERGY | B1 | 3 | Butler add capacitor bank | NA | 301342 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Clark add capacitor bank | NA | 300070 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Valley add capacitor bank | NA | 300143 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Gonzales add capacitor bank | NA | 335625 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Memorial add capacitor bank | NA | 300136 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Blackriver add capacitor bank | NA | 337318 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Pinebergen add capacitor bank | NA | 33866 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Centerville add capacitor bank | NA | 336520 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Trussell Crossing add capacitor bank | NA | 303310 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Searcy South add capacitor bank | NA | 338046 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | PPG add capacitor bank | NA | 335136 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 3 | Morton add capacitor bank | NA | 336898 | NA | NA | Low Voltage | Address low voltage for contingenies
ENTERGY | B1 | 1 | Insert series reactor, Madisonville Fairview | NA | 336138 | 500510 | 1 | Loading >100% of System Emergency | Fairview - Gypsy 230 kV Ckt 1 overloads FTLO Bogalusa - Franklin 500 kV Ckt 1
ENTERGY | B1 | 1 | Construct Freeport to Hornlake 230 kV Ckt 2 | 3.8 | 337162 | 337180 | 2 | Loading >100% of System Emergency | Freeport - Twinkle Town overloads FTLO Freeport - Hornlake Ckt 1
ENTERGY | B1 | 3 | Construct Carpenter to Albright 115kV ckt | 10 | 337721 | 337718 | 1 | Loading >100% of System Emergency | Hotsprings to Carpenter 115 kV overload ftlo Blakely to Mountain Pine South
ENTERGY | B1 | 1 | Add Huben 345/161 kV second auto | NA | 300042 | 300088 | 2 | Loading >100% of System Emergency | Huben 345/161 kV auto Ckt 1 overloads FTLO Morgan - Brookline 345 kV
ENTERGY | B1 | 3 | New Lewis Creek to West Conroe SS 230 kV | 12 | 334069 | 334088 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1 | 3 | New West Conroe SS to Grimes 230 kV | 38 | 334088 | 334990 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1 | 3 | New 345/230 kV auto at Grimes | NA | 334990 | 334028 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1 | 3 | New 230/138/13/8 kV three winding transformer at Conroe SS | NA | 334088 | 334099 | 1 | Loading >100% of System Emergency | Needed to relieve the overload on the the underlying 138 kV system in Entergy's Western Region under various contingency events
ENTERGY | B1 | 3 | Construct 2nd Plantation to Vidalia 115 kV line | 2.39 | 337320 | 337321 | 2 | Loading >100% of System Emergency | Ntachez to Redgum 115kV overload FTLO Plantation to Vidalia 115 kV
ENTERGY | B1 | 1 | Upgrade PPG to Rosebluff 230 kV Ckt 1 | 5.28 | 335136 | 335072 | 1 | Loading >100% of System Emergency | Rosebluff - PPG 230 kV Ckt 1 overloads FTLO Verdine - PPG 230 kV Ckt 1
ENTERGY | B1 | 1 | Add Sportsman 345/161 kV third auto | NA | 300740 | 300741 | 3 | Loading >100% of System Emergency | Sportsman 345/161 kV auto Ckt 1 overloads FTLO Sportsman 345/161 kV auto Ckt 2
ENTERGY | B1 | 1 | Add Thomasville 345/161 kV second auto | NA | 300049 | 300120 | 2 | Loading >100% of System Emergency | Thomasville 345/161 kv Ckt 1 overloads FTLO MCCRED to Thomasville 345 kV Ckt 1
ENTERGY | B1 | 1 | Upgrade Verdine to PPG 230 kV Ckt 1 | 2.27 | 335135 | 335136 | 1 | Loading >100% of System Emergency | Verdine - PPG 230 kV Ckt 1 overloads FTLO Rosebluff - PPG 230 kV Ckt 1
ENTERGY | B1 | 1 | Upgrade Viney to Hergett 161 kV Ckt 1 | 4 | 338157 | 505420 | 1 | Loading >100% of System Emergency | Viney - Hergett 161 kV Ckt 1 overloads FTLO Viney - Hergett 161 kV Ckt 2
ENTERGY | B1 | 1 | Upgrade Viney to Hergett 161 kV Ckt 2 | 4 | 338157 | 505420 | 2 | Loading >100% of System Emergency | Viney - Hergett 161 kV Ckt 2 overloads FTLO Viney - Hergett 161 kV Ckt 1
MAPP_CA | B1 | 1 | CODETTE - NIPAWIN 230kV TL | 3 | 672649 | 672650 | 2 | Loading >100% of System Emergency | double ckt existing single ckt line.
MAPP_CA | B1 | 1 | BD - REGINA 230kV TL | 140 | 672601 | 672607 | 3,4 | Loading >100% of System Emergency | For outage of one, the other overladed. Solved by reconductoring both
MAPP_CA | B1 | 1 | BEATTY - STOON E 230kV TL | 88 | 672638 | 672639 | 3,4 | Loading >100% of System Emergency | For outage of one, the other overladed. Solved by reconductoring both
MAPP_CA | B1 | 1 | EBCAMPB - CODETTE 230kV TL | 55 | 672630 | 672649 | 2 | Loading >100% of System Emergency | outage of E.B. Cambell-Beatty. Double ckt existing E.B. Cambell-Codette.
MAPP_CA | B1 | 1 | EBCAMPB - BEATTY 230kV TL | 100 | 672630 | 672638 | 2 | Loading >100% of System Emergency | outage of E.B. Cambell-Codette. Double ckt existing E.B. Cambell-Beatty.
MAPP_CA | B1 | 2 | BD - KENNEDY 230kV TL | 90 | 672601 | 672609 | 1 | Loading >100% of System Emergency | overloaded for outage of Peebles - Shand. Solved by reconductoring.
MAPP_CA | B1 | 1 | ROSSER - RIDGEWY 230kV TL | 10.15 | 667038 | 667039 | 2 | Loading >100% of System Emergency | This line overloaded for outage of Dorsey-Riel 50kV line, so double ckt existing single ckt line
MAPP_US | B1 | 1 | LELND1TY 345/230kV XFMR | NA | 659105 | 659106 | 2 | Loading >100% of System Emergency | existing transformer overload for outage of parallel transformer, so add a second transformer
MAPP_US | B1 | 1 | LELND2TY 345/230kV XFMR | NA | 659105 | 659106 | 2 | Loading >100% of System Emergency | existing transformer overload for outage of parallel transformer, so add a second transformer
MAPP_US | B1 | 2 | BISMARK - WASHBRN 230kV TL | 39.49 | 652426 | 652456 | 2,3 | Loading >100% of System Emergency | overloaded due to Stanton to Leland Olds outgage. Replace with new double ckt
MAPP_US | B1 | 2 | WASHBRN -LELANDO 230kV TL | 14.62 | 652456 | 659106 | 2,3 | Loading >100% of System Emergency | overloaded due to Stanton to Leland Olds outgage. Replace with new double ckt
MISO_IN | B1 | 1 | Bloomington 230 Bus Tie | NA | 249605 | 249640 | 2 | Loading >100% of System Emergency | Loss of Bloomington 345/230 Xfmr
MISO_IN | B1 | 1 | Columbus 345/230 Xfmr | NA | 249506 | 249612 | 2 | Loading >100% of System Emergency | Loss of Columbus - Prescott 345
MISO_IN | B1 | 1 | Wilson - Reid 345 Reconductor | 25 | 340561 | 340562 | 1 | Loading >100% of System Emergency | Loss of Jefferson - Rockport 765
MISO_MI | B1 | 1 | Covert - T-94A 345 | NA | 256018 | 292290 | 2 | Loading >100% of System Emergency | Loss of Covert - Palisades 345
MISO_MI | B1 | 1 | Covert - Palisades 345 | 0.6 | 256018 | 256019 | 2 | Loading >100% of System Emergency | Loss of Covert - T-94A 345
MISO_MI | B1 | 1 | MCV - Tittabawasee 345 Reconductor | 2.47 | 256016 | 256027 | 2 | Loading >100% of System Emergency | Loss of MCV - Tittabawasee 345 Ckt 1
MISO_MI | B1 | 1 | MCV - Tittabawasee 345 Reconductor | 2.47 | 256016 | 256027 | 1 | Loading >100% of System Emergency | Loss of MCV - Tittabawasee 345 Ckt 2
MISO_MO_IL | B1 | 1 | Palmyra - Quincy 345 | 14 | 345435 | 347010 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_MO_IL | B1 | 1 | Quincy - Meredosia 345 | 47 | 347010 | 347679 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_MO_IL | B1 | 1 | Quincy 345/138 Xfmr | NA | 347010 | 347080 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_MO_IL | B1 | 1 | Meredosia - Ipava 345 | 43 | 347688 | 347288 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_MO_IL | B1 | 1 | Meredosia - Pawnee 345 | 55 | 347688 | 347962 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_MO_IL | B1 | 1 | Meredosia 345/138 Xfmr | NA | 347688 | 347680 | 1 | Loading >100% of System Emergency | Loss of Montgomery - Spencer 345
MISO_W | B1 | 0 | Ellendale - Big Stone 345 | 145 | 661025 | 620313 | 1 | Interconnect New Generation | Wind Integration
MISO_W | B1 | 0 | Brookings County - Big Stone 345 | 100 | 601031 | 620313 | 1 | Interconnect New Generation | Wind Integration
MISO_WUMS | B1 | 1 | Green Bay-Morgan 345kV TL | 23 | 699553 | 699547 | 1 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Morgan-Plains 345kV TL #2 | 75 | 699547 | 699918 | 2 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Plains-National 345kV TL | 57 | 699918 | 699976 | 1 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | National 345/138kV XFMR #1 | NA | 699976 | 699892 | 1 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | National 345/138kV XFMR #1 | NA | 699976 | 699892 | 2 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Green Bay 345/138kV XFMR | NA | 699553 | 699052 | 1 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Green Bay-Morgan 138kV TL | 23 | 699052 | 699570 | 1 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Plains 345/138kV XFMR #2 | NA | 699918 | 699569 | 2 | Loading >100% of System Emergency | Overload of Pulliam-Stiles 138kV Non-convergence of Morgan-Plains 345kV contingency Non-convergence of Plains-Arnold 345kV contingency Non-convergence of Arnold-Dead River 345kV contingency Non-convergence of Dead River-Presque Isle 138kV contingency
MISO_WUMS | B1 | 1 | Barnhart-Cedarsauk 345-kV Uprate | 24.1 | 693607 | 699396 | 1 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV
MISO_WUMS | B1 | 1 | St Rita-Racine 138kV TL reconductor | 8.8 | 699481 | 699472 | 1 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV
MISO_WUMS | B1 | 1 | Oak Creek-St Rita 138kV TL reconductor | 5.4 | 699371 | 699481 | 1 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV
MISO_WUMS | B1 | 1 | Oak Creek-Racine 138kV TL reconductor | 13.1 | 699371 | 698868 | 1 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV
MISO_WUMS | B1 | 1 | Elm Rd-Racine 345kV TL #2 | 13 | 699367 | 699471 | 2 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Pleasant Prairie-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV
MISO_WUMS | B1 | 1 | Arcadian-Pleasant Prairie 345kV TL #2 (loop of Arcadian-Zion 345kV TL into Pleasant Prairie) | NA | 699247 | 699432 | 2 | Loading >100% of System Emergency | Overload of Elm Rd-Racine 345kV Overload of Pleasant Prairie-Racine 345kV Overload of Oak Creek-Racine 138kV Overload of Oak Creek-St Rita 138kV Overload of St Rita-Racine 138 kV Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Granville-Bluemound 345kV TL | 10 | 698871 | 694080 | 1 | Loading >100% of System Emergency | Overload of Granville 345/138 XFMR #3 Overload of Butler-Granville 138kV Overload of Granville-Tamarack Tap 138kV
MISO_WUMS | B1 | 1 | Bluemound 345/230kV XFMR | NA | 694080 | 698862 | 1 | Loading >100% of System Emergency | Overload of Granville 345/138 XFMR #3 Overload of Butler-Granville 138kV Overload of Granville-Tamarack Tap 138kV
MISO_WUMS | B1 | 1 | Oak Creek-Elm Rd 230-345kV XFMR Replacement | NA | 698857 | 699367 | 1 | Loading >100% of System Emergency | Overload of Oak Creek-Elm Rd 230-345kV XFMR
MISO_WUMS | B1 | 1 | Indian Lake-Hiawatha 138-kV TL (convert from 69kV to 138kV operation) | 41.2 | 699801 | 699765 | 1 | Loading >100% of System Emergency | Overload of Pleasant Prairie-Zion 345kV Overload of Pleasant Prairie-Zion EC 345kV Overload of Kenosha-Lakeview 138kV Overload of Lakeview-Zion 138kV
MISO_WUMS | B1 | 1 | Kenosha-Lakeview 138kV TL reconductor | 5 | 699345 | 699362 | 1 | Loading >100% of System Emergency | Overload of Pleasant Prairie-Zion 345kV Overload of Pleasant Prairie-Zion EC 345kV Overload of Kenosha-Lakeview 138kV Overload of Lakeview-Zion 138kV
MISO_WUMS | B1 | 1 | Lakeview-Zion 138kV TL reconductor | 4.8 | 699362 | 272896 | 1 | Loading >100% of System Emergency | Overload of Pleasant Prairie-Zion 345kV Overload of Pleasant Prairie-Zion EC 345kV Overload of Kenosha-Lakeview 138kV Overload of Lakeview-Zion 138kV
MISO_WUMS | B1 | 1 | Pleasant Prairie-Zion 345kV TL #2 Reconductor (loop of Arcadian-Zion 345kV TL into Pleasant Prairie) | NA | 699432 | 270942 | 2 | Loading >100% of System Emergency | Overload of Pleasant Prairie-Zion 345kV Overload of Pleasant Prairie-Zion EC 345kV Overload of Kenosha-Lakeview 138kV Overload of Lakeview-Zion 138kV
MISO_WUMS | B1 | 1 | Paris-Albers 138kV TL reconductor | 12.6 | 699410 | 699249 | 1 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Somers-Albers 138kV TL rebuild | 3.3 | 699499 | 699248 | 1 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Albers-Kenosha 138kV TL reconductor | 3.8 | 699249 | 699345 | 1 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Bain-Albers 138kV TL reconductor | 5.1 | 699259 | 699249 | 1 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Racine-Pleasant Prairie 345kV TL #2 | 13 | 698853 | 699432 | 2 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Racine-Somers 138kV TL rebuild | 4.3 | 699472 | 699499 | 1 | Loading >100% of System Emergency | Overload of Racine-Pleasant Prairie 345kV Overload of Albers-Kenosha 138kV Overload of Paris-Albers 138kV
MISO_WUMS | B1 | 1 | Branch River 345kV 8x50MVAR Reactors | NA | 693636 |  |  | High Voltage | Voltage at Pt Beach Nuclear exceeds IA level
New England ISO | B1 | 1 | Scobie - Tewksbury 345 kV TL |  | 104143 | 113951 | 1 | Loading >100% of System Emergency | Loss of the Seabrook - NU_394_SBK 345 kV TL - New Line
New England ISO | B1 | 1 | Tewksbury - Woburn 345 kV TL |  | 113951 | 110756 | 2 | Loading >100% of System Emergency | Loss of the Seabrook - NU_394_SBK 345 kV TL - New Line
New England ISO | B1 | 1 | Woburn - N. Cambridge 345 kV TL |  | 110756 | 110758 | 3 | Loading >100% of System Emergency | Loss of the Seabrook - NU_394_SBK 345 kV TL - New Line
New England ISO | B1 | 1 | Ward Hill - Wakefield JCT 345 kV TL |  | 113952 | 114476 | 1 | Loading >100% of System Emergency | Loss of the Seabrook - NU_394_SBK 345 kV TL - New Line
NYISO__A-F | B1 | 0 | Leeds - Pleasant Valley 345 kV |  | 137451 | 126296 | 3 | Loading >100% of System Emergency | L/O parrallel Leeds-Athens/Pleasant Valley Line(s)
NYISO__A-F | B1 | 3 | Packard - Sawyer 230 kV |  | 135415 | 135303 | 2 | Loading >100% of System Emergency | L/O parrallel Packard-Sawyer-Huntley Line
NYISO__A-F | B1 | 3 | Sawyer - Huntley 230 kV |  | 135303 | 135414 | 2 | Loading >100% of System Emergency | L/O parrallel Packard-Sawyer-Huntley Line
PJM_Eastern_MAAC | B1 | 1 | Essex - Kearny 4-6 230kV TL (terminal equip uprate) |  | 217079 | 217061 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1 | 1 | Peach Bottom - Conastone 230kV TL (terminal equip uprate) |  | 200013 | 200004 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1 | 1 | Peach Bottom - Cooper 230kV TL (terminal equip uprate) |  | 213869 | 214089 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1 | 1 | Cooper - Graceton 230kV TL (terminal equip uprate) |  | 214089 | 220964 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Eastern_MAAC | B1 | 1 | Kearny 4-6 - Kearny 1-3 230kV TL (terminal equip uprate) |  | 217061 | 217060 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | 2nd Dauphin - Juniata 230kV TL |  | 207955 | 208005 | 2 | Loading >100% of System Emergency | Loss of Cumberland - Juniata 230kV TL
PJM_Rest_of_MAAC | B1 | 1 | 2nd Cumberland - Juniata 230kV TL |  | 207950 | 208004 | 2 | Loading >100% of System Emergency | Loss of Dauphin - Juniata 230kV TL
PJM_Rest_of_MAAC | B1 | 1 | Brighton - Kemptown 500kV TL (PATH) |  | 200003 | 235632 | 1 | Loading >100% of System Emergency | PATH project to solve non-convergence issues due to voltage collapse around Bedington - Blackoak and Eastern Interfaces. It also solves thermal overloads in the seems between PJM_Rest_of_RTO and PJM_Rest_of_MAAC.
PJM_Rest_of_MAAC | B1 | 1 | Safe Harbor - Graceton 230kV TL (terminal equip uprate) |  | 208071 | 220964 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | North Temple - Lyons 230kV TL (terminal equip uprate) |  | 204508 | 204503 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Ironwood - South Lebanon 230kV TL (terminal equip uprate) |  | 204518 | 204511 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Otter Creek - Conastone 230kV TL (terminal equip uprate) |  | 208048 | 220963 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Dickerson - Station H - Dickerson 230kV TL (terminal equip uprate) |  | 223938 | 223937 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Glade - Forest 230kV TL (terminal equip uprate) |  | 200593 | 200581 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Altoona - Raystown 230kV TL (terminal equip uprate) |  | 200500 | 200517 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Raystown - Lewistown 2 230kV TL (terminal equip uprate) |  | 200517 | 200513 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | North Temple - North Kill 230kV TL (terminal equip uprate) |  | 204508 | 204875 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | North Temple - Hosensack-Ppl 230kV TL (terminal equip uprate) |  | 204508 | 207983 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Juniata - Juniata 230kV TL (terminal equip uprate) |  | 208005 | 208004 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Graceton - Bagley 230kV TL (terminal equip uprate) |  | 220964 | 221000 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | High Ridge - Howard 230kV TL (terminal equip. uprate) |  | 220941 | 220954 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Forest - Elko 230kV TL |  | 200581 | 235175 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Glade - Warren 230kV TL |  | 200593 | 200811 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Lewistown 2 - Juniata 230kV TL |  | 200513 | 208005 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Juniata - Cumberland 230kV TL |  | 208004 | 207950 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Hummerlstown - Steelton 230kV TL |  | 207990 | 208105 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Elimsport - Lycoming 230kV TL |  | 207968 | 207970 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | Re-conductor Middletown Junction - Brunner Island 230kV TL |  | 204504 | 207922 | 2 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | 2nd Three Mile Island 500/230kV XFMR |  | 200016 | 204514 | 3 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 2 | 2nd Juniata 500/230kV XFMR |  | 200009 | 208005 | 3 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_MAAC | B1 | 1 | Brighton - Kemptown 500kV TL (PATH) |  | 200003 | 235632 | 2 | Loading >100% of System Emergency
PJM_Rest_of_MAAC | B1 | 1 | Conastone - Kemptown 500kV TL (PATH) |  | 200004 | 235632 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 1 | Re-conductor Nelson - P20 345kv TL |  | 270730 | 294490 | 2 | Loading >100% of System Emergency | Loss of Byron - Lee County 345kV TL
PJM_Rest_of_RTO | B1 | 1 | Re-conductor Electric Junction - P20 345kV TL |  | 270828 | 294490 | 2 | Loading >100% of System Emergency | Loss of Byron - Lee County 345kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Taylor - West Loop 345kV TL |  | 270898 | 270922 | 2 | Loading >100% of System Emergency | Loss of Crawford - Goodings Grove 345kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Brambleton - Greenway 230kV TL |  | 314098 | 314171 | 2 | Loading >100% of System Emergency | Loss of Greenway - Brambleton 230kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Reynolds - Meadow Lake 345kV TL |  | 243230 | 243878 | 2 | Loading >100% of System Emergency | Loss of Jefferson - Rockport 765kV TL
PJM_Rest_of_RTO | B1 | 1 | Elmont - Hanover 230kV TL (terminal equip. uprate) |  | 314218 | 314222 | 1 | Loading >100% of System Emergency | Loss of Mine Rd - Ladysmith 230kV TL
PJM_Rest_of_RTO | B1 | 1 | Four Rivers - Hanover 230kV TL (terminal equip. uprate) |  | 314212 | 314222 | 1 | Loading >100% of System Emergency | Loss of Mine Road - Ladysmith 230kV TL
PJM_Rest_of_RTO | B1 | 1 | 2nd Clover 500/230kV XFMR |  | 314906 | 314686 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | 2nd Byron - Wemplton 345kV TL |  | 270679 | 270918 | 2 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Gainesville - Loudoun 230kV TL (terminal equip uprate) |  | 314037 | 314061 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Convoy - Robison Park 230kV TL (terminal equip uprate) |  | 242933 | 243231 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Ballston - Clarendon 230kV TL (terminal equip uprate) |  | 314820 | 314120 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Clarendon - Ballston 230kV TL (terminal equip uprate) |  | 314120 | 314820 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | T-94 - Benton Harbor 230kV TL (terminal equip uprate) |  | 292292 | 243212 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Covert - T-94 230kV TL (terminal equip uprate) |  | 256018 | 292290 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Charter Grove - Byron (Blue) 230kV TL |  | 270692 | 270678 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Charter Grove - Byron (Red) 230kV TL |  | 270693 | 270679 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Charter Grove - Wayne (Blue) 230kV TL |  | 270692 | 270916 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Charter Grove - Wayne (Red) 230kV TL |  | 270693 | 270917 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Charter Grove - Charter Grove 230kV TL |  | 270692 | 270693 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Wayne (Blue) - Wayne (Red) 230kV TL |  | 270916 | 270917 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Wayne (Blue) - Itasca (Blue) 230kV TL |  | 270916 | 270780 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Wayne (Red) - Itasca (Red) 230kV TL |  | 270917 | 270781 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Itasca (Blue) - Itasca (Red) 230kV TL |  | 270780 | 270781 | 1 | Interconnect New Generation | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | Re-conductor Nelson (Blue) - P20 345kV TL |  | 270828 | 294490 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | Re-conductor Electric Junction (Blue) - P20 345kV TL |  | 270730 | 294490 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | Re-conductor Elmont - Hanover 230kV TL |  | 314218 | 314222 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | Possum Point - Dumfries 230kV TL (terminal equip. uprate) |  | 314074 | 314029 | 1 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | 2nd T130 - R60 345kV TL |  | 292438 | 296566 | 2 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | 2nd East Lima - T130 345kV TL |  | 242935 | 292438 | 2 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 2 | Re-conductor Idylwood - Idylwood 230kV TL |  | 314052 | 314100 | 2 | Loading >100% of System Emergency | PJM Interconnection Analysis (Peak)
PJM_Rest_of_RTO | B1 | 1 | Doubs - Kemptown 500kV TL (PATH) |  | 235105 | 235632 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 1 | Meadow Brook - Welton Springs 500kV TL (PATH) |  | 235110 | 235637 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 1 | Welton Springs - Kemptown 765kV TL (PATH) |  | 235632 | 237045 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 1 | Welton Springs - John Amos 765kV TL (PATH) |  | 235634 | 242508 | 1 | Loading >100% of System Emergency
PJM_Rest_of_RTO | B1 | 1 | Welton Springs - Mt Storm 500kV TL (PATH) |  | 235637 | 314917 | 2 | Loading >100% of System Emergency
SOCO | B1 | 1 | Hopewell 230kV/115kV TL | NA | 380209 | 380363 | 1 | Loading >100% of System Emergency | Addition of McFrau Ford - Hopewell 230kV TL - Upgrade XFMR
SOCO | B1 | 1 | Chickasaw - Barry 230kV TL | 18 | 384638 | 384700 | 2 | Loading >100% of System Emergency | Loss of the Chickasaw - Barry 230kV TL #1 - New Line
SOCO | B1 | 1 | Klondike 500/230kV XFMR | NA | 381919 | 380073 | 2 | Loading >100% of System Emergency | Loss of the Klondike - Norcross 500kV TL - New XFMR
SOCO | B1 | 1 | Klondike - Minola Dr. 230kV TL | 7 | 380073 | 380072 | 1 | Loading >100% of System Emergency | Loss of the Klondike - Norcross 500kV TL - New XFMR
SOCO | B1 | 1 | Minola Dr. - Snapfinger 230kV TL | 2 | 380072 | 380071 | 1 | Loading >100% of System Emergency | Loss of the Klondike - Norcross 500kV TL - New XFMR
SOCO | B1 | 1 | Snapfinger - Austin Dr. 230kV TL | 3 | 380071 | 380070 | 1 | Loading >100% of System Emergency | Loss of the Klondike - Norcross 500kV TL - New XFMR
SOCO | B1 | 1 | McGrau Ford - Hopewell 230kV TL | 12 | 380088 | 380209 | 2 | Loading >100% of System Emergency | Loss of the Ocee - Marconi 230kV TL - New Line
SOCO | B1 | 1 | Ohara 500/230kV XFMR | NA | 380016 | 380171 | 2 | Loading >100% of System Emergency | Loss of the Ohara 500/230kV XFMR #1 - New XFMR
SOCO | B1 | 1 | Warrenton - Thomson 230kV TL | 17 | 380107 | 381413 | 1 | Loading >100% of System Emergency | Loss of the Rockville - Scherer 500kV TL - Upgrade Line
SOCO | B1 | 1 | Thomson 500/230kV XFMR | NA | 381413 | 381490 | 2 | Loading >100% of System Emergency | Loss of the Thomson 500/230 kV XFMR #1 - New XFMR
SOCO | B1 | 1 | Union 500/230kV XFMR | NA | 380005 | 380026 | 2 | Loading >100% of System Emergency | Loss of the Union 500/230 kV XFMR #1 - New XFMR
SOCO | B1 | 1 | Villa Rica 500/230kV XFMR | NA | 380022 | 380185 | 2 | Loading >100% of System Emergency | Loss of the Villa Rica 500/230 kV XFMR #1- New XFMR
SOCO | B1 | 1 | W. Brunswick - Thalmann 230kV TL | 8 | 380165 | 382592 | 2 | Loading >100% of System Emergency | Loss of the W. Brunswick - Thal LS 230kV TL - Reconductor Line
SOCO | B1 | 1 | W. Brunswick - Thalmann 230kV TL | 8 | 380165 | 382591 | 1 | Loading >100% of System Emergency | Loss of the W. Brunswick - Thalman 230kV TL #2 - Reconducotr Line
SOCO | B1 | 1 | Yates - Yellow Dirt 230kV TL | 15 | 380123 | 382480 | 2 | Loading >100% of System Emergency | Loss of the Yates - Yellow Dirt 230kV TL #1 - New Line
SPP_N | B1/B13 | 3 | Post Rock - Knoll 230kV | 1 | 530584 | 530558 | 2 | Loading >100% of System Emergency | Loss of Post Rock - Knoll 230kV #1 - New Line
SPP_N | B1/B13 | 3 | Post Rock - South Hayes | 11.3 | 530584 | 530582 | 2 | Loading >100% of System Emergency | Loss of Post Rock - South Hayes 230kV #1 - New Line
SPP_N | B1/B13 | 3 | Knoll - Smoky Hill 230kV | 62.3 | 530558 | 530592 | 1 | Loading >100% of System Emergency | reconductor
SPP_N | B1/B13 | 3 | Smoky Hill - Summit 230kV | 39.5 | 530592 | 532873 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Lebrock - Tenaska 345kV | 30 | 508572 | 508585 | 2 | Loading >100% of System Emergency | Loss of Lebrock - Tenaska 345kV #1 - New Line
SPP_S | B1 | 3 | Plant X - Tolk East 230kV | 10 | 525481 | 525524 | 3 | Loading >100% of System Emergency | Loss of Plant X - Tolk East 230kV #2 - New Line
SPP_S | B1 | 3 | Plant X - Tolk West 230kV | 9.7 | 525481 | 525531 | 2 | Loading >100% of System Emergency | Loss of Plant X - Tolk West 230kV #1 - New Line
SPP_S | B1/B13 | 3 | Potter - Cherry 230kV | 5.5 | 523959 | 524010 | 2 | Loading >100% of System Emergency | Loss of Potter - Cherry #1 230kV - New Line
SPP_S | B1/B13 | 3 | Potter - Harrington West 230kV | 11.3 | 523959 | 523977 | 3 | Loading >100% of System Emergency | Loss of Potter - Harrington West #2 230kV - New Line
SPP_S | B1/B13 | 3 | Carroll - Messick 230kV | 15.1 | 500140 | 500570 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Clarn - Messick 230kV | 13.5 | 500170 | 500570 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Potter - Bushland 230kV | 19 | 523959 | 524267 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Potter - Newhart 230kV | 68.3 | 523959 | 525461 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Harrington East - Cherry 230kV | 5.5 | 523979 | 524010 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Bushland - Deaf Smith 230kV | 30 | 524267 | 524623 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Newhart - Plant X 230kV | 36.4 | 525461 | 525481 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Plant X - Tolk West 230kV | 9.7 | 525481 | 525531 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Tolk East - Tuco 230kV | 54.3 | 525524 | 525830 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Tuco - Carlisle 230kV | 26.9 | 525830 | 526161 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Tuco - Jones 230kV | 29.7 | 525830 | 526337 | 2 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Tuco - Jones 230kV | 29.7 | 525830 | 526337 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Lubbock South - Jones | 5.4 | 526269 | 526337 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Lubbock South - Jones | 5.4 | 526269 | 526338 | 2 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Sundown - Amoco 230kV | 5.2 | 526435 | 526460 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Sundown - Wolfforth 230kV | 24.6 | 526435 | 526525 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Harrington West - Nichols 230kV | 1 | 523977 | 524044 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1/B13 | 3 | Harrington Midwest - Nichols 230kV | 1 | 523978 | 524044 | 2 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Madison - Mandeville 230kV | 10 | 500510 | 500520 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Grapevine - Nichols 230kV | 53.4 | 523771 | 524044 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Harrington West - Nichols 230kV | 1 | 523977 | 524044 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Harrington Midwest - Nichols 230kV | 1 | 523978 | 524044 | 2 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Oasis - SW 230kV | 9.7 | 524875 | 524915 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Roosevelt South - SW 230kV | 10 | 524911 | 524915 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Roosevelt South - Tolk East 230kV | 39.4 | 524911 | 525524 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Newhart - Plant X 230kV | 36.4 | 525461 | 525481 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 3 | Tolk West - Yoakum 230kV | 87.8 | 525531 | 526935 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 4 | Pirkey - Lebrock 345kV | 6.7 | 508563 | 508572 | 1 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 4 | Pirkey - Lebrock 345kV | 6.7 | 508563 | 508572 | 2 | Loading >100% of System Emergency | reconductor
SPP_S | B1 | 4 | Plant X - Sundown 230kV | 48.2 | 525481 | 526435 | 1 | Loading >100% of System Emergency | reconductor
VACAR | B1 | 3 | Morningstar - Oakboro 230 kV TL | 32 | 306145 | 306141 | 2 | Loading >100% of System Emergency | For loss of 500 kV line - install 2nd circuit
VACAR | B1 | 3 | Morningstar - Newport 230 kV TL | 34 | 306144 | 306141 | 1 | Loading >100% of System Emergency | For loss of 500 kV line - install 2nd circuit and bundle
VACAR | B1 | 3 | Morningstar - Newport 230 kV TL | 34 | 306144 | 306141 | 2 | Loading >100% of System Emergency | For loss of 500 kV line - install 2nd circuit and bundle
VACAR | B1 | 3 | Antioch 500/230 kV XFMR | N/A | 306100 | 306112 | 1 | Loading >100% of System Emergency | For loss of the parallel bank - increase capacity
VACAR | B1 | 3 | Antioch 500/230 kV XFMR | N/A | 306100 | 306112 | 2 | Loading >100% of System Emergency | For loss of the parallel bank - increase capacity
VACAR | B1 | 3 | Antioch - Mitchell River 230 kV TL | N/A | 306140 | 306112 | 1 | Loading >100% of System Emergency | For loss of the parallel line - breaker upgrade to increase rating
VACAR | B1 | 3 | Antioch - Mitchell River 230 kV TL | N/A | 306140 | 306112 | 2 | Loading >100% of System Emergency | For loss of the parallel line - breaker upgrade to increase rating
VACAR | B1 | 3 | Harrisburg - Oakboro 230 kV TL | N/A | 306130 | 306145 | 1 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1 | 3 | Harrisburg - Oakboro 230 kV TL | N/A | 306130 | 306145 | 2 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1 | 3 | Allen - Woodlawn 230 kV TL | N/A | 306110 | 306164 | 1 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1 | 3 | Allen - Woodlawn 230 kV TL | N/A | 306139 | 306154 | 2 | Loading >100% of System Emergency | For loss of the parallel line - install reactor
VACAR | B1 | 0 | LNS2-Newport 500 kV TL | 28 | 306104 | 309601 | 1 | Interconnect New Generation
VACAR | B1 | 0 | LNS2-Oconee 500 kV TL | 86 | 306105 | 309601 | 1 | Interconnect New Generation
VACAR | B1 | 0 | LNS1-Catawba 230 kV TL | 29 | 306121 | 309600 | 1 | Interconnect New Generation
VACAR | B1 | 0 | LNS1-Catawba 230 kV TL | 29 | 306121 | 309600 | 2 | Interconnect New Generation
VACAR | B1 | 0 | LNS1-Pacolet 230 kV TL | 22 | 306147 | 309600 | 1 | Interconnect New Generation
VACAR | B1 | 0 | LNS1-Pacolet 230 kV TL | 22 | 306147 | 309600 | 2 | Interconnect New Generation
VACAR | B1 | 0 | Wake-Wommack 500kV TL |  | 304183 | 305998 | 1 | Interconnect New Generation
VACAR | B1 | 0 | Harris#3-Wake 230kV TL |  | 304190 | 305997 | 1 | Interconnect New Generation
VACAR | B1 | 0 | Harris#3-Erwin 230kV TL |  | 304196 | 305997 | 1 | Interconnect New Generation
VACAR | B1 | 0 | Cumberland-Wommack 500kV TL |  | 304391 | 305998 | 1 | Interconnect New Generation
VACAR | B1 | 0 | Harris#3-FtBrWoodruff 230kV TL |  | 304398 | 305997 | 1 | Interconnect New Generation
VACAR | B1 | 0 | New Bern 500/230kV XFMR |  | 304465 | 305999 | 1 | Interconnect New Generation
VACAR | B1 | 0 | New Bern 500/230kV XFMR |  | 304465 | 305999 | 2 | Interconnect New Generation
VACAR | B1 | 0 | New Bern-Wommack 500kV TL |  | 305998 | 305999 | 1 | Interconnect New Generation
VACAR | B1 | 0 | New Bern-Wommack 500kV TL |  | 305998 | 305999 | 2 | Interconnect New Generation

## do not edit (hidden)
Reason | Region | Load Block | Pass
Interconnect New Generation | ENTERGY | B1 | 0
Loading >100% of System Normal | FRCC | B13 | 1
Loading >100% of System Emergency | IESO | B1/B13 | 2
Low Voltage | MAPP_CA |  | 3
High Voltage | MAPP_US |  | 4
| MISO_IN |  | 5
| MISO_MI |  | 6
| MISO_MO_IL |  | 7
| MISO_W |  | 8
| MISO_WUMS |  | 9
| Nebraska |  | 10
| New England ISO |  | 11
| Non_RTO_Midwest |  | 12
| NYISO__A-F |  | 13
| NYISO_GHI |  | 14
| NYISO_J_&_K |  | 15
| PJM_Eastern_MAAC |  | 16
| PJM_Rest_of_MAAC |  | 17
| PJM_Rest_of_RTO |  | 18
| SOCO |  | 19
| SPP_N |  | 20
| SPP_S |  | 21
| TVA |  | 22
| VACAR |  | 23
| EIPC |  | 24
25