## Component Estimates
Future 2 OL 75 Total Cost: |  | 34122876200 | 48799582300
Future | Transfer Limit Increase |  |  | Transmission Building Blocks | [7 empty] | Multiplier range |  | Cost range
Scenario | Region1 | Region2 | Transfer Limit Increase (MW) | Termination 1 | Termination 2 or Device Description | Voltage (kV) | # of Circuits | Capability (MW) | Length (Miles) | Generic Per Unit Cost | Upgrade Region | Low Mult. | High Mult. | Cost Low | Cost High | Notes
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Mitchell Co | Hampton Corner | 765 | 1 | 4000 | 92 | 5550000 | MISO_W | 0.5 | 0.6 | 255300000 | 306360000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | New MN 765 Sub 1 | New MN 765 Sub 2 | 765 | 1 | 4000 | 26 | 5550000 | MISO_W | 0.5 | 0.6 | 72150000 | 86580000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Brookings County | New MN 765 Sub 2 | 765 | 1 | 4000 | 20 | 5550000 | MISO_W | 0.5 | 0.6 | 55500000 | 66600000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Brookings County | Hampton Corner | 765 | 1 | 4000 | 211 | 5550000 | MISO_W | 0.5 | 0.6 | 585525000 | 702630000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Grimes | Hills | 765 | 1 | 4000 | 141 | 5550000 | MISO_W | 0.5 | 0.6 | 391275000 | 469530000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | IA-G Station | Grimes | 765 | 1 | 4000 | 105 | 5550000 | MISO_W | 0.5 | 0.6 | 291375000 | 349650000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Lakefield Junction | New MN 765 Sub 1 | 765 | 1 | 4000 | 58 | 5550000 | MISO_W | 0.5 | 0.6 | 160950000 | 193140000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Lakefield Junction | IA-G Station | 765 | 1 | 4000 | 109 | 5550000 | MISO_W | 0.5 | 0.6 | 302475000 | 362970000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Mitchell Co | Hills | 765 | 1 | 4000 | 179 | 5550000 | MISO_W | 0.5 | 0.6 | 496725000 | 596070000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Mitchell Co | North La Crosse | 765 | 1 | 4000 | 89 | 5550000 | MISO_W | 0.5 | 0.6 | 246975000 | 296370000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Quad Cities | Hills | 765 | 1 | 4000 | 77 | 5550000 | MISO_W | 0.5 | 0.6 | 213675000 | 256410000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | North La Crosse | North Madison | 765 | 1 | 4000 | 119 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 396270000 | 462315000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | North Madison | Darlington | 765 | 1 | 4000 | 65 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 216450000 | 252525000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Montgomery | St. Francois | 765 | 1 | 4000 | 104 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 288600000 | 346320000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Fairport | Montgomery | 765 | 1 | 4000 | 205 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 568875000 | 682650000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Fairport | Grimes | 765 | 1 | 4000 | 141 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 391275000 | 469530000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Reynolds | Greentown | 765 | 1 | 4000 | 66 | 5550000 | MISO_IN | 0.5 | 0.7 | 183150000 | 256410000 | MISO Cand MVP Portolio 1
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | MISO Regional Generator Outlet Study 345 lines |  | 345 | 1 | 1800 | 2124 | 2500000 | MISO | 0.4 | 0.8 | 2124000000 | 4248000000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Montgomery | PA change (Don Marquis) | 765 | 1 | 4000 | 248 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 688200000 | 825840000
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | PA change (Montgomery) | Don Marquis | 765 | 1 | 4000 | 250 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1110000000 | 1248750000 | $62.3 mil sub/xfmr cost
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | St Francois | Rockport | 765 | 1 | 4000 | 187 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 518925000 | 622710000 | MISO RGOS 765 overlay
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Rockport | Baker | 765 | 1 | 4000 | 223 | 5550000 | PJM_ROR | 0.8 | 0.9 | 990120000 | 1113885000
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Darlington | PA change (Dumont/Marysville tap) | 765 | 1 | 4000 | 40 | 5550000 | MISO_W | 0.5 | 0.6 | 111000000 | 133200000
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | PA change (Darlington) | Dumont/Marysville tap | 765 | 1 | 4000 | 365 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1620600000 | 1823175000 | $333.5 mil sub/xfmr cost
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | Quad Cities | PA change (Marysville/Flatlick tap) | 765 | 1 | 4000 | 84 | 5550000 | MISO_W | 0.5 | 0.6 | 233100000 | 279720000
Future 2 OL 75 | MISO_W | PJM_ROR | 12420 | PA change (Quad Cities) | Marysville/Flatlick tap | 765 | 1 | 4000 | 354 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1571760000 | 1768230000 | $106.3 mil sub/xfmr cost
[12 empty] | Total Cost: |  | 14084250000 | 18219570000
Future 2 OL 75 | MISO_IN | MISO_MI | 768 | Hiple | IN/MI border | 345 | 1 | 900 | 30 | 2100000 | MISO_IN | 0.5 | 0.8 | 31500000 | 50400000 | circuit 1
Future 2 OL 75 | MISO_IN | MISO_MI | 768 | IN/MI border | Battle Creek | 345 | 1 | 900 | 45 | 2100000 | MISO_MI | 0.5 | 0.7 | 47250000 | 66150000 | circuit 1
Future 2 OL 75 | MISO_IN | MISO_MI | 768 | Hiple | IN/MI border | 345 | 1 | 900 | 30 | 2100000 | MISO_IN | 0.5 | 0.8 | 31500000 | 50400000 | circuit 2
Future 2 OL 75 | MISO_IN | MISO_MI | 768 | IN/MI border | Battle Creek | 345 | 1 | 900 | 45 | 2100000 | MISO_MI | 0.5 | 0.7 | 47250000 | 66150000 | circuit 2
[12 empty] | Total Cost: |  | 157500000 | 233100000
Future 2 OL 75 | IESO | MISO_MI | 751 | Longwood | Lambton | 230 | 2 | 1200 | 50 | 1800000 | IESO | 0.8 | 1.4 | 72000000 | 126000000 | line 1
Future 2 OL 75 | IESO | MISO_MI | 751 | Longwood | Lambton | 230 | 2 | 1200 | 50 | 1800000 | IESO | 0.8 | 1.4 | 72000000 | 126000000 | line 1 N-1 backup
Future 2 OL 75 | IESO | MISO_MI | 751 | Lambton | PAR | 230/345 | 1 | 750 | 1 | 20000000 | IESO | 0.8 | 1.4 | 16000000 | 28000000 | Phase Angle Regulator
Future 2 OL 75 | IESO | MISO_MI | 751 | Lambton | PAR | 230/345 | 1 | 750 | 1 | 20000000 | IESO | 0.8 | 1.4 | 16000000 | 28000000 | Phase Angle Regulator N-1 backup
Future 2 OL 75 | IESO | MISO_MI | 751 | Lambton | St Clair | 345 | 1 | 900 | 4 | 2100000 | IESO | 0.8 | 1.4 | 6720000 | 11760000 | Tie Line IESO-MISO_MI
Future 2 OL 75 | IESO | MISO_MI | 751 | Lambton | St Clair | 345 | 1 | 900 | 4 | 2100000 | MISO_MI | 0.5 | 0.7 | 4200000 | 5880000 | Tie Line IESO-MISO_MI N-1 backup
[12 empty] | Total Cost: |  | 186920000 | 325640000
Future 2 OL 75 | IESO | MISO_W | 67 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | IESO | 0.8 | 1.9 | 92000000 | 218500000 | line 1
Future 2 OL 75 | IESO | MISO_W | 67 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | MISO_W | 0.8 | 1.9 | 92000000 | 218500000 | line 1 N-1 backup
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer N-1 backup
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | IESO | 0.8 | 1.4 | 880000 | 1540000 | Tie Line IESO-MISO_W
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | MISO_W | 0.5 | 1.6 | 550000 | 1760000 | Tie Line IESO-MISO_W N-1 backup
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator
Future 2 OL 75 | IESO | MISO_W | 67 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator N-1 backup
[12 empty] | Total Cost: |  | 192630000 | 452900000
Future 2 OL 75 | MISO_MO-IL | SPP_N | 2019 | Iatan | Fairport | 765 | 1 | 4000 | 72 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 199800000 | 239760000 | N-1 backup for NE to MISO_W
[12 empty] | Total Cost: |  | 199800000 | 239760000
Future 2 OL 75 | MISO_W | NE | 2489 | Nebraska Sta. A | Iowa Sta. A | 765 | 1 | 4000 | 79 | 5550000 | SPP_N | 0.4 | 0.8 | 175380000 | 350760000 | NSA to state line. Satisfies N-1 condition for SPP_N to MISO MO_IL
Future 2 OL 75 | MISO_W | NE | 2489 | Nebraska Sta. A | Transformation | 765/345 | 1 |  | 1 | 53000000 | NE | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Substation
Future 2 OL 75 | MISO_W | NE | 2489 | Nebraska Sub A | Iowa Sub G | 765 | 1 | 4000 | 65 | 5550000 | MISO_W | 0.5 | 0.6 | 180375000 | 216450000 | N-1 backup for SPP_N to MISO_MO-IL
[12 empty] | Total Cost: |  | 403455000 | 646710000
Future 2 OL 75 | Entergy | SoCo | 1900 | McAdams | South Bessemer | 230 | 2 | 1200 | 40 | 1800000 | Entergy | 0.9 | 1.7 | 64800000 | 122400000 | Tie Line - Entergy/SoCo
Future 2 OL 75 | Entergy | SoCo | 1900 | McAdams | South Bessemer | 230 | 2 | 1200 | 120 | 1800000 | SoCo | 0.7 | 1.3 | 151200000 | 280800000 | Tie Line - Entergy/SoCo
Future 2 OL 75 | Entergy | SoCo | 1900 | Batesville | Miller | 230 | 2 | 1200 | 56 | 1800000 | Entergy | 0.9 | 1.7 | 90720000 | 171360000 | Tie Line - Entergy/SoCo
Future 2 OL 75 | Entergy | SoCo | 1900 | Batesville | Miller | 230 | 2 | 1200 | 124 | 1800000 | SoCo | 0.7 | 1.3 | 156240000 | 290160000 | Tie Line - Entergy/SoCo
Future 2 OL 75 | Entergy | SoCo | 1900 | Bogalusa | Big Creek | 230 | 1 | 900 | 5 | 1580000 | Entergy | 0.9 | 1.7 | 7110000 | 13430000 | Tie Line - Entergy/SoCo
Future 2 OL 75 | Entergy | SoCo | 1900 | Bogalusa | Big Creek | 230 | 1 | 900 | 95 | 1580000 | SoCo | 0.5 | 0.9 | 75050000 | 135090000 | Tie Line - Entergy/SoCo
[12 empty] | Total Cost: |  | 545120000 | 1013240000
Future 2 OL 75 | NYISO_A-F | NYISO_GHI | 1435 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 2 OL 75 | NYISO_A-F | NYISO_GHI | 1435 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 2 OL 75 | NYISO_A-F | NYISO_GHI | 1435 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 2 OL 75 | NYISO_A-F | NYISO_GHI | 1435 | Leeds |  | 345 | 3 |  |  |  | NYISO_A-F |  |  | 9000000 | 27000000 | Line terminal addition
Future 2 OL 75 | NYISO_A-F | NYISO_GHI | 1435 | Pleasant Valley |  | 345 | 3 |  |  |  | NYISO_GHI |  |  | 9000000 | 27000000 | Line terminal addition
[12 empty] | Total Cost: |  | 446400000 | 658800000
Future 2 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Roseland | Linden | 230 | 1 | 600 | 20 | 1150000 | PJM_Eastern_MAAC | 4 | 4.7 | 92000000 | 108100000
Future 2 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Goethals | Linden | 230 | [7 empty] | 0 | 0 | Allow VFT flow from NY to PJM
[12 empty] | Total Cost: |  | 92000000 | 108100000
Future 2 OL 75 | NEISO | NYISO_J_&_K | 315 | Pleasant Valley | NE Border | 345 | 1 | 900 | 17.8 | 2100000 | NYISO_GHI | 1.7 | 4.3 | 63546000 | 160734000 | NEISO-NYISO_GHI tie; relieves contingency constraint on NNC
Future 2 OL 75 | NEISO | NYISO_J_&_K | 315 | Long Mountain | NY Border | 345 | 1 | 900 | 5.6 | 2100000 | NEISO | 1.4 | 2.9 | 16464000 | 34104000 | Tie Line NEISO - NYISO_GHI
Future 2 OL 75 | NEISO | NYISO_J_&_K | 315 | Norwalk | Norwalk Harbor | 115 | 1 | 300 | 6.67 | 1100000 | NEISO | 1.8 | 2.7 | 25076200 | 30214300 | Some underground - 1.48 mi
Future 2 OL 75 | NEISO | NYISO_J_&_K | 315 | Pleasant Valley |  | 345 | 1 | [6 empty] | 3000000 | 9000000 | Line terminal addition
[12 empty] | Total Cost: |  | 108086200 | 234052300
Future 2 OL 75 | MISO_WUMS | MISO_MI | 688 | Point Beach | Ludington | HVDC SC | 2 | 2400 | 65 | 7500000 | MISO_WUMS | 0.7 | 1.1 | 341250000 | 536250000 | Submarine Cable
Future 2 OL 75 | MISO_WUMS | MISO_MI | 688 | Point Beach | (DC Terminal) | HVDC |  | 1200 | 1 | 170000000 | MISO_WUMS | 1 | 1 | 170000000 | 170000000
Future 2 OL 75 | MISO_WUMS | MISO_MI | 688 | Ludington | (DC Terminal) | HVDC |  | 1200 | 1 | 170000000 | MISO_MI | 1 | 1 | 170000000 | 170000000
[12 empty] | Total Cost: |  | 681250000 | 876250000
Future 2 OL 75 | MISO_WUMS | MISO_W | 38 | Saratoga | Petenwell | 138 | 1 | 300 | 16 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 8800000 | 28160000 | Rebuild of existing line
Future 2 OL 75 | MISO_WUMS | MISO_W | 38 | Kilbourn | Council Creek | 138 | 1 | 300 | 50 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 27500000 | 88000000 | 69kV ROW exists
[12 empty] | Total Cost: |  | 36300000 | 116160000
Future 2 OL 75 | SPP_N | Entergy | 13843 | Sooner | Fort Smith | 765 | 1 | 4000 | 185 | 5550000 | SPP_N | 0.4 | 0.8 | 410700000 | 821400000 | Fort Smith is terminal for Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Fort Smith | Transformation | 765/500 | 0 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie Point Substation
Future 2 OL 76 | SPP_N | Entergy | 13843 | Fort Smith | Sabine | 500 | 1 | 2600 | 380 | 3450000 | Entergy | 0.7 | 1.4 | 917700000 | 1835400000 | 500 kV tie line into Entergy Region
Future 2 OL 76 | SPP_N | Entergy | 13843 | Sabine | Transformation | 500/230 |  |  | 2 | 25000000 | Entergy | 0.9 | 1.5 | 45000000 | 75000000 | Tie into Sabine area
Future 2 OL 76 | SPP_N | Entergy | 13843 | Flint Creek | Fort Smith | 500 | 1 | 2600 | 70 | 3450000 | Entergy | 0.7 | 1.4 | 169050000 | 338100000 | Back up for N-1 loss of 765 source
Future 2 OL 75 | SPP_N | Entergy | 13843 | Rose Hill | Flint Creek | 765 | 1 | 4000 | 178 | 5550000 | SPP_N | 0.4 | 0.8 | 395160000 | 790320000 | Flint Crk. Is terminal for Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Flint Creek | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie PointSubstation
Future 2 OL 75 | SPP_N | Entergy | 13843 | Flint Creek | McKnight | 500 | 1 | 2600 | 450 | 3450000 | Entergy | 0.7 | 1.4 | 1086750000 | 2173500000 | 500 kV tie line into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Flint Creek | Nelson | 500 | 1 | 2600 | 420 | 3450000 | Entergy | 0.7 | 1.4 | 1014300000 | 2028600000 | 500 kV tie line into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Flint Creek | Morgan | 500 | 1 | 2600 | 125 | 3450000 | Entergy | 0.7 | 1.4 | 301875000 | 603750000 | Back up for N-1 loss of 765 source
Future 2 OL 75 | SPP_N | Entergy | 13843 | Summit | Lang | 765 | 1 | 4000 | 84 | 5550000 | SPP_N | 0.4 | 0.8 | 186480000 | 372960000 | Satisfies SPP internal requirment
Future 2 OL 75 | SPP_N | Entergy | 13843 | Summit | Transformation | 765/345kV | 1 |  | 1 | 25000000 | SPP_N | 0.9 | 1.5 | 22500000 | 37500000 | 765/345kV Sub
Future 2 OL 75 | SPP_N | Entergy | 13843 | Lang | Transmission Sub | 765 | 1 |  | 1 | 25000000 | SPP_N | 0.9 | 1.5 | 22500000 | 37500000 | 765kV Transmission Sub
Future 2 OL 75 | SPP_N | Entergy | 13843 | Lang | LaCygne | 765 | 1 | 4000 | 84 | 5550000 | SPP_N | 0.4 | 0.8 | 186480000 | 372960000 | Satisfies N-1 condition. Lacygna is terminal for Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | LaCygne | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie Point Substation
Future 2 OL 75 | SPP_N | Entergy | 13843 | LaCygne | ISES | 500 | 1 | 2600 | 270 | 3450000 | Entergy | 0.7 | 1.4 | 652050000 | 1304100000 | 500 kV tie line into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | LaCygne | Transformation | 500/345 | 1 |  | 2 | 22000000 | Entergy | 0.9 | 1.5 | 39600000 | 66000000 | 500/345 kV Substation
Future 2 OL 75 | SPP_N | Entergy | 13843 | LaCygne | Franks | 345 | 1 | 1800 | 150 | 2500000 | Entergy | 1 | 1.9 | 375000000 | 712500000 | 345 kV tie into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | LaCygne | Sibley | 345 | 1 | 1800 | 80 | 2500000 | Entergy | 1 | 1.9 | 200000000 | 380000000 | Back up for N-1 loss of 765 source
Future 2 OL 75 | SPP_N | Entergy | 13843 | Lang | Morgan | 765 | 1 | 4000 | 168 | 5550000 | SPP_N | 0.4 | 0.8 | 372960000 | 745920000 | Morgan is terminal for Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Morgan | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie Point Substation
Future 2 OL 75 | SPP_N | Entergy | 13843 | Morgan | White Bluff | 500 | 1 | 2600 | 250 | 3450000 | Entergy | 0.7 | 1.4 | 603750000 | 1207500000 | 500 kV tie line into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Morgan | LaCygne | 500 | 1 | 2600 | 100 | 3450000 | Entergy | 0.7 | 1.4 | 241500000 | 483000000 | Back up for N-1 loss of 765 source
Future 2 OL 75 | SPP_N | Entergy | 13843 | Iatan | Sibley | 765 | 1 | 4000 | 49 | 5550000 | SPP_N | 0.4 | 0.8 | 108780000 | 217560000 | Sibley is terminal for EES/AECI
Future 2 OL 75 | SPP_N | Entergy | 13843 | Sibley | Transformation | 765/345 | 1 |  | 1 | 25000000 | SPP_N | 0.9 | 1.5 | 22500000 | 37500000 | 765/345 kV Tie Point Substation
Future 2 OL 75 | SPP_N | Entergy | 13843 | Sibley | Franks | 345 | 1 | 1800 | 170 | 2500000 | Entergy | 1 | 1.9 | 425000000 | 807500000 | 345 kV tie into Entergy Region
Future 2 OL 75 | SPP_N | Entergy | 13843 | Rose Hill | Lang | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
Future 2 OL 75 | SPP_N | Entergy | 13843 | Lang | Iatan | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
[12 empty] | Total Cost: |  | 8412235000 | 16610170000
Future 2 OL 75 | SPP-S | Entergy | 1992 | Crockett | Lewis Creek | 345 | 1 | 1800 | 21 | 2500000 | SPP-S | 0.4 | 0.8 | 21000000 | 42000000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Crockett | Lewis Creek | 345 | 1 | 1800 | 49 | 2500000 | Entergy | 1 | 1.9 | 122500000 | 232750000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Lewis Creek | Transformer | 345-230 | 2 |  | 2 | 20000000 | Entergy | 0.9 | 1.5 | 36000000 | 60000000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Turk | McNeil | 345 | 1 | 1800 | 25 | 2500000 | SPP-S | 0.4 | 0.8 | 25000000 | 50000000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Turk | McNeil | 345 | 1 | 1800 | 25 | 2500000 | Entergy | 1 | 1.9 | 62500000 | 118750000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | McNeil | Transformer | 500-345 | 2 |  | 2 | 25000000 | Entergy | 0.9 | 1.5 | 45000000 | 75000000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Dolet Hills | Sterlington | 345 | 1 | 900 | 16 | 2100000 | SPP-S | 0.5 | 1 | 16800000 | 33600000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Dolet Hills | Sterlington | 345 | 1 | 900 | 94 | 2100000 | Entergy | 1.2 | 2.2 | 236880000 | 434280000 | Tie Line - SPP-S/Entergy
Future 2 OL 75 | SPP-S | Entergy | 1992 | Sterlington | Transformer | 500-345 | 1 | 900 | 1 | 12500000 | Entergy | 0.9 | 1.5 | 11250000 | 18750000 | Tie Line - SPP-S/Entergy
[12 empty] | Total Cost: |  | 576930000 | 1065130000
Future 2 OL 75 | SPP |  |  | SPP 765kV Overlay |  | 765 |  |  | 1 | 8000000000 | SPP | 1 | 1 | 8000000000 | 8000000000 | This overlay is required to source the pipes for the future 2 xfer requirements