## Component Estimates
Future 5 OL 75 Total Cost: |  | 39191496200 | 58332337300
Future | Transfer Limit Increase |  |  | Transmission Building Blocks | [7 empty] | Multiplier range |  | Cost range
Scenario | Region1 | Region2 | Transfer Limit Increase (MW) | Termination 1 | Termination 2 or Device Description | Voltage (kV) | # of Circuits | Capability (MW) | Length (Miles) | Generic Per Unit Cost | Upgrade Region | Low Mult. | High Mult. | Cost Low | Cost High | Notes
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Mitchell Co | Hampton Corner | 765 | 1 | 4000 | 92 | 5550000 | MISO_W | 0.5 | 0.6 | 255300000 | 306360000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Mitchell Co | North La Crosse | 765 | 1 | 4000 | 89 | 5550000 | MISO_W | 0.5 | 0.6 | 246975000 | 296370000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Quad Cities | Hills | 765 | 1 | 4000 | 77 | 5550000 | MISO_W | 0.5 | 0.6 | 213675000 | 256410000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | North La Crosse | North Madison | 765 | 1 | 4000 | 119 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 396270000 | 462315000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | North Madison | Darlington | 765 | 1 | 4000 | 65 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 216450000 | 252525000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Pawnee | Breed | 345 | 1 | 1800 | 105 | 2500000 | MISO_MO_IL | 0.3 | 0.6 | 78750000 | 157500000
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Rockport | Baker | 765 | 1 | 4000 | 223 | 5550000 | PJM_ROR | 0.8 | 0.9 | 990120000 | 1113885000
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Darlington | PA change (Dumont/Marysville tap) | 765 | 1 | 4000 | 40 | 5550000 | MISO_W | 0.5 | 0.6 | 111000000 | 133200000
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | PA change (Darlington) | Dumont/Marysville tap | 765 | 1 | 4000 | 365 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1620600000 | 1823175000 | $333.5 mil sub/xfmr cost
Future 5 OL 75 | MISO_W | PJM_ROR | 9362 | Powerton | Marysville/Flatlick tap | 765 | 1 | 4000 | 354 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1571760000 | 1768230000 | $106.3 mil sub/xfmr cost
[12 empty] | Total Cost: |  | 5700900000 | 6569970000
Future 5 OL 75 | MISO_IN | MISO_MO_IL | 4129 | Fairport | Powerton | 765 | 1 | 4000 | 308 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 854700000 | 1025640000 | Ckt 1
Future 5 OL 75 | MISO_IN | MISO_MO_IL | 4129 | Powerton | New Reynolds | 765 | 1 | 4000 | 158 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 438450000 | 526140000 | Ckt 1
Future 5 OL 75 | MISO_IN | MISO_MO_IL | 4129 | New Reynolds | Greentown | 765 | 1 | 4000 | 66 | 5550000 | MISO_IN | 0.5 | 0.7 | 183150000 | 256410000 | Ckt 1. MISO Cand MVP Portolio 1
Future 5 OL 75 | MISO_IN | MISO_MO_IL | 4129 | St Francois | Rockport | 765 | 1 | 4000 | 187 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 518925000 | 622710000 | Ckt 2. MISO RGOS 765 overlay
[12 empty] | Total Cost: |  | 1995225000 | 2430900000
Future 5 OL 75 | MISO_W | MISO_MO_IL | 4073 | Grimes | Fairport | 765 | 1 | 4000 | 141 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 391275000 | 469530000 | Ckt 1. MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | MISO_MO_IL | 4073 | Fairport | Montgomery | 765 | 1 | 4000 | 205 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 568875000 | 682650000 | Ckt 1. MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | MISO_MO_IL | 4073 | Montgomery | St. Francois | 765 | 1 | 4000 | 104 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 288600000 | 346320000 | Ckt 1. MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | MISO_MO_IL | 4073 | Quad Cities | Powerton | 765 | 1 | 4000 | 84 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 233100000 | 279720000 | Ckt 2
Future 5 OL 75 | MISO_W | MISO_MO_IL | 4073 | Powerton | Montgomery | 765 | 1 | 4000 | 185 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 513375000 | 616050000 | Ckt 2
[12 empty] | Total Cost: |  | 1995225000 | 2394270000
Future 5 OL 75 | IESO | MISO_W | 74 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | IESO | 0.8 | 1.9 | 92000000 | 218500000 | line 1
Future 5 OL 75 | IESO | MISO_W | 74 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | MISO_W | 0.8 | 1.9 | 92000000 | 218500000 | line 1 N-1 backup
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer N-1 backup
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | IESO | 0.8 | 1.4 | 880000 | 1540000 | Tie Line IESO-MISO_W
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | MISO_W | 0.5 | 1.6 | 550000 | 1760000 | Tie Line IESO-MISO_W N-1 backup
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator
Future 5 OL 75 | IESO | MISO_W | 74 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator N-1 backup
[12 empty] | Total Cost: |  | 192630000 | 452900000
Future 5 OL 75 | MISO_W | SPP_N | 263 | [10 empty] | 0 | 0 | Covered by MISO_W to NE plans
[12 empty] | Total Cost: |  | 0 | 0
Future 5 OL 75 | MISO_IN | MISO_MI | 81 | [10 empty] | 0 | 0 | Covered by existing plans
[12 empty] | Total Cost: |  | 0 | 0
Future 5 OL 75 | MISO_W | NE | 17497 | New MN 765 Sub 1 | New MN 765 Sub 2 | 765 | 1 | 4000 | 26 | 5550000 | MISO_W | 0.5 | 0.6 | 72150000 | 86580000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Brookings County | New MN 765 Sub 2 | 765 | 1 | 4000 | 20 | 5550000 | MISO_W | 0.5 | 0.6 | 55500000 | 66600000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Brookings County | Hampton Corner | 765 | 1 | 4000 | 211 | 5550000 | MISO_W | 0.5 | 0.6 | 585525000 | 702630000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Grimes | Hills | 765 | 1 | 4000 | 141 | 5550000 | MISO_W | 0.5 | 0.6 | 391275000 | 469530000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | IA-G Station | Grimes | 765 | 1 | 4000 | 105 | 5550000 | MISO_W | 0.5 | 0.6 | 291375000 | 349650000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Lakefield Junction | New MN 765 Sub 1 | 765 | 1 | 4000 | 58 | 5550000 | MISO_W | 0.5 | 0.6 | 160950000 | 193140000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Lakefield Junction | IA-G Station | 765 | 1 | 4000 | 109 | 5550000 | MISO_W | 0.5 | 0.6 | 302475000 | 362970000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Mitchell Co | Hills | 765 | 1 | 4000 | 179 | 5550000 | MISO_W | 0.5 | 0.6 | 496725000 | 596070000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | MISO Regional Generator Outlet Study 345 lines |  | 345 | 1 | 1800 | 2124 | 2500000 | MISO | 0.4 | 0.8 | 2124000000 | 4248000000 | MISO RGOS 765 overlay
Future 5 OL 75 | MISO_W | NE | 17497 | Holt County | White (Brookings Co) | 765 | 1 | 4000 | 217 | 5550000 | MISO_W | 0.5 | 0.6 | 602175000 | 722610000 | Tie 1
Future 5 OL 75 | MISO_W | NE | 17497 | Sheldon (PA change) | Fairport | 765 | 1 | 4000 | 87 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 241425000 | 289710000 | Tie 2. MISO portion
Future 5 OL 75 | MISO_W | NE | 17497 | Cass County | Grimes | 765 | 1 | 4000 | 163 | 5550000 | MISO_W | 0.5 | 0.6 | 452325000 | 542790000 | Tie 3
Future 5 OL 75 | MISO_W | NE | 17497 | Iatan | Montgomery | 765 | 1 | 4000 | 216 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 599400000 | 719280000 | Tie 4
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. A | IA-G Station | 765 | 1 | 4000 | 65 | 5550000 | MISO_W | 0.5 | 0.6 | 180375000 | 216450000 | Tie 5. MISO portion
Future 5 OL 75 | MISO_W | NE | 17497 | Axtell | Sheldon Sta. | 765 | 1 | 4000 | 130 | 5550000 | SPP_N | 0.4 | 0.8 | 288600000 | 577200000 | Satisfies SPP internal requirment
Future 5 OL 75 | MISO_W | NE | 17497 | Sheldon Sta | Transformation | 765/345kV | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Sub
Future 5 OL 75 | MISO_W | NE | 17497 | Sheldon Sta | SPP/MISO Line | 765 | 1 | 4000 | 135 | 5550000 | SPP_N | 0.4 | 0.8 | 299700000 | 599400000 | 765kV pipe to MISO_W
Future 5 OL 75 | MISO_W | NE | 17497 | Iatan | SPP/MISO Line | 765 | 1 | 4000 | 20 | 5550000 | SPP_N | 0.4 | 0.8 | 44400000 | 88800000 | 765kV pipe to MISO_W
Future 5 OL 75 | MISO_W | NE | 17497 | Axtell | Nebraska Sta. A | 765 | 1 | 4000 | 120 | 5550000 | SPP_N | 0.4 | 0.8 | 266400000 | 532800000 | Satisfies SPP internal requirment
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. A | Transformation | 765/345 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Transmission Sub
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. A | SPP/MISO Line | 765 | 1 | 4000 | 100 | 5550000 | SPP_N | 0.4 | 0.8 | 222000000 | 444000000 | 765kV pipe to MISO_W
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. A | Cass Co | 765 | 1 | 4000 | 150 | 5550000 | SPP_N | 0.4 | 0.8 | 333000000 | 666000000 | 765kV pipe to MISO_W
Future 5 OL 75 | MISO_W | NE | 17497 | Cass Co | Transfomation | 765/345 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Transmission Sub
Future 5 OL 75 | MISO_W | NE | 17497 | Hooker | Nebraska Sta. B | 765 | 1 | 4000 | 75 | 5550000 | SPP_N | 0.4 | 0.8 | 166500000 | 333000000 | Satisfies SPP internal requirment
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. B | Transformation | 765/345 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Substation
Future 5 OL 75 | MISO_W | NE | 17497 | Nebraska Sta. B | Holt Co. | 765 | 1 | 4000 | 150 | 5550000 | SPP_N | 0.4 | 0.8 | 333000000 | 666000000 | Satisfies SPP internal requirment
Future 5 OL 75 | MISO_W | NE | 17497 | Holt Co | Transformation | 765/345 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Substation
Future 5 OL 75 | MISO_W | NE | 17497 | Holt Co | SPP/MISO Line | 765 | 1 | 4000 | 10 | 5550000 | SPP_N | 0.4 | 0.8 | 22200000 | 44400000 | 765kV pipe to MISO_W
[12 empty] | Total Cost: |  | 8769975000 | 13915110000
Future 5 OL 75 | Entergy | SoCo | 431 | McAdams | South Bessemer | 230 | 1 | 600 | 40 | 1150000 | Entergy | 1.1 | 2.1 | 50600000 | 96600000 | Tie Line - Entergy/SoCo
Future 5 OL 75 | Entergy | SoCo | 431 | McAdams | South Bessemer | 230 | 1 | 600 | 120 | 1150000 | SoCo | 0.7 | 1.7 | 96600000 | 234600000 | Tie Line - Entergy/SoCo
Future 5 OL 75 | Entergy | SoCo | 431 | Bogalusa | Big Creek | 230 | 1 | 600 | 5 | 1150000 | Entergy | 1.1 | 2.1 | 6325000 | 12075000 | Tie Line - Entergy/SoCo
Future 5 OL 75 | Entergy | SoCo | 431 | Bogalusa | Big Creek | 230 | 1 | 600 | 95 | 1150000 | SoCo | 0.7 | 1.7 | 76475000 | 185725000 | Tie Line - Entergy/SoCo
[12 empty] | Total Cost: |  | 230000000 | 529000000
Future 5 OL 75 | NYISO_A-F | NYISO_GHI | 638 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 5 OL 75 | NYISO_A-F | NYISO_GHI | 638 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 5 OL 75 | NYISO_A-F | NYISO_GHI | 638 | Leeds |  | 345 | 2 |  |  |  | NYISO_A-F |  |  | 6000000 | 18000000 | Line terminal addition
Future 5 OL 75 | NYISO_A-F | NYISO_GHI | 638 | Pleasant Valley |  | 345 | 2 |  |  |  | NYISO_GHI |  |  | 6000000 | 18000000 | Line terminal addition
[12 empty] | Total Cost: |  | 297600000 | 439200000
Future 5 OL 75 | NEISO | NYISO_J_&_K | 90 | Pleasant Valley | NE Border | 345 | 1 | 900 | 17.8 | 2100000 | NYISO_GHI | 1.7 | 4.3 | 63546000 | 160734000 | NEISO-NYISO_GHI tie; relieves contingency constraint on NNC
Future 5 OL 75 | NEISO | NYISO_J_&_K | 90 | Long Mountain | NY Border | 345 | 1 | 900 | 5.6 | 2100000 | NEISO | 1.4 | 2.9 | 16464000 | 34104000 | Tie Line NEISO - NYISO_GHI
Future 5 OL 75 | NEISO | NYISO_J_&_K | 90 | Norwalk | Norwalk Harbor | 115 | 1 | 300 | 6.67 | 1100000 | NEISO | 1.8 | 2.7 | 25076200 | 30214300 | Some underground - 1.48 mi
Future 5 OL 75 | NEISO | NYISO_J_&_K | 90 | Pleasant Valley |  | 345 | 1 | [6 empty] | 3000000 | 9000000 | Line terminal addition
[12 empty] | Total Cost: |  | 108086200 | 234052300
Future 5 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Roseland | Linden | 230 | 1 | 600 | 20 | 1150000 | PJM_Eastern_MAAC | 4 | 4.7 | 92000000 | 108100000
Future 5 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Goethals | Linden | 230 | [7 empty] | 0 | 0 | Allow VFT flow from NY to PJM
[12 empty] | Total Cost: |  | 92000000 | 108100000
Future 5 OL 75 | MAPP_CA | MISO_W | 88 | Riel | Moranville | 230 | 1 | 600 | 110 | 1150000 | MAPP_CA | 0.3 | 0.6 | 37950000 | 75900000 | N-1 for MAPP_CA to MAPP_US
Future 5 OL 75 | MAPP_CA | MISO_W | 88 | Moranville | Shannon | 230 | 1 | 600 | 150 | 1150000 | MISO_W | 0.4 | 0.9 | 69000000 | 155250000 | N-1 for MAPP_CA to MAPP_US
Future 5 OL 75 | MAPP_CA | MISO_W | 88 | Shannon | Arrowhead | 230 | 1 | 600 | 75 | 1150000 | MISO_W | 0.4 | 0.9 | 34500000 | 77625000 | N-1 for MAPP_CA to MAPP_US
[12 empty] | Total Cost: |  | 141450000 | 308775000
Future 5 OL 75 | MAPP_CA | MAPP_US | 65 | Letellier | Drayton | 230 | 1 | 600 | 38 | 1150000 | MAPP_US | 0.8 | 1.3 | 34960000 | 56810000 | N-1 for MAPP_CA to MISO_W
Future 5 OL 75 | MAPP_CA | MAPP_US | 65 | Drayton | Prairie | 230 | 1 | 600 | 58 | 1150000 | MAPP_US | 0.8 | 1.3 | 53360000 | 86710000 | N-1 for MAPP_CA to MISO_W
[12 empty] | Total Cost: |  | 88320000 | 143520000
Future 5 OL 75 | MISO_WUMS | MISO_MI | 49 | Indian Lake | Hiawatha | 138 | 1 | 300 | 41 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 22550000 | 72160000 | Line exists but termianls do not
[12 empty] | Total Cost: |  | 22550000 | 72160000
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | N LaCrosse | N Madison | 345 | 1 | 1800 | 136 | 2500000 | MISO_WUMS | 0.6 | 0.8 | 204000000 | 272000000
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | N Madison | Cardinal | 345 | 1 | 1800 | 21 | 2500000 | MISO_WUMS | 0.6 | 0.8 | 31500000 | 42000000
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | Cardinal | Spring Green | 345 | 1 | 1800 | 28 | 2500000 | MISO_WUMS | 0.6 | 0.8 | 42000000 | 56000000
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | Spring Green | Dubuque | 345 | 1 | 1800 | 75 | 2500000 | MISO_WUMS | 0.6 | 0.8 | 112500000 | 150000000
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | Saratoga | Petenwell | 138 | 1 | 300 | 16 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 8800000 | 28160000 | Rebuild of existing line
Future 5 OL 75 | MISO_WUMS | MISO_W | 2127 | Kilbourn | Council Creek | 138 | 1 | 300 | 50 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 27500000 | 88000000 | 69kV ROW exists
[12 empty] | Total Cost: |  | 426300000 | 636160000
Future 5 OL 75 | PJM_ROR | VACAR | 865 | Tarboro | PA change (Farmville) | 230 | 1 | 900 | 10 | 1580000 | PJM_ROR | 0.8 | 1.1 | 12640000 | 17380000
Future 5 OL 75 | PJM_ROR | VACAR | 865 | PA change (Tarboro) | Farmville | 230 | 1 | 900 | 10 | 1580000 | VACAR | 0.5 | 1 | 7900000 | 15800000
Future 5 OL 75 | PJM_ROR | VACAR | 865 | E. Danville | PA change (Sadler) | 230 | 1 | 900 | 10 | 1580000 | PJM_ROR | 0.8 | 1.1 | 12640000 | 17380000
Future 5 OL 75 | PJM_ROR | VACAR | 865 | PA change (E. Danville) | Sadler | 230 | 1 | 900 | 15 | 1580000 | VACAR | 0.5 | 1 | 11850000 | 23700000
[12 empty] | Total Cost: |  | 45030000 | 74260000
Future 5 OL 75 | SPP_N | Entergy | 7440 | Rose Hill | Flint Creek | 765 | 1 | 4000 | 178 | 5550000 | SPP_N | 0.4 | 0.8 | 395160000 | 790320000 | Flint Crk. Is terminal for Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | Flint Creek | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie PointSubstation
Future 5 OL 75 | SPP_N | Entergy | 7440 | Flint Creek | Nelson | 500 | 1 | 2600 | 420 | 3450000 | Entergy | 0.7 | 1.4 | 1014300000 | 2028600000 | 500 kV tie line into Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | Flint Creek | Morgan | 500 | 1 | 2600 | 125 | 3450000 | Entergy | 0.7 | 1.4 | 301875000 | 603750000 | Back up for N-1 loss of 765 source
Future 5 OL 75 | SPP_N | Entergy | 7440 | Summit | Lang | 765 | 1 | 4000 | 84 | 5550000 | SPP_N | 0.4 | 0.8 | 186480000 | 372960000 | Satisfies SPP internal requirment
Future 5 OL 75 | SPP_N | Entergy | 7440 | Summit | Transformation | 765/345kV | 1 |  | 1 | 25000000 | SPP_N | 0.9 | 1.5 | 22500000 | 37500000 | 765/345kV Sub
Future 5 OL 75 | SPP_N | Entergy | 7440 | Lang | Transmission Sub | 765 | 1 |  | 1 | 25000000 | SPP_N | 0.9 | 1.5 | 22500000 | 37500000 | 765kV Transmission Sub
Future 5 OL 75 | SPP_N | Entergy | 7440 | Lang | LaCygne | 765 | 1 | 4000 | 84 | 5550000 | SPP_N | 0.4 | 0.8 | 186480000 | 372960000 | Satisfies N-1 condition. Lacygna is terminal for Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | LaCygne | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie Point Substation
Future 5 OL 75 | SPP_N | Entergy | 7440 | LaCygne | Baxter Wilson | 500 | 1 | 2600 | 500 | 3450000 | Entergy | 0.7 | 1.4 | 1207500000 | 2415000000 | 500 kV tie line into Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | Lang | Morgan | 765 | 1 | 4000 | 168 | 5550000 | SPP_N | 0.4 | 0.8 | 372960000 | 745920000 | Morgan is terminal for Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | Morgan | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Tie Point Substation
Future 5 OL 75 | SPP_N | Entergy | 7440 | Morgan | Fancy Point | 500 | 1 | 2600 | 625 | 3450000 | Entergy | 0.7 | 1.4 | 1509375000 | 3018750000 | 500 kV tie line into Entergy Region
Future 5 OL 75 | SPP_N | Entergy | 7440 | Morgan | LaCygne | 500 | 1 | 2600 | 100 | 3450000 | Entergy | 0.7 | 1.4 | 241500000 | 483000000 | Back up for N-1 loss of 765 source
Future 5 OL 75 | SPP_N | Entergy | 7440 | Morgan | Waterford | 500 | 1 | 2600 | 700 | 3450000 | Entergy | 0.7 | 1.4 | 1690500000 | 3381000000 | Sibley is terminal for EES/AECI
Future 5 OL 75 | SPP_N | Entergy | 7440 | Rose Hill | Lang | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
Future 5 OL 75 | SPP_N | Entergy | 7440 | Lang | Iatan | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
[12 empty] | Total Cost: |  | 7716030000 | 15369360000
Future 2 OL 75 | SPP-S | Entergy | 4282 | Sooner | Fort Smith | 765 | 1 | 4000 | 185 | 5550000 | SPP_S | 0.4 | 0.8 | 410700000 | 821400000 | Fort Smith is terminal for EES/AECI
Future 2 OL 75 | SPP-S | Entergy | 4282 | Fort Smith | Transformation | 765/500 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Substation
Future 2 OL 75 | SPP-S | Entergy | 4282 | Fort Smith | ANO | 500 | 1 | 2600 | 75 | 3450000 | Entergy | 0.7 | 1.4 | 181125000 | 362250000 | SPP S Tie to Entergy Region
Future 5 OL 75 | SPP-S | Entergy | 4282 | Woodward | Seminole | 765 | 1 | 4000 | 180 | 5550000 | SPP_S | 0.4 | 0.8 | 399600000 | 799200000 | Woodward - Seminole - NW Texarkana - Dolett Hills 765kV transmission line. Dolett Hills is terminal for EES/AECI
Future 5 OL 75 | SPP-S | Entergy | 4282 | Seminole | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 2 OL 75 | SPP-S | Entergy | 4282 | Seminole | NW Texarkana | 765 | 1 | 4000 | 180 | 5550000 | SPP_S | 0.4 | 0.8 | 399600000 | 799200000
Future 5 OL 75 | SPP-S | Entergy | 4282 | NW Texarkana | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 5 OL 75 | SPP-S | Entergy | 4282 | NW Texarkana | Dolett Hills | 765 | 1 | 4000 | 115 | 5550000 | SPP_S | 0.4 | 0.8 | 255300000 | 510600000
Future 2 OL 75 | SPP-S | Entergy | 4282 | Dolett Hills | Transformation | 765/500 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 5 OL 75 | SPP-S | Entergy | 4282 | Dolett Hills | Sterlington | 500 | 1 | 2600 | 110 | 3450000 | Entergy | 0.7 | 1.4 | 265650000 | 531300000 | SPP_S to Entergy Region Tie
Future 5 OL 75 | SPP-S | Entergy | 4282 | Turk | McNeil | 345 | 1 | 1800 | 25 | 2500000 | SPP S | 0.4 | 0.8 | 25000000 | 50000000 | SPP_S to Entergy Region Tie
Future 2 OL 75 | SPP-S | Entergy | 4282 | Turk | McNeil | 345 | 1 | 1800 | 25 | 2500000 | Entergy | 1 | 1.9 | 62500000 | 118750000 | SPP_S to Entergy Region Tie
[12 empty] | Total Cost: |  | 2190275000 | 4310700000
Future 5 OL 75 | SPP_N | SPP_S |  | SPP 765kV Overlay |  | 765 |  |  | 1 | 8000000000 | SPP | 1 | 1 | 8000000000 | 8000000000 | This overlay is required to source the pipes for the future 5 xfer requirements
Future 5 OL 75 | SPP_N | SPP_S | 1571 |  |  | 765 |  |  | 1 | 0 | SPP | 1 | 1 | 0 | 0 | Cost is included in SPP 765kV Overlay cost shown above
[12 empty] | Total Cost: |  | 8000000000 | 8000000000
Future 5 OL 75 | SPP_N | NE | 10998 | Axtell | Spearville | 765 | 1 | 4000 | 230 | 5550000 | NE, SPP_N | 0.4 | 0.8 | 510600000 | 1021200000 | Satisfies SPP internal requirment
Future 5 OL 75 | SPP_N | NE | 10998 | Axtell | Summit | 765 | 1 | 4000 | 180 | 5550000 | NE, SPP_N | 0.4 | 0.8 | 399600000 | 799200000 | 765/345kV Sub
Future 5 OL 75 | SPP_N | NE | 10998 | Axtell | Gentleman | 765 | 1 | 4000 | 100 | 5550000 | NE, SPP_N | 0.4 | 0.8 | 222000000 | 444000000 | 765kV Transmission Sub
Future 5 OL 75 | SPP_N | NE | 10998 | Axtell | Transmission Sub | 765/345kV | 1 |  | 1 | 53000000 | NE, SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Sub
[12 empty] | Total Cost: |  | 1179900000 | 2343900000