## Component Estimates
Future 6 OL 25 Total Cost: |  | 2069929200 | 3114593550
Future | Transfer Limit Increase |  |  | Transmission Building Blocks | [7 empty] | Multiplier range |  | Cost range
Scenario | Region1 | Region2 | Transfer Limit Increase (MW) | Termination 1 | Termination 2 or Device Description | Voltage (kV) | # of Circuits | Capability (MW) | Length (Miles) | Generic Per Unit Cost | Upgrade Region | Low Mult. | High Mult. | Cost Low | Cost High | Notes
Future 6 OL 25 | MISO_WUMS | MISO_MI | 830 | Point Beach | Ludington | HVDC SC | 2 | 2400 | 65 | 7500000 | MISO_WUMS | 0.7 | 1.1 | 341250000 | 536250000 | Submarine Cable
Future 6 OL 25 | MISO_WUMS | MISO_MI | 830 | Point Beach | (DC Terminal) | HVDC |  | 1200 | 1 | 170000000 | MISO_WUMS | 1 | 1 | 170000000 | 170000000
Future 6 OL 25 | MISO_WUMS | MISO_MI | 830 | Ludington | (DC Terminal) | HVDC |  | 1200 | 1 | 170000000 | MISO_MI | 1 | 1 | 170000000 | 170000000
[12 empty] | Total Cost: |  | 681250000 | 876250000
Future 6 OL 25 | MAPP_CA | MISO_W | 18 | [10 empty] | 0 | 0 | Very small relative to the existing capacity
[12 empty] | Total Cost: |  | 0 | 0
Future 6 OL 25 | NYISO_A-F | NYISO_GHI | 507 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 6 OL 25 | NYISO_A-F | NYISO_GHI | 507 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 6 OL 25 | NYISO_A-F | NYISO_GHI | 507 | Leeds |  | 345 | 2 |  |  |  | NYISO_A-F |  |  | 6000000 | 18000000 | Line terminal addition
Future 6 OL 25 | NYISO_A-F | NYISO_GHI | 507 | Pleasant Valley |  | 345 | 2 |  |  |  | NYISO_GHI |  |  | 6000000 | 18000000 | Line terminal addition
[12 empty] | Total Cost: |  | 297600000 | 439200000
Future 6 OL 25 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Roseland | Linden | 230 | 1 | 600 | 20 | 1150000 | PJM_Eastern_MAAC | 4 | 4.7 | 92000000 | 108100000
Future 6 OL 25 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Goethals | Linden | 230 | [7 empty] | 0 | 0 | Allow VFT flow from NY to PJM
[12 empty] | Total Cost: |  | 92000000 | 108100000
Future 6 OL 25 | NYISO_GHI | NYISO_J_&_K | 58 | Sprain Brook | West 49th Street | 345 | UG | 600 | 17.89 | 19750000 | NYISO_J_&_K | 1.2 | 1.5 | 423993000 | 529991250
Future 6 OL 25 | NYISO_GHI | NYISO_J_&_K | 58 | Sprain Brook |  | 345 | 1 |  |  |  | NYISO_GHI |  |  | 3000000 | 9000000 | Line terminal addition
Future 6 OL 25 | NYISO_GHI | NYISO_J_&_K | 58 |  | West 49th Street | 345 | 1 |  |  |  | NYISO_J_&_K | 1.87 | 2.7 | 20000000 | 30000000 | Line terminal addition
[12 empty] | Total Cost: |  | 446993000 | 568991250
Future 6 OL 25 | NEISO | NYISO_J_&_K | 70 | Pleasant Valley | NE Border | 345 | 1 | 900 | 17.8 | 2100000 | NYISO_GHI | 1.7 | 4.3 | 63546000 | 160734000 | NEISO-NYISO_GHI tie; relieves contingency constraint on NNC
Future 6 OL 25 | NEISO | NYISO_J_&_K | 70 | Pleasant Valley |  | 345 | 1 | [6 empty] | 3000000 | 9000000 | Line terminal addition
Future 6 OL 25 | NEISO | NYISO_J_&_K | 70 | Long Mountain | NY Border | 345 | 1 | 900 | 5.6 | 2100000 | NEISO | 1.4 | 2.9 | 16464000 | 34104000 | Tie Line NEISO - NYISO_GHI
Future 6 OL 25 | NEISO | NYISO_J_&_K | 70 | Norwalk | Norwalk Harbor | 115 | 1 | 300 | 6.67 | 1100000 | NEISO | 1.87 | 2.7 | 25076200 | 30214300 | Some underground - 1.48 mi
[12 empty] | Total Cost: |  | 108086200 | 234052300
Future 6 OL 25 | SPP_N | NE | 1201 | Sheldon Station | Jeffrey Energy Ctr. | 345 | 1 | 1800 | 110 | 2500000 | SPP_N/NE | 0.4 | 0.8 | 110000000 | 220000000
Future 6 OL 25 | SPP_N | NE | 1201 | Pauline | Summit | 345 | 1 | 1800 | 145 | 2500000 | SPP_N/NE | 0.4 | 0.8 | 145000000 | 290000000 | Satisfies N-1 Requirement
[12 empty] | Total Cost: |  | 255000000 | 510000000
Future 6 OL 25 | SPP_N | SPP_S | 383 | Medicine Lodge | Woodring | 345 | 1 | 900 | 90 | 2100000 | SPP_N/SPP_S | 0.5 | 1 | 94500000 | 189000000
Future 6 OL 25 | SPP_N | SPP_S | 383 | Medicine Lodge | Woodring | 345 | 1 | 900 | 90 | 2100000 | SPP_N/SPP_S | 0.5 | 1 | 94500000 | 189000000 | Satisfies N-1 Requirement
[12 empty] | Total Cost: |  | 189000000 | 378000000