## Component Estimates
Future 8 OL 75 Total Cost: |  | 36684818200 | 51054582550
Future | Transfer Limit Increase |  |  | Transmission Building Blocks | [7 empty] | Multiplier range |  | Cost range
Scenario | Region1 | Region2 | Transfer Limit Increase (MW) | Termination 1 | Termination 2 or Device Description | Voltage (kV) | # of Circuits | Capability (MW) | Length (Miles) | Generic Per Unit Cost | Upgrade Region | Low Mult. | High Mult. | Cost Low | Cost High | Notes
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Mitchell Co | Hampton Corner | 765 | 1 | 4000 | 92 | 5550000 | MISO_W | 0.5 | 0.6 | 255300000 | 306360000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | New MN 765 Sub 1 | New MN 765 Sub 2 | 765 | 1 | 4000 | 26 | 5550000 | MISO_W | 0.5 | 0.6 | 72150000 | 86580000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Brookings County | New MN 765 Sub 2 | 765 | 1 | 4000 | 20 | 5550000 | MISO_W | 0.5 | 0.6 | 55500000 | 66600000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Brookings County | Hampton Corner | 765 | 1 | 4000 | 211 | 5550000 | MISO_W | 0.5 | 0.6 | 585525000 | 702630000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Grimes | Hills | 765 | 1 | 4000 | 141 | 5550000 | MISO_W | 0.5 | 0.6 | 391275000 | 469530000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | IA-G Station | Grimes | 765 | 1 | 4000 | 105 | 5550000 | MISO_W | 0.5 | 0.6 | 291375000 | 349650000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Lakefield Junction | New MN 765 Sub 1 | 765 | 1 | 4000 | 58 | 5550000 | MISO_W | 0.5 | 0.6 | 160950000 | 193140000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Lakefield Junction | IA-G Station | 765 | 1 | 4000 | 109 | 5550000 | MISO_W | 0.5 | 0.6 | 302475000 | 362970000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Mitchell Co | Hills | 765 | 1 | 4000 | 179 | 5550000 | MISO_W | 0.5 | 0.6 | 496725000 | 596070000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Mitchell Co | North La Crosse | 765 | 1 | 4000 | 89 | 5550000 | MISO_W | 0.5 | 0.6 | 246975000 | 296370000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Quad Cities | Hills | 765 | 1 | 4000 | 77 | 5550000 | MISO_W | 0.5 | 0.6 | 213675000 | 256410000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | North La Crosse | North Madison | 765 | 1 | 4000 | 119 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 396270000 | 462315000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | North Madison | Darlington | 765 | 1 | 4000 | 65 | 5550000 | MISO_WUMS | 0.6 | 0.7 | 216450000 | 252525000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Montgomery | St. Francois | 765 | 1 | 4000 | 104 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 288600000 | 346320000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Fairport | Montgomery | 765 | 1 | 4000 | 205 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 568875000 | 682650000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Fairport | Grimes | 765 | 1 | 4000 | 141 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 391275000 | 469530000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Reynolds 765 | Greentown | 765 | 1 | 4000 | 66 | 5550000 | MISO_IN | 0.5 | 0.7 | 183150000 | 256410000 | MISO Cand MVP Portolio 1
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | MISO Regional Generator Outlet Study 345 lines |  | 345 | 1 | 1800 | 2124 | 2500000 | MISO | 0.4 | 0.8 | 2124000000 | 4248000000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | St Francois | Rockport | 765 | 1 | 4000 | 187 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 518925000 | 622710000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Reynolds 765 (Pontiac/Greentown Tap) | Sullivan | 765 | 1 | 4000 | 120 | 5550000 | PJM_ROR | 0.8 | 0.9 | 532800000 | 599400000 | MISO RGOS 765 overlay
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Rockport | Baker | 765 | 1 | 4000 | 223 | 5550000 | PJM_ROR | 0.8 | 0.9 | 990120000 | 1113885000 | Tie 1
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Montgomery | PA change (Don Marquis) | 765 | 1 | 4000 | 248 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 688200000 | 825840000 | Tie 2
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | PA change (Montgomery) | Don Marquis | 765 | 1 | 4000 | 250 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1110000000 | 1248750000 | Tie 2 $62.3 mil sub/xfmr cost
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Darlington | PA change (Dumont/Marysville tap) | 765 | 1 | 4000 | 40 | 5550000 | MISO_W | 0.5 | 0.6 | 111000000 | 133200000 | Tie 3
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | PA change (Darlington) | Dumont/Marysville tap | 765 | 1 | 4000 | 365 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1620600000 | 1823175000 | Tie 3 $333.5 mil sub/xfmr cost
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Powerton | Marysville/Flatlick tap | 765 | 1 | 4000 | 354 | 5550000 | PJM_ROR | 0.8 | 0.9 | 1571760000 | 1768230000 | Tie 4 $106.3 mil sub/xfmr cost
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Quad Cities | Reynolds 765 | 765 | 1 | 4000 | 230 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 638250000 | 765900000 | Tie 5 $22 mil sub cost
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | St Francois | Jefferson | 765 | 1 | 4000 | 335 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 929625000 | 1115550000 | Tie 6
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Fairport | Powerton | 765 | 1 | 4000 | 307 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 851925000 | 1022310000
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Montgomery | Powerton | 765 | 1 | 4000 | 185 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 513375000 | 616050000
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Hazelton | Darlington | 765 | 1 | 4000 | 119 | 5550000 | MISO_W | 0.5 | 0.6 | 330225000 | 396270000
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Darlington | Quad Cities | 765 | 1 | 4000 | 120 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 333000000 | 399600000
Future 8 OL 75 | MISO_W | PJM_ROR | 19066 | Quad Cities | Powerton | 765 | 1 | 4000 | 84 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 233100000 | 279720000
[12 empty] | Total Cost: |  | 18213450000 | 23134650000
Future 8 OL 75 | MISO_W | MISO_MO_IL | 248 | Ottumwa | Adair | 345 | 1 | 900 | 64 | 2100000 | MISO_MO_IL | 0.3 | 0.6 | 40320000 | 80640000 | Candidate MVP Port.1
Future 8 OL 75 | MISO_W | MISO_MO_IL | 248 | Adair | Palmyra | 345 | 1 | 900 | 64 | 2100000 | MISO_MO_IL | 0.3 | 0.6 | 40320000 | 80640000 | Candidate MVP Port.1
[12 empty] | Total Cost: |  | 80640000 | 161280000
Future 8 OL 75 | MISO_IN | MISO_MI | 490 | Hiple | IN/MI border | 345 | 1 | 900 | 30 | 2100000 | MISO_IN | 0.5 | 0.8 | 31500000 | 50400000 | circuit 1
Future 8 OL 75 | MISO_IN | MISO_MI | 490 | IN/MI border | Battle Creek | 345 | 1 | 900 | 45 | 2100000 | MISO_MI | 0.5 | 0.7 | 47250000 | 66150000 | circuit 1
Future 8 OL 75 | MISO_IN | MISO_MI | 490 | Hiple | IN/MI border | 345 | 1 | 900 | 30 | 2100000 | MISO_IN | 0.5 | 0.8 | 31500000 | 50400000 | circuit 2
Future 8 OL 75 | MISO_IN | MISO_MI | 490 | IN/MI border | Battle Creek | 345 | 1 | 900 | 45 | 2100000 | MISO_MI | 0.5 | 0.7 | 47250000 | 66150000 | circuit 2
[12 empty] | Total Cost: |  | 157500000 | 233100000
Future 8 OL 75 | IESO | MISO_MI | 1285 | Longwood | Lambton | 230 | 2 | 1200 | 50 | 1800000 | IESO | 0.8 | 1.4 | 72000000 | 126000000 | line 1
Future 8 OL 75 | IESO | MISO_MI | 1285 | Longwood | Lambton | 230 | 2 | 1200 | 50 | 1800000 | IESO | 0.8 | 1.4 | 72000000 | 126000000 | line 2
Future 8 OL 75 | IESO | MISO_MI | 1285 | Longwood | Lambton | 230 | 1 | 600 | 50 | 1150000 | IESO | 0.8 | 1.9 | 46000000 | 109250000 | N-1 backup
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | PAR | 230/345 | 1 | 750 | 1 | 20000000 | IESO | 0.8 | 1.4 | 16000000 | 28000000 | Phase Angle Regulator_1
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | PAR | 230/345 | 1 | 750 | 1 | 20000000 | IESO | 0.8 | 1.4 | 16000000 | 28000000 | Phase Angle Regulator_2
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | PAR | 230/345 | 1 | 750 | 1 | 20000000 | IESO | 0.8 | 1.4 | 16000000 | 28000000 | Phase Angle Regulator N-1 backup
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | St Clair | 345 | 1 | 900 | 4 | 2100000 | IESO | 0.8 | 1.4 | 6720000 | 11760000 | Tie Line_1 IESO-MISO_MI Ontario portion
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | St Clair | 345 | 1 | 900 | 4 | 2100000 | IESO | 0.8 | 1.4 | 6720000 | 11760000 | Tie Line_2 IESO-MISO_MI Ontario portion
Future 8 OL 75 | IESO | MISO_MI | 1285 | Lambton | St Clair | 345 | 1 | 900 | 4 | 2100000 | IESO | 0.8 | 1.4 | 6720000 | 11760000 | Tie Line_3 IESO-MISO_MI N-1 backup
Future 8 OL 75 | IESO | MISO_MI | 1285 | PA Border | St Clair | 345 | 3 | 900 | 6 | 2100000 | MISO_MI | 0.5 | 0.7 | 6300000 | 8820000 | MISO portion of tie lines 3x2miles
[12 empty] | Total Cost: |  | 264460000 | 489350000
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Indian Lake | Hiawatha | 138 | 1 | 300 | 41 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 22550000 | 72160000 | Line exists but termianls do not
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Hiawatha | Pine River | 138 | 1 | 300 | 48 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 26400000 | 84480000 | Convert 69kV circuit to 138kV
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Munising | Roberts | 138 | 1 | 300 | 59 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 32450000 | 103840000
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Roberts | 9Mile | 138 | 1 | 300 | 55 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 30250000 | 96800000 | 69kV ROW exists
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | 9Mile | Pine River | 138 | 1 | 300 | 17 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 9350000 | 29920000 | 69kV ROW exists
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Pine River | Straits | 138 | 2 | 300 | 25 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 13750000 | 44000000 | Convert 69kV double circuit to 138kV
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Straits | McGulpin | 138 | 2 | 300 | 5 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 2750000 | 8800000 | 3rd & 4th Submarine Cables
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | McGulpin | Livingston | 138 | 2 | 300 | 59 | 1100000 | MISO_MI | 0.5 | 1.6 | 32450000 | 103840000
Future 8 OL 75 | MISO_WUMS | MISO_MI | 195 | Holmes | Chandler | 138 | 1 | 300 | 81 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 44550000 | 142560000 | 69kV ROW exists
[12 empty] | Total Cost: |  | 214500000 | 686400000
Future 8 OL 75 | IESO | MISO_W | 55 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | IESO | 0.8 | 1.9 | 92000000 | 218500000 | line 1
Future 8 OL 75 | IESO | MISO_W | 55 | Mackenzie | Fort Frances | 230 | 1 | 600 | 100 | 1150000 | IESO | 0.8 | 1.9 | 92000000 | 218500000 | line 1 N-1 backup
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | Fort Frances | 230/115 | 1 | 125 | 1 | 2500000 | IESO | 0.8 | 1.4 | 2000000 | 3500000 | Autotransformer N-1 backup
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | IESO | 0.8 | 1.4 | 880000 | 1540000 | Tie Line IESO-MISO_W
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | International Falls | 115 | 1 | 300 | 1 | 1100000 | IESO | 0.8 | 1.4 | 880000 | 1540000 | Tie Line IESO-MISO_W N-1 backup
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator
Future 8 OL 75 | IESO | MISO_W | 55 | Fort Frances | PAR | 115/115 | 1 | 100 | 1 | 2000000 | IESO | 0.8 | 1.4 | 1600000 | 2800000 | Phase Angle Regulator N-1 backup
[12 empty] | Total Cost: |  | 192960000 | 452680000
Future 8 OL 75 | MAPP_CA | IESO | 7 | [10 empty] | 0 | 0 | Very small relative to the existing capacity
[12 empty] | Total Cost: |  | 0 | 0
Future 8 OL 75 | MISO_W | SPP_N | 250 | [10 empty] | 0 | 0 | See MISO_W to NE
[12 empty] | Total Cost: |  | 0 | 0
Future 8 OL 75 | MISO_MO-IL | SPP_N | 1954 | Iatan | Fairport | 765 | 1 | 4000 | 72 | 5550000 | MISO_MO_IL | 0.5 | 0.6 | 199800000 | 239760000 | Satisfies N-1 condition for NE to MISO_W
[12 empty] | Total Cost: |  | 199800000 | 239760000
Future 8 OL 75 | MISO_W | NE | 2014 | Nebraska Sta. A | Iowa Sta. A | 765 | 1 | 4000 | 79 | 5550000 | SPP_N | 0.4 | 0.8 | 175380000 | 350760000 | NSA to state line. Satisfies N-1 condition for SPP_N to MISO MO_IL
Future 8 OL 75 | MISO_W | NE | 2014 | Nebraska Sta. A | Transformation | 765/345 | 1 |  | 1 | 53000000 | NE | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Substation
Future 8 OL 75 | MISO_W | NE | 2014 | Nebraska Sub A | Iowa Sub G | 765 | 1 | 4000 | 65 | 5550000 | MISO_W | 0.5 | 0.6 | 180375000 | 216450000 | N-1 backup for SPP_N to MISO_MO-IL
[12 empty] | Total Cost: |  | 403455000 | 646710000
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Niagara | IESO Border | 230 | 1 | 600 | 3.9 | 1150000 | NYISO_A-F | 1.3 | 2.6 | 5830500 | 11661000
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Niagara | IESO Border | 230 | 1 | 600 | 3.9 | 1150000 | NYISO_A-F | 1.3 | 2.6 | 5830500 | 11661000
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Niagara |  | 230 | 2 |  |  |  | NYISO_A-F |  |  | 5000000 | 10000000 | Line terminal addition
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Beck 2 | NYISO border | 230 | 1 | 600 | 5 | 1150000 | IESO | 0.8 | 1.9 | 4600000 | 10925000 | line 1
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Beck 2 | NYISO border | 230 | 1 | 600 | 5 | 1150000 | IESO | 0.8 | 1.9 | 4600000 | 10925000 | line 1 N-1 backup
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Beck 2 | Regulator | 230 | 1 | 500 | 1 | 15000000 | IESO | 0.8 | 1.4 | 12000000 | 21000000 | Voltage Regulator
Future 8 OL 75 | NYISO_A-F | IESO | 499 | Beck 2 | Regulator | 230 | 1 | 500 | 1 | 15000000 | IESO | 0.8 | 1.4 | 12000000 | 21000000 | Voltage Regulator backup
[12 empty] | Total Cost: |  | 49861000 | 97172000
Future 8 OL 75 | NYISO_A-F | NYISO_GHI | 1016 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 8 OL 75 | NYISO_A-F | NYISO_GHI | 1016 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 8 OL 75 | NYISO_A-F | NYISO_GHI | 1016 | Leeds | Pleasant Valley | 345 | 1 | 900 | 40 | 2100000 | NYISO_A-F | 1.7 | 2.4 | 142800000 | 201600000
Future 8 OL 75 | NYISO_A-F | NYISO_GHI | 1016 | Leeds |  | 345 | 3 |  |  |  | NYISO_A-F |  |  | 9000000 | 27000000 | Line terminal addition
Future 8 OL 75 | NYISO_A-F | NYISO_GHI | 1016 | Pleasant Valley |  | 345 | 3 |  |  |  | NYISO_GHI |  |  | 9000000 | 27000000 | Line terminal addition
[12 empty] | Total Cost: |  | 446400000 | 658800000
Future 8 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Roseland | Linden | 230 | 1 | 600 | 20 | 1150000 | PJM_Eastern_MAAC | 4 | 4.7 | 92000000 | 108100000
Future 8 OL 75 | NYISO_J_&_K | PJM_Eastern_MAAC | 330 | Goethals | Linden | 230 | [7 empty] | 0 | 0 | Allow VFT flow from NY to PJM
[12 empty] | Total Cost: |  | 92000000 | 108100000
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Pleasant Valley | NE Border | 345 | 1 | 900 | 17.8 | 2100000 | NYISO_GHI | 1.7 | 4.3 | 63546000 | 160734000 | NEISO-NYISO_GHI tie; relieves contingency constraint on NNC, add'l 350MW on NNC; remaining 258MW thru NYISO_GHI to NYISO_J_&_K
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Pleasant Valley |  | 345 | 1 | [6 empty] | 3000000 | 9000000 | Line terminal addition
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Pleasant Valley | Sprain Brook | 345 | 1 | 900 | 60.9 | 2100000 | NYISO_GHI | 1.7 | 4.3 | 217413000 | 549927000 | Remaining 258MW wheel thru NEISO to NYISO_J&K
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Pleasant Valley |  | 345 | 1 |  |  |  | NYISO_GHI |  |  | 3000000 | 9000000 | Line terminal addition
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Long Mountain | NY Border | 345 | 1 | 900 | 5.6 | 2100000 | NEISO | 1.4 | 2.9 | 16464000 | 34104000 | Tie Line NEISO - NYISO_GHI
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Norwalk | Norwalk Harbor | 115 | 1 | 300 | 6.67 | 1100000 | NEISO | 1.87 | 2.7 | 25076200 | 30214300 | Some underground - 1.48 mi
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 |  | Sprain Brook | 345 | 1 |  |  |  | NYISO_GHI |  |  | 3000000 | 9000000 | Line terminal addition
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Sprain Brook | West 49th Street | 345 | UG | 600 | 17.89 | 19750000 | NYISO_J_&_K | 1.2 | 1.5 | 423993000 | 529991250 | Remaining 258MW wheel thru NEISO to NYISO_J&K
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 | Sprain Brook |  | 345 | 1 |  |  |  | NYISO_GHI |  |  | 3000000 | 9000000 | Line terminal addition
Future 8 OL 75 | NEISO | NYISO_J_&_K | 608 |  | West 49th Street | 345 | 1 |  |  |  | NYISO_J_&_K |  |  | 20000000 | 30000000 | Line terminal addition
[12 empty] | Total Cost: |  | 778492200 | 1370970550
Future 8 OL 75 | MISO_WUMS | MISO_W | 118 | Saratoga | Petenwell | 138 | 1 | 300 | 16 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 8800000 | 28160000 | Rebuild of existing line
Future 8 OL 75 | MISO_WUMS | MISO_W | 118 | Kilbourn | Council Creek | 138 | 1 | 300 | 50 | 1100000 | MISO_WUMS | 0.5 | 1.6 | 27500000 | 88000000 | 69kV ROW exists
[12 empty] | Total Cost: |  | 36300000 | 116160000
Future 8 OL 75 | SPP_N | Entergy | 5546 | Summit | Lang | 765 | 1 | 4000 | 84 | 5550000 | SPP_N | 0.4 | 0.8 | 186480000 | 372960000 | Satisfies SPP internal requirment
Future 8 OL 75 | SPP_N | Entergy | 5546 | Summit | Transformation | 765/345 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/345kV Sub
Future 8 OL 75 | SPP_N | Entergy | 5546 | Lang | Transmission Sub | 765 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765kV Transmission Sub
Future 8 OL 75 | SPP_N | Entergy | 5546 | Lang | Morgan | 765 | 1 | 4000 | 168 | 5550000 | SPP_N | 0.4 | 0.8 | 372960000 | 745920000 | Morgan is terminal for EES/AECI
Future 8 OL 75 | SPP_N | Entergy | 5546 | Morgan | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Substation
Future 8 OL 75 | SPP_N | Entergy | 5546 | Morgan | White Bluff | 500 | 1 | 2600 | 250 | 3450000 | Entergy | 0.7 | 1.4 | 603750000 | 1207500000 | Tie into White Bluff area
Future 8 OL 75 | SPP_N | Entergy | 5546 | Morgan | Transformation | 500/345 | 1 |  | 2 | 22000000 | Entergy | 0.9 | 1.5 | 39600000 | 66000000 | Accommodate back up tie to LaCygne
Future 8 OL 75 | SPP_N | Entergy | 5546 | Morgan | LaCygne | 345 | 1 | 1800 | 100 | 2500000 | Entergy | 1 | 1.9 | 250000000 | 475000000 | Back up for N-1 loss of 765 source
Future 8 OL 75 | SPP_N | Entergy | 5546 | Rose Hill | Flint Creek | 765 | 1 | 4000 | 178 | 5550000 | SPP_N | 0.4 | 0.8 | 395160000 | 790320000 | Flint Crk. Is terminal for EES/AECI
Future 8 OL 75 | SPP_N | Entergy | 5546 | Flint Creek | Transformation | 765/500 | 1 |  | 1 | 53000000 | SPP_N | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Substation
Future 8 OL 75 | SPP_N | Entergy | 5546 | Flint Creek | McKnight | 500 | 1 | 2600 | 450 | 3450000 | Entergy | 0.7 | 1.4 | 1086750000 | 2173500000 | Tie into McKnight area
Future 8 OL 75 | SPP_N | Entergy | 5546 | Rose Hill | Lang | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
Future 8 OL 75 | SPP_N | Entergy | 5546 | Lang | Iatan | 765 | 1 | 4000 | 95 | 5550000 | SPP_N | 0.4 | 0.8 | 210900000 | 421800000 | Satisfies SPP internal requirment
Future 8 OL 75 | SPP_N | Entergy | 5546 | LaCygna | Transformation | 345/500 | 2 | 1800 | 2 | 53000000 | SPP_N | 0.9 | 1.5 | 95400000 | 159000000 | Satisfies N-1 requirement
Future 8 OL 75 | SPP_N | Entergy | 5546 | LaCygna | Franks | 345 | 1 | 1800 | 150 | 2500000 | Entergy | 1 | 1.9 | 375000000 | 712500000 | Tie into Franks area
Future 8 OL 75 | SPP_N | Entergy | 5546 | LaCygna | Franks | 345 | 1 | 1800 | 150 | 2500000 | Entergy | 1 | 1.9 | 375000000 | 712500000 | Tie into Franks area
[12 empty] | Total Cost: |  | 4392700000 | 8576800000
Future 8 OL 75 | SPP-S | Entergy | 3430 | Sooner | Fort Smith | 765 | 1 | 4000 | 185 | 5550000 | SPP_S | 0.4 | 0.8 | 410700000 | 821400000 | Fort Smith is terminal for EES/AECI
Future 8 OL 75 | SPP-S | Entergy | 3430 | Fort Smith | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000 | 765/500kV Substation
Future 8 OL 76 | SPP-S | Entergy | 3430 | Fort Smith | Eldorado | 345 | 1 | 1800 | 240 | 2500000 | Entergy | 1 | 1.9 | 600000000 | 1140000000 | Tie into Eldorado area
Future 8 OL 77 | SPP-S | Entergy | 3430 | Fort Smith | ANO | 345 | 1 | 1800 | 80 | 2500000 | Entergy | 1 | 1.9 | 200000000 | 380000000 | Tie into ANO area
Future 8 OL 78 | SPP-S | Entergy | 3430 | ANO | Transformation | 500/345 | 1 |  | 2 | 22000000 | Entergy | 0.9 | 1.5 | 39600000 | 66000000 | Transformer for tie back to 500 kV system
Future 8 OL 79 | SPP-S | Entergy | 3430 | Woodward | Seminole | 765 | 1 | 4000 | 180 | 5550000 | SPP_S | 0.4 | 0.8 | 399600000 | 799200000 | Woodward - Seminole - NW Texarkana - Dolett Hills 765kV transmission line. Dolett Hills is terminal for EES/AECI
Future 8 OL 80 | SPP-S | Entergy | 3430 | Seminole | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 8 OL 81 | SPP-S | Entergy | 3430 | Seminole | NW Texarkana | 765 | 1 | 4000 | 180 | 5550000 | SPP_S | 0.4 | 0.8 | 399600000 | 799200000
Future 8 OL 82 | SPP-S | Entergy | 3430 | NW Texarkana | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 8 OL 83 | SPP-S | Entergy | 3430 | NW Texarkana | Dolett Hills | 765 | 1 | 4000 | 115 | 5550000 | SPP_S | 0.4 | 0.8 | 255300000 | 510600000
Future 8 OL 84 | SPP-S | Entergy | 3430 | Dolett Hills | Transformation | 765/345 | 0 |  | 1 | 53000000 | SPP_S | 0.9 | 1.5 | 47700000 | 79500000
Future 8 OL 85 | SPP-S | Entergy | 3430 | Dolett Hills | Sterlington | 345 | 1 | 1800 | 110 | 2500000 | Entergy | 1 | 1.9 | 275000000 | 522500000 | Tie into Sterlington area
Future 8 OL 86 | SPP-S | Entergy | 3430 | Dolett Hills | Nelson | 345 | 1 | 1800 | 125 | 2500000 | Entergy | 1 | 1.9 | 312500000 | 593750000 | Tie into Nelson area
Future 8 OL 87 | SPP-S | Entergy | 3430 | Sterlington | Transformation | 500/345 | 1 |  | 2 | 22000000 | Entergy | 0.9 | 1.5 | 39600000 | 66000000 | Transformer for tie back to 500 kV system
Future 8 OL 75 | SPP-S | Entergy | 3430 | Nelson | Transformation | 500/345 | 1 |  | 2 | 22000000 | Entergy | 0.9 | 1.5 | 39600000 | 66000000 | Transformer for tie back to 500 kV system
[12 empty] | Total Cost: |  | 3162300000 | 6082650000
Future 8 OL 75 | SPP |  |  | SPP 765kV Overlay |  | 765 |  |  | 1 | 8000000000 | SPP | 1 | 1 | 8000000000 | 8000000000 | This overlay is required to source the pipes for the future 2 xfer requirements