## 28S
Show Transfers - Sink Area |  |  |  |  | Show Transfers - Limiting Fac Area |  |  |  | Show Transfers - Outaged Fac Area
| NITC |  | FCITC |  |  |  | Rating | TDF |  |  | Limiting Element | [7 empty] | Outage Element
Transfer | (MW) |  | (MW) |  | Limiting Facility | Limiting PA | (MVA) | (%) | Outaged Facility | Cont, PA
SERC to FRCC | 4200 |  |  |  | Pine Grove-Sterling 230 kV 1 | SOCO (SERC) | 478 | 10.8 | None |  | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 2100 |  | ONEIL 230/138 kV 1 | FPL-JEA (FRCC) | 143 | 5.6 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 401/406 | 401 | 406 | FPL-JEA | FRCC | FRCC | FRCC | FPL-JEA (FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2200 |  | Kingsland-YULEE TRANSMISSION SUB 230 kV 1 | SOCO-FPL (SERC-FRCC) | 539 | 23.1 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2200 |  | Thalmann 1-Colerain 230 kV 1 | SOCO (SERC) | 596 | 17 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2300 |  | West Valdosta 230/115 kV 1 | SOCO (SERC) | 285 | 4 | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2300 |  | Colerain-Kingsland 2 230 kV 1 | SOCO (SERC) | 596 | 17.2 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2300 |  | BAKER TAP; TALQUIN CO-OP-MICCOSUKEE TAP; TALQUIN CO-OP 115 kV 1 | DEF (FRCC) | 84 | 3 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2400 |  | ONEIL 230/138 kV 1 | FPL-JEA (FRCC) | 143 | 3.6 | ONEIL 230/138 kV 1 | FPL (FRCC) | 401/406 | 401 | 406 | FPL-JEA | FRCC | FRCC | FRCC | FPL-JEA (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2500 |  | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 2598 | 93.1 | Hatch Duval Shunt Reactor-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2500 |  | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 2598 | 89.1 | Plant Hatch-Hatch Duval Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | KILLEARN TAP1; 115KV JQ LINE-BAKER TAP; TALQUIN CO-OP 115 kV 1 | DEF (FRCC) | 98 | 3 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2600 |  | Seminole Generation Station Collector Bus-HUDSON 230 kV 1 | SEC-FPL (FRCC) | 637 | 8.3 | RICE -ROBERTS 500 kV 1 | FPL (FRCC) | 412/401 | 412 | 401 | SEC-FPL | FRCC | FRCC | FRCC | SEC-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2700 |  | Hatch Duval Shunt Reactor-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 2598 | 80.1 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2800 |  | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 509 | 8.5 | Adel #5 (Linde)-North Tifton 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2800 |  | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 509 | 8.7 | Pine Grove-Adel #5 (Linde) 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3000 |  | Townsend-Zuta 115 kV 1 | SOCO (SERC) | 114 | 3.1 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3000 |  | Townsend-Zuta 115 kV 1 | SOCO (SERC) | 114 | 3.8 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3100 |  | RICE -PUTNAM 230 kV 1 | FPL (FRCC) | 588 | 10.7 | RICE -ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3100 |  | Loch Laurel-SUWANNEE RIVER SUBSTATION 115 kV 1 | SOCO-DEF (SERC-FRCC) | 126 | 3.3 | Pine Grove-Sterling 230 kV 1 | SOCO (SERC) | 346/402 | 346 | 402 | SOCO-DEF | SERC | FRCC | SERC-FRCC | SOCO-DEF (SERC-FRCC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3100 |  | Zuta-West Brunswick 115 kV 1 | SOCO (SERC) | 114 | 4.5 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3200 |  | Zuta-West Brunswick 115 kV 1 | SOCO (SERC) | 114 | 4.6 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3200 |  | HUDSON-PUTNAM 230 kV 1 | FPL (FRCC) | 637 | 9.1 | RICE -ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3300 |  | Zuta-West Brunswick 115 kV 1 | SOCO (SERC) | 114 | 4.2 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | MICCOSUKEE TAP; TALQUIN CO-OP-LLOYD ;TRI-COUNTY CO-OP TAP 115 kV 1 | DEF (FRCC) | 98 | 3.9 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3400 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 509 | 34.3 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | Loch Laurel-SUWANNEE RIVER SUBSTATION 115 kV 1 | SOCO-DEF (SERC-FRCC) | 126 | 4 | Sterling-SUWANNEE RIVER SUBSTATION 230 kV 1 | SOCO-DEF (SERC-FRCC) | 346/402 | 346 | 402 | SOCO-DEF | SERC | FRCC | SERC-FRCC | SOCO-DEF (SERC-FRCC) | 346/402 | 346 | 402 | SOCO-DEF | SERC | FRCC | SERC-FRCC | SOCO-DEF (SERC-FRCC)
|  |  | 3400 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 509 | 13.3 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 509 | 7.6 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | LLOYD ;TRI-COUNTY CO-OP TAP-JEFFERSON POWER PLANT TAP 115 kV 1 | DEF (FRCC) | 98 | 3.9 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3400 |  | Pine Grove 2 230/115 kV 1 | SOCO (SERC) | 280 | 3.8 | Pine Grove-Pine Grove 2 230 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | JEFFERSON POWER PLANT TAP-DRIFTON 115 kV 1 | DEF (FRCC) | 98 | 4.1 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3500 |  | FORT WHITE 115/69 kV 1 | DEF (FRCC) | 146 | 5.2 | FORT WHITE 230KV BUS SPLIT NORTH-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3500 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 509 | 10.9 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3500 |  | MICCOSUKEE TAP; TALQUIN CO-OP-LLOYD ;TRI-COUNTY CO-OP TAP 115 kV 1 | DEF (FRCC) | 98 | 3.8 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3500 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 509 | 10.7 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3500 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 509 | 11.2 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3500 |  | LLOYD ;TRI-COUNTY CO-OP TAP-JEFFERSON POWER PLANT TAP 115 kV 1 | DEF (FRCC) | 98 | 4.4 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3500 |  | JEFFERSON POWER PLANT TAP-DRIFTON 115 kV 1 | DEF (FRCC) | 98 | 4.3 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3500 |  | Hatch-Union School 230 kV 1 | SOCO (SERC) | 509 | 7 | Plant Hatch 500/230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3600 |  | Adel #5 (Linde)-Pine Grove 230 kV 1 | SOCO (SERC) | 509 | 7.6 | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3600 |  | Rayonier-Jesup North 115 kV 1 | SOCO (SERC) | 124 | 6.6 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3700 |  | Union School-Offerman 230 kV 1 | SOCO (SERC) | 509 | 7.6 | Plant Hatch 500/230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3900 |  | Bradfordville West 115kV Cap Bus-KILLEARN TAP1; 115KV JQ LINE 115 kV 1 | DEF (FRCC) | 150 | 10 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4000 |  | Bradfordville West 115kV Cap Bus-KILLEARN TAP1; 115KV JQ LINE 115 kV 1 | DEF (FRCC) | 150 | 3.8 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4000 |  | SUWANNEE RIVER SUBSTATION-SCOTT TAP; SUWANNEE VALLEY CO-OP 115 kV 1 | DEF (FRCC) | 126 | 3.9 | FORT WHITE 230KV BUS SPLIT NORTH-SUWANNEE RIVER SUBSTATION 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4000 |  | Adel #5 (Linde)-Pine Grove 230 kV 1 | SOCO (SERC) | 509 | 9.7 | Spain-Daisy Solar 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 4300 |  | FORT WHITE 230KV BUS SPLIT SOUTH-GINNIE 230 kV 1 | DEF (FRCC) | 436 | 29.2 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
NPCC to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 4300 |  | Plano (B)-Electric Jct (B) 345 kV 1 | CE (PJM) | 1341 | 3.4 | Electric Jct3 (R)-Plano (R) 345 kV 1 | CE (PJM) | 222/222 | 222 | 222 | CE | PJM | PJM | PJM | CE (PJM) | 222/222 | 222 | 222 | CE | PJM | PJM | PJM | CE (PJM)
|  |  | 4500 |  | LAMBTON_P1K1-Lambton 220 kV Z1 | IESO (NPCC) | 729 | 16 | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4500 |  | LAMBTON_P1K1-Lambton 220 kV Z1 | IESO (NPCC) | 729 | 16 | LAMBTON_L4D-St Clair 345 kV 1 | IESO-ITCT (NPCC-MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO)
|  |  | 4600 |  | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 845 | 17.6 | LAMBTON_L51D-St. Clair 220 kV 1 | IESO-ITCT (NPCC-MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO)
|  |  | 4600 |  | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 845 | 17.6 | LAMBTON_P1K1-Lambton 220 kV Z1 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4600 |  | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 845 | 17.6 | St Clair 345/220 kV 1 | ITCT (MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 219/219 | 219 | 219 | ITCT | MISO | MISO | MISO | ITCT (MISO)
|  |  | 4800 |  | Lambton-LAMBTON_L51D 220 kV 51 | IESO (NPCC) | 845 | 16.9 | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4800 |  | Lambton-LAMBTON_L51D 220 kV 51 | IESO (NPCC) | 845 | 16.9 | LAMBTON_L4D-St Clair 345 kV 1 | IESO-ITCT (NPCC-MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
PJM to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SERC to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 2600 |  | Daniel-Daniel Intermediate 230 kV 1 | SOCO (SERC) | 1000 | 6.6 | Daniel Intermediate-Daniel 230 kV 2 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | Daniel-Daniel Intermediate 230 kV 2 | SOCO (SERC) | 1000 | 6.6 | Daniel Intermediate-Daniel 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
SPP to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 1100 |  | 645458 S3458 3 345-645456 S3456 3 345 345 kV 1 | OPPD (SPP) | 956 | 4.2 | 645455 S3455 3 345-645740 S3740 3 345 345 kV 1 | OPPD (SPP) | 645/645 | 645 | 645 | OPPD | SPP | SPP | SPP | OPPD (SPP) | 645/645 | 645 | 645 | OPPD | SPP | SPP | SPP | OPPD (SPP)
|  |  | 2400 |  | 645740 S3740 3 345-645455 S3455 3 345 345 kV 1 | OPPD (SPP) | 1073 | 3.5 | 645456 S3456 3 345-645458 S3458 3 345 345 kV 1 | OPPD (SPP) | 645/645 | 645 | 645 | OPPD | SPP | SPP | SPP | OPPD (SPP) | 645/645 | 645 | 645 | OPPD | SPP | SPP | SPP | OPPD (SPP)
|  |  | 2900 |  | Bayou Labutte-Willow Glen 500 500 kV 1 | EES (MISO) | 1732 | 3.2 | Mcknight-Coly 500 500 kV 1 | EES (MISO) | 351/351 | 351 | 351 | EES | MISO | MISO | MISO | EES (MISO) | 351/351 | 351 | 351 | EES | MISO | MISO | MISO | EES (MISO)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
MISO to NPCC | 2400 |  |  |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 420 | 7.2 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 3300 |  |  |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 400 | 7.2 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4300 |  |  |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 403 | 7.4 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4700 |  |  |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 410 | 3.2 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 3200 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 584 | 11.1 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3200 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 584 | 11.1 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3300 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 5.7 | Maywood Bus Section 1-Saddle Brook Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 3400 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 11.3 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3400 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 11.3 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3800 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 584 | 9.9 | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 3800 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 740 | 11.3 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3800 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 740 | 11.4 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3900 |  | North Rockland-Buchanan South 345 kV 1 | NYISO (NPCC) | 2121 | 13.7 | Buchanan North-Ramapo 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3900 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 5.8 | Maywood Bus Section 1-Maywood Bus Section 2 230 kV Z | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4100 |  | Ladentown-North Rockland 345 kV 1 | NYISO (NPCC) | 2121 | 13 | Buchanan North-Ramapo 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4100 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 10.1 | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4500 |  | Lambton-LAMBTON_P1K1 220 kV Z1 | IESO (NPCC) | 729 | 16.9 | LAMBTON_L4D-St Clair 345 kV 1 | IESO-ITCT (NPCC-MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO)
|  |  | 4500 |  | Lambton-LAMBTON_P1K1 220 kV Z1 | IESO (NPCC) | 729 | 16.9 | LAMBTON_P2K2-LAMBTON_T7T8 220 kV S4 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4600 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 5.9 | New Milford-Maywood Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4600 |  | Saddle Brook Bus Section 2-Maywood Bus Section 1 230 kV 1 | PSE&G (PJM) | 650 | 6 | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4700 |  | LAMBTON_T7T8-LAMBTON_P2K2 220 kV S4 | IESO (NPCC) | 845 | 18.3 | St Clair 345/220 kV 1 | ITCT (MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 219/219 | 219 | 219 | ITCT | MISO | MISO | MISO | ITCT (MISO)
|  |  | 4700 |  | LAMBTON_T7T8-LAMBTON_P2K2 220 kV S4 | IESO (NPCC) | 845 | 18.3 | Lambton-LAMBTON_L51D 220 kV 51 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4700 |  | LAMBTON_T7T8-LAMBTON_P2K2 220 kV S4 | IESO (NPCC) | 845 | 18.3 | LAMBTON_L51D-St. Clair 220 kV 1 | IESO-ITCT (NPCC-MISO) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO)
|  |  | 4700 |  | Bergenfield Bus Section 1-New Milford 230 kV 1 | PSE&G (PJM) | 589 | 6 | Maywood Bus Section 1-Saddle Brook Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4800 |  | Waterman-KEITH_J5D_PS 230 kV 1 | ITCT-IESO (MISO-NPCC) | 415 | 6 | BRIGHTON_J20-Bright 220 kV 1 | IESO (NPCC) | 219/103 | 219 | 103 | ITCT-IESO | MISO | NPCC | MISO-NPCC | ITCT-IESO (MISO-NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4800 |  | Waterman-KEITH_J5D_PS 230 kV 1 | ITCT-IESO (MISO-NPCC) | 415 | 6 | KEITH_TS-Bright 220 kV Z1 | IESO (NPCC) | 219/103 | 219 | 103 | ITCT-IESO | MISO | NPCC | MISO-NPCC | ITCT-IESO (MISO-NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4900 |  | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 688 | 10.2 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4900 |  | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 688 | 10.1 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
PJM to NPCC | 2100 |  |  |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 420 | 8.1 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 2900 |  |  |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 400 | 8.1 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 3800 |  |  |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 403 | 8.3 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4100 |  |  |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 410 | 3.7 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 2800 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 584 | 12.3 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 2800 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 584 | 12.3 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 2900 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 6.5 | Maywood Bus Section 1-Saddle Brook Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 3000 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 12.6 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3000 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 12.6 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3400 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 740 | 12.6 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3400 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 740 | 12.6 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3400 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 6.5 | Maywood Bus Section 1-Maywood Bus Section 2 230 kV Z | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 3600 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 544 | 11.3 | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 3600 |  | North Rockland-Buchanan South 345 kV 1 | NYISO (NPCC) | 2121 | 14.7 | Buchanan North-Ramapo 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3800 |  | Ladentown-North Rockland 345 kV 1 | NYISO (NPCC) | 2121 | 13.9 | Buchanan North-Ramapo 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4000 |  | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 589 | 6.6 | New Milford-Maywood Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4100 |  | Saddle Brook Bus Section 2-Maywood Bus Section 1 230 kV 1 | PSE&G (PJM) | 650 | 6.7 | Leonia Bus Section 2-Bergenfield Bus Section 3 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4100 |  | Bergenfield Bus Section 1-New Milford 230 kV 1 | PSE&G (PJM) | 589 | 6.7 | Maywood Bus Section 1-Saddle Brook Bus Section 2 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4400 |  | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 688 | 11.2 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4400 |  | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 688 | 11.2 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4400 |  | Saddle Brook Bus Section 2-Maywood Bus Section 1 230 kV 1 | PSE&G (PJM) | 650 | 6.7 | Bergenfield Bus Section 2-Bergenfield Bus Section 3 230 kV Z | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4700 |  | Bergenfield Bus Section 1-New Milford 230 kV 1 | PSE&G (PJM) | 589 | 6.7 | Maywood Bus Section 1-Maywood Bus Section 2 230 kV Z | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4700 |  | North Rockland-Buchanan South 345 kV 1 | NYISO (NPCC) | 2121 | 14.1 | Buchanan North-Eastview 2 North 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4800 |  | Roseland-Cedar Grove 230 kV 1 | PSE&G (PJM) | 887 | 8.3 | Roseland-Williams Pipeline/Transco - Roseland Station 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4800 |  | Hawthorne Section 2-Waldwick Phase Shifter - E Line 230 kV 1 | PSE&G (PJM) | 750 | 13.6 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4800 |  | Hawthorne Section 2-Waldwick Phase Shifter - E Line 230 kV 1 | PSE&G (PJM) | 750 | 13.6 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4900 |  | Ladentown-North Rockland 345 kV 1 | NYISO (NPCC) | 2121 | 13.3 | Buchanan North-Eastview 2 North 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
MISO to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
NPCC to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 30 |  | Hanmer TS-Nobel 500 kV 1 | IESO (NPCC) | 1801 | 3.4 | Hanmer TS-Nobel 500 kV 1 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 1500 |  | Hanmer TS-Nobel 500 kV 1 | IESO (NPCC) | 1801 | 3.4 | Essa TS-Nobel 500 kV 1 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 1700 |  | Hanmer TS-Nobel 500 kV 1 | IESO (NPCC) | 1801 | 3.4 | Nobel-Nobel 500 kV 1 | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
SERC to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
FRCC to SERC | 3100 |  |  |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 656 | 9.9 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 3200 |  |  |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 476 | 7.7 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4300 |  |  |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 409 | 6.2 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4400 |  |  |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 476 | 7.2 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4900 |  |  |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 11.1 | None |  | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 150 |  | 409000 POLKPLNT 230-409050 PEBB 230 230 kV 2 | TECO (FRCC) | 729 | 3.5 | 409000 POLKPLNT 230-409060 PEBBLDLE682 230 230 kV 1 | TECO (FRCC) | 416/416 | 416 | 416 | TECO | FRCC | FRCC | FRCC | TECO (FRCC) | 416/416 | 416 | 416 | TECO | FRCC | FRCC | FRCC | TECO (FRCC)
|  |  | 1100 |  | Silver Springs North-MARTIN WEST 230 kV 1 | SEC-DEF (FRCC) | 485 | 8.8 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 412/402 | 412 | 402 | SEC-DEF | FRCC | FRCC | FRCC | SEC-DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 1200 |  | MARTIN WEST-Williston 230 kV 1 | DEF (FRCC) | 436 | 9.1 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 1700 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 436 | 9.5 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 1900 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 762 | 13.2 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2000 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 436 | 9.8 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2200 |  | CANOE CREEK-HOLOPAW 230KV BUS SPLIT 2 230 kV 1 | DEF (FRCC) | 492 | 3.2 | ANDYTOWN-Q 206 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2300 |  | 409000 POLKPLNT 230-409050 PEBB 230 230 kV 2 | TECO (FRCC) | 729 | 3.9 | 409050 PEBB 230-409060 PEBBLDLE682 230 230 kV Z1 | TECO (FRCC) | 416/416 | 416 | 416 | TECO | FRCC | FRCC | FRCC | TECO (FRCC) | 416/416 | 416 | 416 | TECO | FRCC | FRCC | FRCC | TECO (FRCC)
|  |  | 2400 |  | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 436 | 9.5 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2400 |  | CANOE CREEK-HOLOPAW 230KV BUS SPLIT 2 230 kV 1 | DEF (FRCC) | 492 | 3.2 | ORANGE RIVER 500/230 kV 1 ORANGE RIVER-998532 152615301531 230 230 kV 1 ORANGE RIVER FIRST AUTO TERTIARY 34.5/230 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2400 |  | CANOE CREEK-HOLOPAW 230KV BUS SPLIT 2 230 kV 1 | DEF (FRCC) | 492 | 3.2 | ORANGE RIVER-Q 206 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2400 |  | FORT WHITE 230KV BUS SPLIT NORTH 230/115 kV 1 | DEF (FRCC) | 336 | 7.6 | FORT WHITE 230KV BUS SPLIT NORTH-SUWANNEE RIVER SUBSTATION 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2600 |  | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 436 | 9.1 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2600 |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 14.1 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2700 |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 575 | 9.4 | BRONSON-Williston 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2700 |  | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 436 | 9.3 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2700 |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 575 | 10.9 | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2800 |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 575 | 10.6 | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2900 |  | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 436 | 9.3 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | GINNIE-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 436 | 9.7 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 9.2 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3200 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 762 | 12.4 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3300 |  | DALLAS-SILVER SPRINGS 230 kV 1 | DEF (FRCC) | 762 | 14.4 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3300 |  | GINNIE-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 436 | 8.7 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3300 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 6.1 | Yemassee-Mateeba 230 kV 1 | SC (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 344/344 | 344 | 344 | SC | SERC | SERC | SERC | SC (SERC)
|  |  | 3500 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 762 | 12.5 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3500 |  | QUASAR-BRADFORD AUTO#2 230 kV 1 | FPL (FRCC) | 402 | 7.7 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.2 | WEST NASSAU TAP-DUVAL 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.2 | WEST NASSAU TAP-MILLS 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 6.3 | Canadys-Yemassee 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 3700 |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 575 | 10 | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3700 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 436 | 6.2 | Deerhaven Unit #2 22/138 kV 1 | GVL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 404/404 | 404 | 404 | GVL | FRCC | FRCC | FRCC | GVL (FRCC)
|  |  | 3700 |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 575 | 10 | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3700 |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 575 | 8.9 | BRONSON-Williston 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3800 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 8.1 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 11.4 | DELTONA-SANFORD OUTSIDE 230 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.3 | YULEE-MILLS 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4000 |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 12.3 | OSTEEN-GACO 230 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4100 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 4.9 | NORTHSIDE 230/18 kV 1 | JEA (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 406/406 | 406 | 406 | JEA | FRCC | FRCC | FRCC | JEA (FRCC)
|  |  | 4100 |  | Yemassee - Yemassee Pseudo Tie Bus-Yemassee 230 kV Z1 | SCEG-SC (SERC) | 797 | 4.8 | Bluffton-Purrysburg 230 kV 1 | SC (SERC) | 343/344 | 343 | 344 | SCEG-SC | SERC | SERC | SERC | SCEG-SC (SERC) | 344/344 | 344 | 344 | SC | SERC | SERC | SERC | SC (SERC)
|  |  | 4200 |  | BARNA-NORRIS 230 kV 1 | FPL (FRCC) | 402 | 4.8 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4200 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 5.2 | Yemassee - Yemassee Pseudo Tie Bus-Yemassee 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 4200 |  | Seminole Generation Station Collector Bus-TITANIUM 230 kV 1 | SEC-FPL (FRCC) | 637 | 10.4 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 412/401 | 412 | 401 | SEC-FPL | FRCC | FRCC | FRCC | SEC-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4200 |  | FORT WHITE 230KV BUS SPLIT NORTH 230/115 kV 1 | DEF (FRCC) | 336 | 17.2 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 4200 |  | TITANIUM-GREEN COVE SPRINGS (FPL) 230 kV 1 | FPL (FRCC) | 637 | 10.5 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4300 |  | RICE -QUASAR 230 kV 1 | FPL (FRCC) | 402 | 7.9 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | VOLUSIA -LPGA 230 kV 1 | FPL (FRCC) | 478 | 9.8 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | VOLUSIA -LPGA 230 kV 1 | FPL (FRCC) | 478 | 11.2 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | FORT WHITE 230KV BUS SPLIT NORTH 230/115 kV 1 | DEF (FRCC) | 336 | 3.6 | PERRY-SUWANNEE RIVER SUBSTATION 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4500 |  | GREEN COVE SPRINGS (FPL)-SPRINGBANK 230 kV 1 | FPL (FRCC) | 637 | 10.5 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4600 |  | YULEE TRANSMISSION SUB-Kingsland 230 kV 1 | FPL-SOCO (FRCC-SERC) | 539 | 17.4 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 401/346 | 401 | 346 | FPL-SOCO | FRCC | SERC | FRCC-SERC | FPL-SOCO (FRCC-SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 4700 |  | DALLAS-SILVER SPRINGS 230 kV 1 | DEF (FRCC) | 762 | 12.9 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | LPGA-FLAGLER BEACH 230 kV 1 | FPL (FRCC) | 502 | 9.7 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | LPGA-FLAGLER BEACH 230 kV 1 | FPL (FRCC) | 502 | 11.1 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | STEPDOWN 138kV (FPUC) 138/230 kV 1 | FPL (FRCC) | 101 | 3.5 | ONEIL 230/138 kV 1 | FPL-JEA (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/406 | 401 | 406 | FPL-JEA | FRCC | FRCC | FRCC | FPL-JEA (FRCC)
|  |  | 4700 |  | FORT WHITE 230KV BUS SPLIT NORTH-SUWANNEE RIVER SUBSTATION 230 kV 1 | DEF (FRCC) | 575 | 9.5 | FORT WHITE 115/230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4700 |  | TOCOI -MILLCREEK 230 kV 1 | FPL (FRCC) | 588 | 10.3 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | BARNA -BARNA 230 kV 1 | FPL (FRCC) | 446 | 5 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4800 |  | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 436 | 9.6 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 4900 |  | PUTNAM -TOCOI 230 kV 1 | FPL (FRCC) | 588 | 8.5 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4900 |  | SILVER SPRINGS-DEARMIN 230 kV 1 | DEF (FRCC) | 575 | 9.2 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4900 |  | SUWANNEE RIVER SUBSTATION-Loch Laurel 115 kV 1 | DEF-SOCO (FRCC-SERC) | 126 | 4 | Pine Grove-Sterling 230 kV 1 | SOCO (SERC) | 402/346 | 402 | 346 | DEF-SOCO | FRCC | SERC | FRCC-SERC | DEF-SOCO (FRCC-SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 4900 |  | FLORATAM-HIGHRIDGE 230 kV 1 | FPL (FRCC) | 402 | 5.8 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
MISO to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
PJM to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SPP to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
MISO to SPP | 4100 |  |  |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 12.9 | None |  | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 1300 |  | Russellville East-Russellville South 161 kV 1 | EES-EAI (MISO) | 446 | 5.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1400 |  | Russellville South-505508 DARDANE5 161 161 kV 1 | EES-EAI-SWPA (MISO-SPP) | 396 | 5.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/515 | 327 | 515 | EES-EAI-SWPA | MISO | SPP | MISO-SPP | EES-EAI-SWPA (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1800 |  | Russellville North-Russellville East 161 kV 1 | EES-EAI (MISO) | 396 | 3.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1800 |  | Russellville East-Russellville East 161 kV R1 | EES-EAI (MISO) | 396 | 3.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 2300 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 12.7 | 532797 WOLFCRK7 345 345/25 kV 1 | OKGE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3000 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 12.1 | 515224 MUSKOGE7 345 345/24 kV 1 | OKGE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3000 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 12.1 | 515224 MUSKOGE7 345 345/18 kV 1 | OKGE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 4100 |  | London-Russellville North 161 kV 1 | EES-EAI (MISO) | 518 | 3.7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4300 |  | Danville-507195 MAGZREC5 161 161 kV 1 | EES-EAI-AEPW (MISO-SPP) | 335 | 4.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/520 | 327 | 520 | EES-EAI-AEPW | MISO | SPP | MISO-SPP | EES-EAI-AEPW (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4400 |  | Lebanon #2-Coffman 161 kV 1 | AECI (SERC) | 261 | 3.8 | Franks-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 4400 |  | Lebanon #2-Coffman 161 kV 1 | AECI (SERC) | 261 | 3.6 | Huben-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC |  | AECI () | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
SERC to SPP | 3100 |  |  |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 16.7 | None |  | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 950 |  | Russellville East-Russellville South 161 kV 1 | EES-EAI (MISO) | 446 | 7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1000 |  | Russellville South-505508 DARDANE5 161 161 kV 1 | EES-EAI-SWPA (MISO-SPP) | 396 | 6.7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/515 | 327 | 515 | EES-EAI-SWPA | MISO | SPP | MISO-SPP | EES-EAI-SWPA (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1200 |  | 505508 DARDANE5 161-505514 CLARKSV5 161 161 kV 1 | SWPA (SPP) | 224 | 3.9 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 515/515 | 515 | 515 | SWPA | SPP | SPP | SPP | SWPA (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1300 |  | Russellville North-Russellville East 161 kV 1 | EES-EAI (MISO) | 396 | 4.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1300 |  | Russellville East-Russellville East 161 kV R1 | EES-EAI (MISO) | 396 | 4.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 1700 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 17 | 532797 WOLFCRK7 345 345/25 kV 1 | WERE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 536/536 | 536 | 536 | WERE | SPP | SPP | SPP | WERE (SPP)
|  |  | 2200 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 16.3 | 515224 MUSKOGE7 345 345/24 kV 1 | OKGE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 2200 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 16.3 | 515224 MUSKOGE7 345 345/18 kV 1 | OKGE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 2700 |  | Daniel-Daniel Intermediate 230 kV 1 | SOCO (SERC) | 1000 | 6.6 | Daniel Intermediate-Daniel 230 kV 2 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2700 |  | Daniel-Daniel Intermediate 230 kV 2 | SOCO (SERC) | 1000 | 6.6 | Daniel Intermediate-Daniel 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2900 |  | 505522 VAN BUR5 161-Liberty Tap 161 kV 1 | SWPA-AECI (SPP-SERC) | 191 | 3.7 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 515/330 | 515 | 330 | SWPA-AECI | SPP | SERC | SPP-SERC | SWPA-AECI (SPP-SERC) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3100 |  | London-Russellville North 161 kV 1 | EES-EAI (MISO) | 518 | 4.7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI (MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO)
|  |  | 3200 |  | Liberty Tap-Akins 161 kV 1 | AECI (SERC) | 191 | 3.7 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3200 |  | 515527 HWY59TP5 161-512655 TAHLQH 5 161 161 kV 1 | OKGE-GRDA (SPP) | 167 | 3.2 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 524/523 | 524 | 523 | OKGE-GRDA | SPP | SPP | SPP | OKGE-GRDA (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3300 |  | Akins-505550 SALISAW5 161 161 kV 1 | AECI-SWPA (SERC-SPP) | 191 | 3.7 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 330/515 | 330 | 515 | AECI-SWPA | SERC | SPP | SERC-SPP | AECI-SWPA (SERC-SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3300 |  | Danville-507195 MAGZREC5 161 161 kV 1 | EES-EAI-AEPW (MISO-SPP) | 335 | 5 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/520 | 327 | 520 | EES-EAI-AEPW | MISO | SPP | MISO-SPP | EES-EAI-AEPW (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3500 |  | 507195 MAGZREC5 161-507190 NMAGZIN5 161 161 kV 1 | AEPW (SPP) | 335 | 5.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 520/520 | 520 | 520 | AEPW | SPP | SPP | SPP | AEPW (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3500 |  | Huben 345/161 kV 1 | AECI (SERC) | 392 | 3.2 | Huben-Morgan 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 3600 |  | St. Joe-Everton Road 161 kV 1 | EES-EAI (MISO) | 363 | 3.3 | South Lead Hill-505461 BULL SH W5 161 161 kV 1 | EES-EAI (MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO)
|  |  | 3600 |  | Hilltop-St. Joe 161 kV 1 | EES-EAI (MISO) | 363 | 3.4 | South Lead Hill-505461 BULL SH W5 161 161 kV 1 | EES-EAI (MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO)
|  |  | 3600 |  | 515301 FTSMTHW5 161-515306 ARKOMA 5 161 161 kV 1 | OKGE (SPP) | 359 | 3.5 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3600 |  | Hilltop-St. Joe 161 kV 1 | EES-EAI (MISO) | 363 | 4.7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3600 |  | St. Joe-Everton Road 161 kV 1 | EES-EAI (MISO) | 363 | 3.3 | Clevenger Cove-South Lead Hill 161 kV 1 | AECI-EES-EAI (SERC-MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 330/327 | 330 | 327 | AECI-EES-EAI | SERC | MISO | SERC-MISO | AECI-EES-EAI (SERC-MISO)
|  |  | 3600 |  | Hilltop-St. Joe 161 kV 1 | EES-EAI (MISO) | 363 | 3.2 | Clevenger Cove-South Lead Hill 161 kV 1 | AECI-EES-EAI (SERC-MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 330/327 | 330 | 327 | AECI-EES-EAI | SERC | MISO | SERC-MISO | AECI-EES-EAI (SERC-MISO)
|  |  | 3600 |  | St. Joe-Everton Road 161 kV 1 | EES-EAI (MISO) | 363 | 4.6 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3600 |  | Lebanon #2-Coffman 161 kV 1 | AECI (SERC) | 261 | 3.9 | Franks-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 3700 |  | Lebanon #2-Coffman 161 kV 1 | AECI (SERC) | 261 | 4.5 | Huben-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 3700 |  | Montgomery 345KV 345 kV Bus A-McCredie Tap 345 kV MTGY-OVER-5 Tap Point 345 kV 1 | AMMO (MISO) | 1102 | 9.9 | Thomas Hill-Thomas Hill GSU #3 High Side 345 kV 1 | AECI (SERC) | 356/356 | 356 | 356 | AMMO | MISO | MISO | MISO | AMMO (MISO) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 3700 |  | Montgomery 345KV 345 kV Bus A-McCredie Tap 345 kV MTGY-OVER-5 Tap Point 345 kV 1 | AMMO (MISO) | 1102 | 9.8 | Thomas Hill Generator #3 24/345 kV 1 | AECI (SERC) | 356/356 | 356 | 356 | AMMO | MISO | MISO | MISO | AMMO (MISO) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 3800 |  | Everton Road-Harrison East 161 kV 1 | EES-EAI (MISO) | 363 | 3.9 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3800 |  | Everton Road-Harrison East 161 kV 1 | EES-EAI (MISO) | 363 | 3.5 | South Lead Hill-505461 BULL SH W5 161 161 kV 1 | EES-EAI (MISO) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO)
|  |  | 3800 |  | 998087 FTSMITH1 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 693 | 9 | 532797 WOLFCRK7 345 345/25 kV 1 | WERE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 536/536 | 536 | 536 | WERE | SPP | SPP | SPP | WERE (SPP)
|  |  | 3800 |  | 515306 ARKOMA 5 161-515308 3RDST 5 161 161 kV 1 | OKGE (SPP) | 335 | 3.4 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3800 |  | 515406 ADABELL5 161-515339 VBI 5 161 161 kV 1 | OKGE (SPP) | 223 | 4 | 515224 MUSKOGE7 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 3800 |  | 515305 FTSMITH8 500 500/345 kV 1 | OKGE (SPP) | 693 | 8.7 | 532797 WOLFCRK7 345 345/25 kV 1 | WERE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 536/536 | 536 | 536 | WERE | SPP | SPP | SPP | WERE (SPP)
|  |  | 3900 |  | Everton Road-Harrison East 161 kV 1 | EES-EAI (MISO) | 363 | 3 | Clevenger Cove-505472 TABLE R5 161 161 kV 1 | AECI (SERC) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 4100 |  | Coffman-Huben 161 kV 1 | AECI (SERC) | 261 | 4.8 | Franks-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 4200 |  | Coffman-Huben 161 kV 1 | AECI (SERC) | 261 | 4.7 | Huben-Franks Reactor 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 4200 |  | Mansfield-Logan 161 kV 1 | AECI (SERC) | 189 | 3.2 | Huben-Morgan 345 kV 1 | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC) | 330/330 | 330 | 330 | AECI | SERC | SERC | SERC | AECI (SERC)
|  |  | 4200 |  | McCredie Tap 345 kV MTGY-OVER-5 Tap Point-Overton 345 kV Bus 1 345 kV 1 | AMMO (MISO) | 956 | 11.9 | 532797 WOLFCRK7 345 345/25 kV 1 | WERE (SPP) | 356/356 | 356 | 356 | AMMO | MISO | MISO | MISO | AMMO (MISO) | 536/536 | 536 | 536 | WERE | SPP | SPP | SPP | WERE (SPP)
|  |  | 4200 |  | Plano (B)-Electric Jct (B) 345 kV 1 | CE (PJM) | 1341 | 3.6 | Electric Jct3 (R)-Plano (R) 345 kV 1 | CE (PJM) | 222/222 | 222 | 222 | CE | PJM | PJM | PJM | CE (PJM) | 222/222 | 222 | 222 | CE | PJM | PJM | PJM | CE (PJM)
|  |  | 4200 |  | 998087 FTSMITH1 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 693 | 9 | 515224 MUSKOGE7 345 345/24 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 4200 |  | 998087 FTSMITH1 345-515302 FTSMITH7 345 345 kV 1 | OKGE (SPP) | 693 | 9 | 515224 MUSKOGE7 345 345/18 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 4300 |  | 515305 FTSMITH8 500 500/345 kV 1 | OKGE (SPP) | 693 | 8.9 | 515224 MUSKOGE7 345 345/24 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 4300 |  | 515305 FTSMITH8 500 500/345 kV 1 | OKGE (SPP) | 693 | 8.9 | 515224 MUSKOGE7 345 345/18 kV 1 | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP) | 524/524 | 524 | 524 | OKGE | SPP | SPP | SPP | OKGE (SPP)
|  |  | 4700 |  | Montgomery 345KV 345 kV Bus A-McCredie Tap 345 kV MTGY-OVER-5 Tap Point 345 kV 1 | AMMO (MISO) | 1102 | 11.6 | Palmyra Tap 345 kV SPCK-SUBT-1 Tap Point-Spencer Creek 345 kV Bus V3-V5 (MTGY-SPCK-1) 345 kV 1 | AMMO (MISO) | 356/356 | 356 | 356 | AMMO | MISO | MISO | MISO | AMMO (MISO) | 356/356 | 356 | 356 | AMMO | MISO | MISO | MISO | AMMO (MISO)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility

## 28W
Show Transfers - Sink Area |  |  |  |  | Show Transfers - Limiting Fac Area |  |  |  | Show Transfers - Outaged Fac Area
| NITC |  | FCITC |  |  |  | Rating | TDF |  |  | Limiting Element | [7 empty] | Outage Element
Transfer | (MW) |  | (MW) |  | Limiting Facility | Limiting PA | (MVA) | (%) | Outaged Facility | Cont, PA
SERC to FRCC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 2100 |  | BAKER TAP; TALQUIN CO-OP-MICCOSUKEE TAP; TALQUIN CO-OP 115 kV 1 | DEF (FRCC) | 101 | 3.3 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2100 |  | KILLEARN TAP1; 115KV JQ LINE-BAKER TAP; TALQUIN CO-OP 115 kV 1 | DEF (FRCC) | 111 | 3.2 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2200 |  | North Tifton 500/230 kV 1 | SOCO (SERC) | 1536 | 5.5 | Raccoon Creek 500/230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2200 |  | ONEIL 230/138 kV 1 | FPL-JEA (FRCC) | 143 | 6 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 401/406 | 401 | 406 | FPL-JEA | FRCC | FRCC | FRCC | FPL-JEA (FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2600 |  | Kingsland-YULEE TRANSMISSION SUB 230 kV 1 | SOCO-FPL (SERC-FRCC) | 607 | 22.8 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2600 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 561 | 10.6 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 561 | 10.9 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 561 | 13.7 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 561 | 12 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2600 |  | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 2598 | 98 | Hatch Duval Shunt Reactor-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 2700 |  | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 2598 | 98.4 | Plant Hatch-Hatch Duval Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2700 |  | Vidalia -Hatch Site 2 230 kV 1 | SOCO (SERC) | 561 | 12.8 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2700 |  | Bonaire Primary 2-Kathleen 230 kV 1 | SOCO (SERC) | 477 | 3.8 | Bonaire-Plant Hatch 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2700 |  | Hatch Site 2-Hatch 230 kV 1 | SOCO (SERC) | 561 | 10.1 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2800 |  | Rayonier-Jesup North 115 kV 1 | SOCO (SERC) | 137 | 4.6 | Thalmann McCall Road Shunt Reactor-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2800 |  | Rayonier-Jesup North 115 kV 1 | SOCO (SERC) | 137 | 5.2 | Thalmann-Thalmann McCall Road Shunt Reactor 500 kV Z1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 2900 |  | Rayonier-Jesup North 115 kV 1 | SOCO (SERC) | 137 | 3.1 | West McIntosh-McCall Road 500 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3100 |  | MICCOSUKEE TAP; TALQUIN CO-OP-LLOYD ;TRI-COUNTY CO-OP TAP 115 kV 1 | DEF (FRCC) | 111 | 4.3 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | Bradfordville West 115kV Cap Bus-KILLEARN TAP1; 115KV JQ LINE 115 kV 1 | DEF (FRCC) | 150 | 4.5 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 561 | 8.3 | Adel #5 (Linde)-North Tifton 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3200 |  | LLOYD ;TRI-COUNTY CO-OP TAP-JEFFERSON POWER PLANT TAP 115 kV 1 | DEF (FRCC) | 111 | 4.9 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | JEFFERSON POWER PLANT TAP-DRIFTON 115 kV 1 | DEF (FRCC) | 111 | 4.9 | FLORIDA GAS TRANSMISSION-ST. MARKS EAST 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | MICCOSUKEE TAP; TALQUIN CO-OP-LLOYD ;TRI-COUNTY CO-OP TAP 115 kV 1 | DEF (FRCC) | 111 | 4.5 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | West Valdosta-Pine Grove 2 230 kV 1 | SOCO (SERC) | 561 | 11 | Pine Grove-Adel #5 (Linde) 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3300 |  | Bradfordville West 115kV Cap Bus-KILLEARN TAP1; 115KV JQ LINE 115 kV 1 | DEF (FRCC) | 150 | 4.9 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3300 |  | LLOYD ;TRI-COUNTY CO-OP TAP-JEFFERSON POWER PLANT TAP 115 kV 1 | DEF (FRCC) | 111 | 3.6 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3300 |  | JEFFERSON POWER PLANT TAP-DRIFTON 115 kV 1 | DEF (FRCC) | 111 | 3.8 | FLORIDA GAS TRANSMISSION-PERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3300 |  | ONEIL 230/138 kV 1 | FPL-JEA (FRCC) | 143 | 6.3 | YULEE-YULEE TRANSMISSION SUB 230 kV 1 | FPL (FRCC) | 401/406 | 401 | 406 | FPL-JEA | FRCC | FRCC | FRCC | FPL-JEA (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3300 |  | North Tifton -Adel #5 (Linde) 230 kV 1 | SOCO (SERC) | 561 | 7 | East Moultrie-East Berlin 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3400 |  | North Tifton -Adel #5 (Linde) 230 kV 1 | SOCO (SERC) | 561 | 7.8 | West Valdosta-East Berlin 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3500 |  | Adel #5 (Linde)-Pine Grove 230 kV 1 | SOCO (SERC) | 561 | 7.5 | East Moultrie-East Berlin 230 kV 1 | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC) | 346/346 | 346 | 346 | SOCO | SERC | SERC | SERC | SOCO (SERC)
|  |  | 3900 |  | RICE -PUTNAM 230 kV 1 | FPL (FRCC) | 588 | 18.5 | RICE -ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
NPCC to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 4900 |  | KEITH_J5D_PS-Waterman 230 kV 1 | IESO-ITCT (NPCC-MISO) | 454 | 9.1 | Belle River-St Clair 345 kV 1 | ITCT (MISO) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO) | 219/219 | 219 | 219 | ITCT | MISO | MISO | MISO | ITCT (MISO)
|  |  | 4900 |  | KEITH_J5D_PS-Waterman 230 kV 1 | IESO-ITCT (NPCC-MISO) | 454 | 8 | Stephens-Caniff 345 kV 1 | ITCT (MISO) | 103/219 | 103 | 219 | IESO-ITCT | NPCC | MISO | NPCC-MISO | IESO-ITCT (NPCC-MISO) | 219/219 | 219 | 219 | ITCT | MISO | MISO | MISO | ITCT (MISO)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
PJM to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SERC to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SPP to MISO | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
MISO to NPCC | 4200 |  |  |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 460 | 7.3 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4700 |  |  |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 439 | 7.4 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 4300 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 11.4 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4300 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 11.4 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4300 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 615 | 11.3 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4300 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 615 | 11.2 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4800 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 10.2 | New Milford-Hillsdale 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4900 |  | Waterman-KEITH_J5D_PS 230 kV 1 | ITCT-IESO (MISO-NPCC) | 454 | 6.2 | BRIGHTON_J20-Bright 220 kV 1 | IESO (NPCC) | 219/103 | 219 | 103 | ITCT-IESO | MISO | NPCC | MISO-NPCC | ITCT-IESO (MISO-NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 4900 |  | Waterman-KEITH_J5D_PS 230 kV 1 | ITCT-IESO (MISO-NPCC) | 454 | 6.2 | KEITH_TS-Bright 220 kV Z1 | IESO (NPCC) | 219/103 | 219 | 103 | ITCT-IESO | MISO | NPCC | MISO-NPCC | ITCT-IESO (MISO-NPCC) | 103/103 | 103 | 103 | IESO | NPCC | NPCC | NPCC | IESO (NPCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
PJM to NPCC | 3600 |  |  |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 460 | 8.6 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4000 |  |  |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 439 | 8.5 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 4500 |  |  |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 442 | 8.7 | None |  | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 3700 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 13 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3700 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 13 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 3700 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 615 | 12.9 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 3800 |  | Jackson Road-Hinchmans Ave Section 4 230 kV 1 | PSE&G (PJM) | 615 | 12.9 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4100 |  | Hinchmans Ave Section 1-Hawthorne Section 1 230 kV 1 | PSE&G (PJM) | 570 | 12.7 | Hillsdale-Waldwick Phase Shifter - F Line 230 kV 1 | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM)
|  |  | 4700 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 800 | 13.2 | Ramapo 500/345 kV 1 | NYISO (NPCC) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 4700 |  | Cedar Grove-Jackson Road 230 kV 1 | PSE&G (PJM) | 800 | 13.2 | Ramapo-Hopatcong 500 kV 1 | NYISO-PJM (NPCC-PJM) | 231/231 | 231 | 231 | PSE&G | PJM | PJM | PJM | PSE&G (PJM) | 102/225 | 102 | 225 | NYISO-PJM | NPCC | PJM | NPCC-PJM | NYISO-PJM (NPCC-PJM)
|  |  | 4800 |  | North Rockland-Buchanan South 345 kV 1 | NYISO (NPCC) | 2121 | 14.8 | Buchanan North-Ramapo 345 kV 1 | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC) | 102/102 | 102 | 102 | NYISO | NPCC | NPCC | NPCC | NYISO (NPCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
MISO to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
NPCC to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SERC to PJM | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 2600 |  | Volunteer-Phipps Bend 500 kV 1 | TVA (SERC) | 1900 | 13.6 | Rogers Road 500 kV-Greenville 500 kV 500 kV 1 | DVP (PJM) | 347/347 | 347 | 347 | TVA | SERC | SERC | SERC | TVA (SERC) | 345/345 | 345 | 345 | DVP | PJM | PJM | PJM | DVP (PJM)
|  |  | 2800 |  | Volunteer-Phipps Bend 500 kV 1 | TVA (SERC) | 1900 | 13.7 | Lackawanna-Lackawanna Energy Center 230 kV 1 | PL (PJM) | 347/347 | 347 | 347 | TVA | SERC | SERC | SERC | TVA (SERC) | 229/229 | 229 | 229 | PL | PJM | PJM | PJM | PL (PJM)
|  |  | 2800 |  | Volunteer-Phipps Bend 500 kV 1 | TVA (SERC) | 1900 | 13.4 | Front Royal 500 kV-Warren County 500 kV 500 kV 1 | DVP (PJM) | 347/347 | 347 | 347 | TVA | SERC | SERC | SERC | TVA (SERC) | 345/345 | 345 | 345 | DVP | PJM | PJM | PJM | DVP (PJM)
|  |  | 2900 |  | Volunteer-Phipps Bend 500 kV 1 | TVA (SERC) | 1900 | 13.6 | Peach Bottom 1 South-Delta 500 kV 1 | PJM (PJM) | 347/347 | 347 | 347 | TVA | SERC | SERC | SERC | TVA (SERC) | 225/225 | 225 | 225 | PJM | PJM | PJM | PJM | PJM (PJM)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
FRCC to SERC | 4000 |  |  |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 573 | 8 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4100 |  |  |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 474 | 4.7 | None |  | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
| 4200 |  |  |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 9.2 | None |  | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
| 4300 |  |  |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 790 | 9.5 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4500 |  |  |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 8.2 | None |  | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
| 4600 |  |  |  | FORT WHITE 230KV BUS SPLIT NORTH 230/115 kV 1 | DEF (FRCC) | 336 | 3.4 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 4800 |  |  |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 476 | 9 | None |  | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
| 5000 | + |  |  | No other limit found at 5000 MW |  |  |  | None
|  |  | 1200 |  | MARTIN WEST-Williston 230 kV 1 | DEF (FRCC) | 524 | 8.8 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 1300 |  | SANFORD INSIDE-GACO 230 kV 1 | FPL (FRCC) | 588 | 12.9 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 1400 |  | Silver Springs North-MARTIN WEST 230 kV 1 | SEC-DEF (FRCC) | 626 | 8.6 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 412/402 | 412 | 402 | SEC-DEF | FRCC | FRCC | FRCC | SEC-DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 1800 |  | Yemassee - Yemassee Pseudo Tie Bus-Yemassee 230 kV Z1 | SCEG-SC (SERC) | 797 | 5.1 | Bluffton-Purrysburg 230 kV 1 | SC (SERC) | 343/344 | 343 | 344 | SCEG-SC | SERC | SERC | SERC | SCEG-SC (SERC) | 344/344 | 344 | 344 | SC | SERC | SERC | SERC | SC (SERC)
|  |  | 2100 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 524 | 9 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2100 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 6.7 | Yemassee-Mateeba 230 kV 1 | SC (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 344/344 | 344 | 344 | SC | SERC | SERC | SERC | SC (SERC)
|  |  | 2500 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 9.7 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2500 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 524 | 9.6 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2500 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 871 | 13.2 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2600 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 6.7 | Canadys-Yemassee 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 2600 |  | QUASAR-BRADFORD AUTO#2 230 kV 1 | FPL (FRCC) | 402 | 8.1 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2600 |  | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 524 | 9.2 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2700 |  | RICE -QUASAR 230 kV 1 | FPL (FRCC) | 402 | 7.6 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2800 |  | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 524 | 9 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2800 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 8.6 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 2800 |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 650 | 10.7 | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 2900 |  | BRONSON-NEWBERRY 230 kV 1 | DEF (FRCC) | 650 | 10.7 | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3000 |  | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 508 | 5.6 | Yemassee - Yemassee Pseudo Tie Bus-Yemassee 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 3100 |  | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 524 | 9.2 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3100 |  | BARNA-NORRIS 230 kV 1 | FPL (FRCC) | 402 | 5.5 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3100 |  | VOLUSIA -LPGA 230 kV 1 | FPL (FRCC) | 478 | 9.8 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3200 |  | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 524 | 9.2 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3200 |  | MILLCREEK-ORANGEDALE 230 kV 1 | FPL (FRCC) | 402 | 5.1 | NORTHSIDE 230/18 kV 1 | JEA (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 406/406 | 406 | 406 | JEA | FRCC | FRCC | FRCC | JEA (FRCC)
|  |  | 3300 |  | VOLUSIA -LPGA 230 kV 1 | FPL (FRCC) | 478 | 11.3 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3500 |  | LPGA-FLAGLER BEACH 230 kV 1 | FPL (FRCC) | 502 | 10.2 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3500 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.2 | WEST NASSAU TAP-DUVAL 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3500 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.2 | WEST NASSAU TAP-MILLS 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | GINNIE-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 524 | 9.4 | FORT WHITE 230KV BUS SPLIT SOUTH-NEWBERRY 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3600 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 871 | 14.9 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | BARNA -BARNA 230 kV 1 | FPL (FRCC) | 446 | 5.8 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3600 |  | LPGA-FLAGLER BEACH 230 kV 1 | FPL (FRCC) | 502 | 9.8 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3700 |  | Seminole Generation Station Collector Bus-TITANIUM 230 kV 1 | SEC-FPL (FRCC) | 637 | 11.1 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 412/401 | 412 | 401 | SEC-FPL | FRCC | FRCC | FRCC | SEC-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3700 |  | TITANIUM-GREEN COVE SPRINGS (FPL) 230 kV 1 | FPL (FRCC) | 637 | 11.7 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3700 |  | GINNIE-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 524 | 9.1 | NEWBERRY-BRONSON 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 3800 |  | NASSAU 138/230 kV 1 | JEA-FPL (FRCC) | 143 | 3.3 | YULEE-MILLS 230 kV 1 | FPL (FRCC) | 406/401 | 406 | 401 | JEA-FPL | FRCC | FRCC | FRCC | JEA-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | TOCOI -MILLCREEK 230 kV 1 | FPL (FRCC) | 588 | 10.6 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | CENTRAL FLORIDA-DALLAS 230 kV 1 | DEF (FRCC) | 871 | 14.1 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | PUTNAM -TOCOI 230 kV 1 | FPL (FRCC) | 588 | 7.8 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | BARNA-NORRIS 230 kV 1 | FPL (FRCC) | 402 | 6 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | GREEN COVE SPRINGS (FPL)-SPRINGBANK 230 kV 1 | FPL (FRCC) | 637 | 12.4 | DUVAL -RICE 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 3900 |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 650 | 10.6 | ARCHER-HAILE TAP 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4000 |  | FLAGLER BEACH-BUNNELL 230 kV 1 | FPL (FRCC) | 502 | 11 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4000 |  | SANFORD OUTSIDE-DELTONA 230 kV 1 | FPL (FRCC) | 526 | 6.1 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4000 |  | NEWBERRY-FORT WHITE 230KV BUS SPLIT SOUTH 230 kV 1 | DEF (FRCC) | 650 | 10.9 | HAILE TAP-GINNIE 230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4100 |  | Jasper-Yemassee 230 kV 1 | SCEG (SERC) | 1016 | 7.2 | Yemassee-Jasper 230 kV 2 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 4100 |  | Jasper-Yemassee 230 kV 2 | SCEG (SERC) | 1016 | 7 | Jasper-Yemassee 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 4200 |  | FLAGLER BEACH-BUNNELL 230 kV 1 | FPL (FRCC) | 502 | 11.6 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4200 |  | DALLAS-SILVER SPRINGS 230 kV 1 | DEF (FRCC) | 871 | 15.7 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4200 |  | QUASAR-BRADFORD AUTO#2 230 kV 1 | FPL (FRCC) | 402 | 5 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4200 |  | VOLUSIA -TOMOKA 230 kV 1 | FPL (FRCC) | 478 | 11 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | Williston-ARCHER 230 kV 1 | DEF (FRCC) | 524 | 10.4 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | RICE -QUASAR 230 kV 1 | FPL (FRCC) | 402 | 7.8 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4400 |  | BARNA -BARNA 230 kV 1 | FPL (FRCC) | 446 | 5.9 | POINSETT-ROBERTS 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4500 |  | QUASAR-BRADFORD AUTO#2 230 kV 1 | FPL (FRCC) | 402 | 3.6 | BRONSON-CRYSTAL RIVER PLANT 230KV YARD 230 kV 30 | DEF (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4500 |  | TOCOI -MILLCREEK 230 kV 1 | FPL (FRCC) | 588 | 6.7 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4500 |  | FLORATAM-HIGHRIDGE 230 kV 1 | FPL (FRCC) | 402 | 7.1 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4500 |  | Yemassee-Canadys 230 kV 1 | SCEG (SERC) | 508 | 5.3 | Yemassee-Ritter 230 kV 1 | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC) | 343/343 | 343 | 343 | SCEG | SERC | SERC | SERC | SCEG (SERC)
|  |  | 4500 |  | VOLUSIA -TOMOKA 230 kV 1 | FPL (FRCC) | 478 | 9.9 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4600 |  | OSTEEN-GACO 230 kV 1 | FPL (FRCC) | 526 | 9.2 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4600 |  | CAPE CANAVERAL-TULSA 230 kV 1 | FPL (FRCC) | 588 | 6 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | Seminole Generation Station Collector Bus-TITANIUM 230 kV 1 | SEC-FPL (FRCC) | 637 | 14.5 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 412/401 | 412 | 401 | SEC-FPL | FRCC | FRCC | FRCC | SEC-FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | TITANIUM-GREEN COVE SPRINGS (FPL) 230 kV 1 | FPL (FRCC) | 637 | 15.5 | DUVAL -GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4700 |  | HIGHRIDGE-VOLUSIA 230 kV 1 | FPL (FRCC) | 402 | 7.5 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4800 |  | NORRIS-FLORATAM 230 kV 1 | FPL (FRCC) | 402 | 5.6 | POINSETT-GACO 500 kV 1 | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC) | 401/401 | 401 | 401 | FPL | FRCC | FRCC | FRCC | FPL (FRCC)
|  |  | 4900 |  | FORT WHITE 230KV BUS SPLIT NORTH-SUWANNEE RIVER SUBSTATION 230 kV 1 | DEF (FRCC) | 650 | 11.6 | FORT WHITE 115/230 kV 1 | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC) | 402/402 | 402 | 402 | DEF | FRCC | FRCC | FRCC | DEF (FRCC)
|  |  | 4900 |  | YULEE TRANSMISSION SUB-Kingsland 230 kV 1 | FPL-SOCO (FRCC-SERC) | 607 | 20.9 | Thalmann-DUVAL 500 kV 1 | SOCO-FPL (SERC-FRCC) | 401/346 | 401 | 346 | FPL-SOCO | FRCC | SERC | FRCC-SERC | FPL-SOCO (FRCC-SERC) | 346/401 | 346 | 401 | SOCO-FPL | SERC | FRCC | SERC-FRCC | SOCO-FPL (SERC-FRCC)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
MISO to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
PJM to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
SPP to SERC | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 5000 | + | No limit found at 5000 MW |  |  |  | Any tested facility
MISO to SPP | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 4200 |  | Russellville South-505508 DARDANE5 161 161 kV 1 | EES-EAI-SWPA (MISO-SPP) | 396 | 5.7 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/515 | 327 | 515 | EES-EAI-SWPA | MISO | SPP | MISO-SPP | EES-EAI-SWPA (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4500 |  | Russellville East-Russellville South 161 kV 1 | EES-EAI (MISO) | 446 | 5.8 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility
SERC to SPP | 5000 | + |  |  | No limit found at 5000 MW |  |  |  | None
|  |  | 3400 |  | Russellville South-505508 DARDANE5 161 161 kV 1 | EES-EAI-SWPA (MISO-SPP) | 396 | 6.4 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/515 | 327 | 515 | EES-EAI-SWPA | MISO | SPP | MISO-SPP | EES-EAI-SWPA (MISO-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 3600 |  | Russellville East-Russellville South 161 kV 1 | EES-EAI (MISO) | 446 | 7.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4100 |  | 505508 DARDANE5 161-505514 CLARKSV5 161 161 kV 1 | SWPA-SWPA (SPP) | 236 | 4.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 515/515 | 515 | 515 | SWPA-SWPA | SPP | SPP | SPP-SPP | SWPA-SWPA (SPP-SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4300 |  | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 1299 | 15.9 | 532797 WOLFCRK7 345 345/25 kV 1 | WERE (SPP) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP) | 536/536 | 536 | 536 | WERE | SPP | SPP | SPP-SPP | WERE (SPP-SPP)
|  |  | 4300 |  | Russellville North-Russellville East 161 kV 1 | EES-EAI (MISO) | 396 | 4.1 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 4300 |  | Russellville East-Russellville East 161 kV R1 | EES-EAI (MISO) | 396 | 4.2 | ANO 500-515305 FTSMITH8 500 500 kV 1 | EES-EAI-OKGE (MISO-SPP) | 327/327 | 327 | 327 | EES-EAI | MISO | MISO | MISO | EES-EAI (MISO) | 327/524 | 327 | 524 | EES-EAI-OKGE | MISO | SPP | MISO-SPP | EES-EAI-OKGE (MISO-SPP)
|  |  | 5000 | + | No other limit found at 5000 MW |  |  |  | Any other tested facility

## 2018 MMWG Data Dictionary (hidden)
101 | ISO-NE | NPCC PC
102 | NYISO | NPCC PC
103 | IESO | NPCC PC
107 | CORNWALL | NPCC PC
104 | TE | NPCC PC
105 | NB | NPCC PC
108 | NF | NPCC PC
106 | NS | NPCC PC
225 | PJM | PJM
225 | PJM500 | PJM
226 | PENELEC | PJM
227 | METED | PJM
228 | JCPL | PJM
228 | JCP&L | PJM
229 | PL | PJM
229 | PPL | PJM
230 | PECO | PJM
231 | PSE&G | PJM
231 | PSEG | PJM
232 | BGE | PJM
233 | PEPCO | PJM
238 | SMECO | PJM
234 | AE | PJM
235 | DP&L | PJM
236 | UGI | PJM
237 | RECO | PJM
201 | AP | PJM
205 | AEP | PJM
202 | ATSI | PJM
206 | OVEC | PJM
207 | HE | MISO
208 | DEI | MISO
212 | DEO&K | PJM
209 | DAY | PJM
210 | SIGE | MISO
215 | DLCO | PJM
216 | IPL | MISO
217 | NIPS | MISO
218 | METC | MISO
219 | ITCT | MISO
222 | CE | PJM
330 | AECI | SERC PC
332 | LAGN | MISO
340 | CPLE | SERC PC
341 | CPLW | SERC PC
342 | DUK | SERC PC
344 | SC | SERC PC
345 | DVP | PJM
350 | PS | SERC PC
346 | SOCO | SERC PC
349 | SMEPA | MISO
363 | LGEE | SERC PC
364 | OMUA | SERC PC
351 | EES | MISO
326 | EES-EMI | MISO
327 | EES-EAI | MISO
352 | YAD | SERC PC
353 | SEHA | SERC PC
354 | SERU | SERC PC
355 | SETH | SERC PC
314 | BREC | MISO
320 | EKPC | PJM
333 | CWLD | MISO
360 | CWLP | MISO
356 | AMMO | MISO
357 | AMIL | MISO
361 | SIPC | MISO
362 | EEI | SERC PC
347 | TVA | SERC PC
343 | SCEG | SERC PC
366 | TAP | SERC PC
365 | SMT | SERC PC
401 | FPL | FRCC PC
401 | FPL-KEYS | FRCC PC
402 | DEF | FRCC PC
403 | FTP | FRCC PC
421 | TCEC | FRCC PC
404 | GVL | FRCC PC
405 | HST | FRCC PC
406 | JEA | FRCC PC
407 | KEY | FRCC PC
411 | FMPP-KIS | FRCC PC
409 | LWU | FRCC PC
410 | NSB | FRCC PC
411 | FMPP-OUC | FRCC PC
411 | FMPP-LAK | FRCC PC
411 | FMPP | FRCC PC
402 | DEF-FMPA | FRCC PC
401 | FPL-FMPA | FRCC PC
402 | DEF-SECI | FRCC PC
412 | SEC | FRCC PC
401 | FPL-SECI | FRCC PC
411 | FMPP-STC | FRCC PC
415 | TAL | FRCC PC
416 | TECO | FRCC PC
417 | VER | FRCC PC
419 | RCU | FRCC PC
418 | NUG | FRCC PC
426 | OSC | FRCC PC
401 | FPL-GA-Co-Op | FRCC PC
427 | OLEANDER | FRCC PC
428 | CALPINE | FRCC PC
438 | IPP-REL | FRCC PC
401 | FPL-LCEC | FRCC PC
502 | CLEC | MISO
503 | LAFA | MISO
504 | LEPA | MISO
520 | AEPW | SPP RTO
515 | SWPA | SPP RTO
523 | GRDA | SPP RTO
524 | OKGE | SPP RTO
525 | WFEC | SPP RTO
526 | SPS | SPP RTO
527 | OMPA | SPP RTO
531 | MIDW | SPP RTO
534 | SUNC | SPP RTO
536 | WERE | SPP RTO
541 | GMO | SPP RTO
541 | KCPL | SPP RTO
542 | KACY | SPP RTO
544 | EMDE | SPP RTO
545 | INDN | SPP RTO
546 | SPRM | SPP RTO
998 | ERCOT | SPP RTO
999 | WECC | SPP RTO
600 | XEL | MISO
620 | OTP | MISO
608 | MP | MISO
680 | DPC | MISO
627 | ALTW | MISO
613 | SMMPA | MISO
615 | GRE | MISO
652 | WAPA | SPP RTO
635 | MEC | MISO
633 | MPW | MISO
640 | NPPD | SPP RTO
645 | OPPD | SPP RTO
641 | HAST | SPP RTO
642 | GRIS | SPP RTO
650 | LES | SPP RTO
997 | WBDC-WECC | SPP RTO
659 | BEPC-SPP | SPP RTO
661 | MDU | MISO
659 | BEPC | SPP RTO
663 | BEPC-MISO | MISO
667 | MHEB | Manitoba
672 | SPC | SaskPower
295 | WEC | MISO
694 | ALTE | MISO
296 | MIUP | MISO
696 | WPS | MISO
697 | MGE | MISO
698 | UPPC | MISO
225 | PJM501 | PJM