## FRCC
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 13:44 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_FRCC.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_FRCC.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes
SOURCE | SINK | 10000 | 1 | 5668.7 | * | L:380015 8THALMANN 500 400356 DUVAL 500 1 |  |  | 1926.9 | 2598 | 0.11838 |  | 0.07567 | 1163.1 | 1592 |  | 380015 | 400356
[7 empty] | C:380014 8HATCH 500 400356 DUVAL 500 1 | 843 | [8 empty] | 380014 | 400356
[7 empty] | Open 380014 8HATCH 500 400356 DUVAL 500 1 |  |  |  |  | 0.73898 | 0.05779 | 1033.7 | 1361.3
|  |  | 2 | 7515.4 | * | L:380014 8HATCH 500 400356 DUVAL 500 1 |  |  | 1792.6 | 2598 | 0.10717 |  | 0.05779 | 1033.7 | 1468
[7 empty] | C:380015 8THALMANN 500 400356 DUVAL 500 1 | 844
[7 empty] | Open 380015 8THALMANN 500 400356 DUVAL 500 1 |  |  |  |  | 0.65249 | 0.07567 | 1163.1 | 1731.8
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow

## MISO
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 13:48 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_MISO.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_MISO.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes
SOURCE | SINK | 10000 | 1 | -8064.6 | * | L:340624 5BRTAP 161 360043 5PARADISE FP 161 1 |  |  | 749.2 | 446 | 0.0376 |  | 0.03628 | 712.3 | 419.6 |  | 300038 | 344974
[7 empty] | C:348493 7XENIA 345 348827 7W MT VERNON 345 1 | 823 | [8 empty] | 300041 | 344154
[7 empty] | Open 348493 7XENIA 345 348827 7W MT VERNON 345 1 |  |  |  |  | 0.03476 | 0.03788 | 1063.7 | 758.1 |  | 300041 | 344327
|  |  | 1335 | -7338.3 |  | L:340624 5BRTAP 161 360043 5PARADISE FP 161 1 |  |  | 712.3 | 446 | 0.03628 | [5 empty] | 336562 | 336839
[7 empty] | Base Case | [9 empty] | 340624 | 360043
|  |  | 2782 | -5136.1 | * | L:300041 7FRANKS 345 344154 7BLAND 345 1 |  |  | -1465.8 | -1273 | -0.03755 |  | -0.02657 | -985.5 | -849 |  | 344224 | 344327
[7 empty] | C:344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 | 739 | [8 empty] | 344974 | 345773
[7 empty] | Open 344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 |  |  |  |  | -0.48334 | 0.02271 | 993.8 | 877.2 |  | 345667 | 345668
|  |  | 2787 | -2099.6 | * | L:346895 7COFFEEN 345 348151 7ROXFORD 345 1 |  |  | 1291.7 | 1195 | 0.04606 |  | 0.03735 | 1047.2 | 968.8 |  | 346895 | 348151
[7 empty] | C:348493 7XENIA 345 348827 7W MT VERNON 345 1 | 823 | [8 empty] | 346992 | 348827
[7 empty] | Open 348493 7XENIA 345 348827 7W MT VERNON 345 1 |  |  |  |  | 0.22989 | 0.03788 | 1063.7 | 984.1 |  | 346992 | 360002
|  |  | 16172 | -2002.9 | * | L:300038 7ESSEX 345 344974 7LUTESVIL 345 1 |  |  | -1279.5 | -1195 | -0.04217 |  | -0.0347 | -1023.5 | -954 |  | 347830 | 348493
[7 empty] | C:360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 | 9348 | [8 empty] | 348493 | 348827
[7 empty] | Open 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  |  |  | -0.1531 | 0.04879 | 1671.7 | 1574
|  |  | 2788 | -1371 | * | L:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 |  |  | -1250.8 | -1195 | -0.04072 |  | -0.03248 | -1046.2 | -1001.7
[7 empty] | C:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 | 2313
[7 empty] | Open 346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  |  |  | -0.21913 | 0.03763 | 933.8 | 882.2
|  |  | 2789 | -1316.7 |  | L:346895 7COFFEEN 345 348151 7ROXFORD 345 1 |  |  | 1047.2 | 998 | 0.03735
Base Case
|  |  | 2793 | 458.7 | * | L:345667 7RUSH 1 345 345668 7RUSH 2 345 Z |  |  | 1478.1 | 1494 | 0.03475 |  | 0.02757 | 1299.6 | 1312.3
[7 empty] | C:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 | 2313
[7 empty] | Open 346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  |  |  | 0.19107 | 0.03763 | 933.8 | 951
|  |  | 2794 | 794.2 |  | L:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 |  |  | -1046.2 | -1072 | -0.03248
Base Case
|  |  | 2795 | 864.7 | * | L:348493 7XENIA 345 348827 7W MT VERNON 345 1 |  |  | 1279.6 | 1319 | 0.04559 |  | 0.03788 | 1063.7 | 1096.4
[7 empty] | C:346895 7COFFEEN 345 348151 7ROXFORD 345 1 | 803
[7 empty] | Open 346895 7COFFEEN 345 348151 7ROXFORD 345 1 |  |  |  |  | 0.20618 | 0.03735 | 1047.2 | 1079.5
|  |  | 2817 | 2732.2 | * | L:347830 7NEWTON 345 348493 7XENIA 345 1 |  |  | 1070.4 | 1195 | 0.04559 |  | 0.03788 | 854.5 | 958
[7 empty] | C:346895 7COFFEEN 345 348151 7ROXFORD 345 1 | 803
[7 empty] | Open 346895 7COFFEEN 345 348151 7ROXFORD 345 1 |  |  |  |  | 0.20618 | 0.03735 | 1047.2 | 1149.2
|  |  | 2822 | 3131.8 | * | L:300038 7ESSEX 345 344974 7LUTESVIL 345 1 |  |  | -1081.4 | -1195 | -0.03626 |  | -0.0347 | -1023.5 | -1132.2
[7 empty] | C:300041 7FRANKS 345 344154 7BLAND 345 1 | 2009
[7 empty] | Open 300041 7FRANKS 345 344154 7BLAND 345 1 |  |  |  |  | 0.05876 | -0.02657 | -985.5 | -1068.7
|  |  | 2823 | 3234.1 | * | L:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  | 1173.3 | 1319 | 0.04506 |  | 0.03763 | 933.8 | 1055.5
[7 empty] | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 760
[7 empty] | Open 344974 7LUTESVIL 345 345773 7ST FRANC 345 1 |  |  |  |  | -0.22892 | -0.03248 | -1046.2 | -1151.2
|  |  | 2850 | 3598.5 |  | L:348493 7XENIA 345 348827 7W MT VERNON 345 1 |  |  | 1063.7 | 1200 | 0.03788
Base Case
|  |  | 9578 | 4941.5 |  | L:300038 7ESSEX 345 344974 7LUTESVIL 345 1 |  |  | -1023.5 | -1195 | -0.0347
Base Case
|  |  | 11049 | 5913.9 | * | L:346992 7E W FKFT 345 348827 7W MT VERNON 345 1 |  |  | -1112.7 | -1319 | -0.03488 |  | -0.0289 | -920.2 | -1091.1
[7 empty] | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 760
[7 empty] | Open 344974 7LUTESVIL 345 345773 7ST FRANC 345 1 |  |  |  |  | 0.18406 | -0.03248 | -1046.2 | -1238.3
|  |  | 11133 | 6481.6 | * | L:336562 8FRANKLIN% 500 336839 8R.BRASWELL% 500 1 |  |  | -1489.9 | -1732 | -0.03735 |  | -0.02364 | -525.4 | -678.6
[7 empty] | C:336562 8FRANKLIN% 500 336820 8GGNS% 500 1 | 604
[7 empty] | Open 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 |  |  |  |  | 0.69007 | -0.01987 | -1397.7 | -1526.4
|  |  | 13778 | 7075.6 |  | L:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  | 933.8 | 1200 | 0.03763
Base Case
|  |  | 13884 | 7796.1 | * | L:344224 7CALAWY 1 345 344327 7LOOSECRK 345 1 |  |  | 1507.9 | 1793 | 0.03657 |  | 0.02271 | 993.8 | 1170.9
[7 empty] | C:300041 7FRANKS 345 344154 7BLAND 345 1 | 2009
[7 empty] | Open 300041 7FRANKS 345 344154 7BLAND 345 1 |  |  |  |  | -0.52163 | -0.02657 | -985.5 | -1192.6
|  |  | 13934 | 8453.3 | * | L:300041 7FRANKS 345 344327 7LOOSECRK 345 1 |  |  | -1311.3 | -1628 | -0.03747 |  | -0.02292 | -771.8 | -965.5
[7 empty] | C:300041 7FRANKS 345 344154 7BLAND 345 1 | 2009
[7 empty] | Open 300041 7FRANKS 345 344154 7BLAND 345 1 |  |  |  |  | 0.54747 | -0.02657 | -985.5 | -1210.1
|  |  | 15437 | 8986.8 |  | L:347830 7NEWTON 345 348493 7XENIA 345 1 |  |  | 854.5 | 1195 | 0.03788
Base Case
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow

## NPCC
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 14:01 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_NPCC.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_NPCC.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes
SOURCE | SINK | 10000 | 3 | -8238.9 | * | L:135305 SAWYER80 230 135414 HUNTLEY2 230 1 |  |  | -966.2 | -654 | -0.03789 |  | -0.02434 | -642.5 | -441.9 | INVALID LIMIT | 130753 | 130755
[7 empty] | C:135306 SAWYER79 230 135414 HUNTLEY2 230 1 | 424 | [8 empty] | 130755 | 130757
[7 empty] | Open 135306 SAWYER79 230 135414 HUNTLEY2 230 1 |  |  |  |  | 0.54611 | -0.02482 | -592.8 | -388.3 |  | 130755 | 130839
|  |  | 10 | -7303.6 | * | L:130762 GARDV230 230 130767 STOLE230 230 1 |  |  | -742.3 | -478 | -0.03619 |  | -0.01753 | -337.6 | -209.6 |  | 130755 | 131157
[7 empty] | C:T:77&78 | 3774 | [8 empty] | 130756 | 135398
[7 empty] | Open 135307 SAWYERB1 230 135436 SAWYER23 23.0 1 |  |  |  |  | -0.36528 | 1e-05 | 62.6 | 62.5 |  | 130757 | 130768
[7 empty] | Open 135303 SAWYER77 230 135307 SAWYERB1 230 1 | [9 empty] | 130757 | 200930
[7 empty] | Open 135303 SAWYER77 230 135414 HUNTLEY2 230 1 |  |  |  |  | -0.36528 | 0.02547 | 488.3 | 302.3 |  | 130762 | 130767
[7 empty] | Open 135303 SAWYER77 230 135415 PACKARD2 230 1 | [9 empty] | 130762 | 135413
[7 empty] | Open 135308 SAWYERB2 230 135436 SAWYER23 23.0 1 |  |  |  |  | -0.36528 | 6e-05 | 64.4 | 64 |  | 130763 | 200675
[7 empty] | Open 135304 SAWYER78 230 135308 SAWYERB2 230 1 | [9 empty] | 130768 | 130876
[7 empty] | Open 135304 SAWYER78 230 135414 HUNTLEY2 230 2 |  |  |  |  | -0.36528 | 0.02555 | 490.4 | 303.8 |  | 131157 | 136153
[7 empty] | Open 135304 SAWYER78 230 135415 PACKARD2 230 2 | [9 empty] | 135250 | 135251
|  |  | 1 | -10315.5 | * | L:135415 PACKARD2 230 147842 NIAGAR2W 230 2 |  |  | -1140.7 | -717 | -0.04107 |  | -0.01979 | -544.6 | -340.5 | STE Rating Used | 135250 | 135413
|  |  | Additional Transfer Using STE -> | 3116.6301 |  |  | C:T:61&64 | 3769 | [8 empty] | 135250 | 146000
|  |  | FCITC Using STE -> | -7198.8699 |  |  | Open 135415 PACKARD2 230 147842 NIAGAR2W 230 1 |  |  |  |  | 0.77981 | -0.02011 | -553.4 | -346 |  | 135251 | 200654
[7 empty] | Open 130766 ROBIN230 230 147841 NIAGAR2E 230 1 |  |  |  |  | 0.44229 | -0.01268 | -371.9 | -241.1 |  | 135398 | 200942
|  |  | 2 | -8296.2 | * | L:135415 PACKARD2 230 147842 NIAGAR2W 230 1 |  |  | -977.5 | -717 | -0.0314 |  | -0.02011 | -553.4 | -386.6 | STE Rating Used | 135413 | 146000
|  |  | Additional Transfer Using STE -> | 4076.4331 |  |  | C:T:62&PA27 | 3772 | [8 empty] | 135415 | 147842
|  |  | FCITC Using STE -> | -4219.7669 |  |  | Open 135415 PACKARD2 230 147842 NIAGAR2W 230 2 |  |  |  |  | 0.78014 | -0.01979 | -544.6 | -380.5 |  | 135415 | 147842
[7 empty] | Open 147842 NIAGAR2W 230 157063 BECK_#2_PA27 230 1 |  |  |  |  | -0.25171 | -0.01645 | -3.2 | 133.3 |  | 136150 | 149001
|  |  | 16 | -7103.8 | * | L:135304 SAWYER78 230 135415 PACKARD2 230 2 |  |  | -953.4 | -644 | -0.04355 |  | -0.02561 | -561 | -379.1 | INVALID LIMIT | 136150 | 149001
[7 empty] | C:135303 SAWYER77 230 135415 PACKARD2 230 1 | 417
[7 empty] | Open 135303 SAWYER77 230 135415 PACKARD2 230 1 |  |  |  |  | 0.70425 | -0.02547 | -557.1 | -376.1
|  |  | 17 | -7074.1 | * | L:135303 SAWYER77 230 135415 PACKARD2 230 1 |  |  | -951.6 | -644 | -0.04348 |  | -0.02547 | -557.1 | -376.9 | INVALID LIMIT
[7 empty] | C:135304 SAWYER78 230 135415 PACKARD2 230 2 | 420
[7 empty] | Open 135304 SAWYER78 230 135415 PACKARD2 230 2 |  |  |  |  | 0.70315 | -0.02561 | -561 | -379.9
|  |  | 23 | -6747.6 | * | L:135306 SAWYER79 230 135414 HUNTLEY2 230 1 |  |  | -913.4 | -654 | -0.03844 |  | -0.02482 | -592.8 | -425.3 | INVALID LIMIT
[7 empty] | C:135305 SAWYER80 230 135419 SUNY-80 230 1 | 423
[7 empty] | Open 135305 SAWYER80 230 135419 SUNY-80 230 1 |  |  |  |  | -0.54855 | 0.02484 | 584.5 | 416.9
|  |  | 28 | -6650.1 | * | L:135305 SAWYER80 230 135419 SUNY-80 230 1 |  |  | 909.7 | 654 | 0.03846 |  | 0.02484 | 584.5 | 419.3 | INVALID LIMIT
[7 empty] | C:135306 SAWYER79 230 135414 HUNTLEY2 230 1 | 424
[7 empty] | Open 135306 SAWYER79 230 135414 HUNTLEY2 230 1 |  |  |  |  | -0.54872 | -0.02482 | -592.8 | -427.7
|  |  | 30 | -6603.8 | * | L:135306 SAWYER79 230 135418 SUNY-79 230 1 |  |  | 907.9 | 654 | 0.03844 |  | 0.02482 | 587.2 | 423.4 | INVALID LIMIT
[7 empty] | C:135305 SAWYER80 230 135419 SUNY-80 230 1 | 423
[7 empty] | Open 135305 SAWYER80 230 135419 SUNY-80 230 1 |  |  |  |  | 0.54855 | 0.02484 | 584.5 | 420.4
|  |  | 41 | -6133.9 | * | L:135413 GRDNVL2 230 135418 SUNY-79 230 1 |  |  | -889.5 | -654 | -0.03839 |  | -0.02484 | -576.7 | -424.3 | INVALID LIMIT
[7 empty] | C:135413 GRDNVL2 230 135419 SUNY-80 230 1 | 432
[7 empty] | Open 135413 GRDNVL2 230 135419 SUNY-80 230 1 |  |  |  |  | 0.54476 | -0.02486 | -574.2 | -421.6
|  |  | 42 | -6104 | * | L:135413 GRDNVL2 230 135419 SUNY-80 230 1 |  |  | -888.4 | -654 | -0.0384 |  | -0.02486 | -574.2 | -422.4 | INVALID LIMIT
[7 empty] | C:135413 GRDNVL2 230 135418 SUNY-79 230 1 | 431
[7 empty] | Open 135413 GRDNVL2 230 135418 SUNY-79 230 1 |  |  |  |  | 0.54491 | -0.02484 | -576.7 | -425.1
|  |  | 62 | -5190.1 | * | L:135303 SAWYER77 230 135414 HUNTLEY2 230 1 |  |  | 878.6 | 654 | 0.04328 |  | 0.02547 | 488.3 | 356.2 | INVALID LIMIT
[7 empty] | C:135304 SAWYER78 230 135415 PACKARD2 230 2 | 420
[7 empty] | Open 135304 SAWYER78 230 135415 PACKARD2 230 2 |  |  |  |  | -0.69573 | -0.02561 | -561 | -428.1
|  |  | 63 | -5184.1 | * | L:135304 SAWYER78 230 135414 HUNTLEY2 230 2 |  |  | 878.5 | 654 | 0.0433 |  | 0.02555 | 490.4 | 357.9 | INVALID LIMIT
[7 empty] | C:135303 SAWYER77 230 135415 PACKARD2 230 1 | 417
[7 empty] | Open 135303 SAWYER77 230 135415 PACKARD2 230 1 |  |  |  |  | -0.69656 | -0.02547 | -557.1 | -425.1
|  |  | 84 | -3956.9 | * | L:130755 OAKDL345 345 130839 OAK2M115 115 1 |  |  | 729.6 | 556 | 0.04387 |  | 0.01269 | 314.4 | 264.2
[7 empty] | C:SB:OAKD345_31-B322 | 3851
[7 empty] | Open 130755 OAKDL345 345 130757 WATRC345 345 1 |  |  |  |  | 0.36371 | 0.06178 | 576.9 | 332.5
[7 empty] | Open 130840 OAK3M115 115 131075 OAKDAL34 34.5 1 |  |  |  |  | -0.01027 | -0.0003 | 41.4 | 42.6
[7 empty] | Open 130755 OAKDL345 345 130840 OAK3M115 115 1 |  |  |  |  | 0.71092 | 0.01225 | 289.7 | 241.2
Open 130838 OAKDL115 115 130840 OAK3M115 115 1
|  |  | 110 | -2365.4 |  | L:135250 DUNKIRK 230 135251 S RIPLEY 230 1 |  |  | 599.8 | 482 | 0.04979
Base Case
|  |  | 111 | -2184.4 |  | L:135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  | 596.8 | 488 | 0.04979
Base Case
|  |  | 112 | -2115.7 | * | L:135250 DUNKIRK 230 135251 S RIPLEY 230 1 |  |  | 655 | 530 | 0.05909 |  | 0.04979 | 599.8 | 494.4
[7 empty] | C:135398 SW345 345 200942 FARM_V_345 345 1 | 2799
[7 empty] | Open 135398 SW345 345 200942 FARM_V_345 345 1 |  |  |  |  | 0.21931 | 0.04239 | 251.9 | 162.2
|  |  | 4059 | -992.4 | * | L:135250 DUNKIRK 230 135413 GRDNVL2 230 2 |  |  | -541.1 | -505 | -0.03637 |  | -0.02424 | -360.6 | -336.5
[7 empty] | C:135413 GRDNVL2 230 146000 BALLHILL 230 1 | 433
[7 empty] | Open 135413 GRDNVL2 230 146000 BALLHILL 230 1 |  |  |  |  | -0.50362 | 0.02408 | 358.5 | 334.6
|  |  | 4144 | -761.6 | * | L:135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  | 652 | 607 | 0.05909 |  | 0.04979 | 596.8 | 558.8
[7 empty] | C:135398 SW345 345 200942 FARM_V_345 345 1 | 2799
[7 empty] | Open 135398 SW345 345 200942 FARM_V_345 345 1 |  |  |  |  | 0.21931 | 0.04239 | 251.9 | 219.6
|  |  | 8354 | 2568.6 | * | L:135413 GRDNVL2 230 146000 BALLHILL 230 1 |  |  | 541.7 | 637 | 0.0371 |  | 0.02408 | 358.5 | 420.3
[7 empty] | C:B:DUNKG3 | 3740
[7 empty] | Open 135250 DUNKIRK 230 135413 GRDNVL2 230 2 |  |  |  |  | -0.53034 | -0.02424 | -360.6 | -422.8
[7 empty] | Open 135250 DUNKIRK 230 135273 DUNKIRK1 115 1 |  |  |  |  | -0.23074 | -0.00074 | 34.6 | 32.7
|  |  | 8357 | 2841.3 | * | L:135250 DUNKIRK 230 146000 BALLHILL 230 1 |  |  | -531.6 | -637 | -0.0371 |  | -0.02408 | -348.3 | -416.7
[7 empty] | C:B:DUNKG3 | 3740
[7 empty] | Open 135250 DUNKIRK 230 135413 GRDNVL2 230 2 |  |  |  |  | 0.53034 | -0.02424 | -360.6 | -429.5
[7 empty] | Open 135250 DUNKIRK 230 135273 DUNKIRK1 115 1 |  |  |  |  | 0.23074 | -0.00074 | 34.6 | 32.5
|  |  | 8360 | 3161.3 | * | L:130762 GARDV230 230 135413 GRDNVL2 230 1 |  |  | 617.9 | 739 | 0.03829 |  | 0.00401 | -125.2 | -112.5
[7 empty] | C:T:77&78 | 3774
[7 empty] | Open 135307 SAWYERB1 230 135436 SAWYER23 23.0 1 |  |  |  |  | 0.67112 | 1e-05 | 62.6 | 62.6
Open 135303 SAWYER77 230 135307 SAWYERB1 230 1
[7 empty] | Open 135303 SAWYER77 230 135414 HUNTLEY2 230 1 |  |  |  |  | 0.67112 | 0.02547 | 488.3 | 568.8
Open 135303 SAWYER77 230 135415 PACKARD2 230 1
[7 empty] | Open 135308 SAWYERB2 230 135436 SAWYER23 23.0 1 |  |  |  |  | 0.67112 | 6e-05 | 64.4 | 64.6
Open 135304 SAWYER78 230 135308 SAWYERB2 230 1
[7 empty] | Open 135304 SAWYER78 230 135414 HUNTLEY2 230 2 |  |  |  |  | 0.67112 | 0.02555 | 490.4 | 571.2
Open 135304 SAWYER78 230 135415 PACKARD2 230 2
|  |  | 8361 | 3177.1 | * | L:130768 WATRC230 230 130876 HILSD230L69 230 1 |  |  | 425.5 | 584 | 0.0499 |  | 0.02467 | 206.5 | 284.8
[7 empty] | C:130757 WATRC345 345 200930 26MAINESBURG 345 1 | 2771
[7 empty] | Open 130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  |  |  | 0.49729 | 0.05074 | 440.4 | 601.6
|  |  | 8362 | 3838.3 | * | L:131157 CLARKCRNS 345 136153 LAFAYTTE 345 1 |  |  | -1120.3 | -1327 | -0.05385 |  | -0.02719 | -993.9 | -1098.3
[7 empty] | C:130753 FRASR345 345 130755 OAKDL345 345 1 | 385
[7 empty] | Open 130753 FRASR345 345 130755 OAKDL345 345 1 |  |  |  |  | -0.45041 | 0.05918 | 280.7 | 507.8
|  |  | 8363 | 4340.9 | * | L:135398 SW345 345 200942 FARM_V_345 345 1 |  |  | 488 | 769 | 0.06473 |  | 0.04239 | 251.9 | 435.9
[7 empty] | C:R:EESR/WF/NWES | 3695
[7 empty] | Open 135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  |  |  | 0.31707 | 0.04979 | 596.8 | 812.9
[7 empty] | Open 135277 FALCONER 115 200579 26WARREN 115 1 |  |  |  |  | 0.48101 | 0.01249 | 91.6 | 145.8
[7 empty] | Open 130836 N.WAV115 115 200676 26E.SAYRE 115 1 |  |  |  |  | 0.03871 | 0.01408 | 74.9 | 136.1
|  |  | 8365 | 4393.9 | * | L:130755 OAKDL345 345 131157 CLARKCRNS 345 1 |  |  | -1065.8 | -1327 | -0.05946 |  | -0.02754 | -914.4 | -1035.4
[7 empty] | C:130753 FRASR345 345 130755 OAKDL345 345 1 | 385
[7 empty] | Open 130753 FRASR345 345 130755 OAKDL345 345 1 |  |  |  |  | -0.5393 | 0.05918 | 280.7 | 540.7
|  |  | 8372 | 5649.8 |  | L:130755 OAKDL345 345 130757 WATRC345 345 1 |  |  | 576.9 | 926 | 0.06178
Base Case
|  |  | 8373 | 5767.2 | * | L:130763 HILSD230 230 200675 26E.TWANDA 230 1 |  |  | 222.4 | 531 | 0.0535 |  | 0.03948 | 100.8 | 328.5
[7 empty] | C:130757 WATRC345 345 200930 26MAINESBURG 345 1 | 2771
[7 empty] | Open 130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  |  |  | 0.2763 | 0.05074 | 440.4 | 733
|  |  | 8374 | 6402.4 | * | L:130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  | 503.1 | 927 | 0.06622 |  | 0.05074 | 440.4 | 765.3
[7 empty] | C:R:C398/NWES | 3687
[7 empty] | Open 200675 26E.TWANDA 230 200940 26SCOTCHHLLW 230 1 |  |  |  |  | 0.02594 | 0.01501 | 370.9 | 467
Open 200701 26GROVER 230 200940 26SCOTCHHLLW 230 1
[7 empty] | Open 130763 HILSD230 230 200675 26E.TWANDA 230 1 |  |  |  |  | 0.28673 | 0.03948 | 100.8 | 353.5
[7 empty] | Open 200674 26TOWANDA 115 200675 26E.TWANDA 230 3 |  |  |  |  | -0.03658 | 0.00627 | -103 | -62.8
[7 empty] | Open 130836 N.WAV115 115 200676 26E.SAYRE 115 1 |  |  |  |  | 0.28349 | 0.01408 | 74.9 | 165.1
|  |  | 8376 | 6687.4 | * | L:130755 OAKDL345 345 130757 WATRC345 345 1 |  |  | 616.4 | 1076 | 0.06872 |  | 0.06178 | 576.9 | 990.1
[7 empty] | C:130765 OAKDL230 230 130838 OAKDL115 115 1 | 2781
[7 empty] | Open 130765 OAKDL230 230 130838 OAKDL115 115 1 |  |  |  |  | -0.50979 | -0.01361 | -77.5 | -168.5
|  |  | 8460 | 7831.2 | * | L:130757 WATRC345 345 130768 WATRC230 230 1 |  |  | -279.6 | -540 | -0.03326 |  | 0.00549 | 67.9 | 110.8
[7 empty] | C:SB:WATRC345_31-2 | 3848
[7 empty] | Open 130755 OAKDL345 345 130757 WATRC345 345 1 |  |  |  |  | -0.7038 | 0.06178 | 576.9 | 1060.8
[7 empty] | Open 130757 WATRC345 345 130768 WATRC230 230 2 |  |  |  |  | 0.85361 | 0.00555 | 68.7 | 112.1
|  |  | 12263 | 8272.6 | * | L:130753 FRASR345 345 130755 OAKDL345 345 1 |  |  | 769.1 | 1380 | 0.07385 |  | 0.05918 | 280.7 | 770.3
[7 empty] | C:SB:LAPER_345_3 | 3878
[7 empty] | Open 130755 OAKDL345 345 131157 CLARKCRNS 345 1 |  |  |  |  | -0.53272 | -0.02754 | -914.4 | -1142.2
[7 empty] | Open 130824 CLARKCRNS115 115 131157 CLARKCRNS 345 1 |  |  |  |  | -0.04019 | 0.00017 | -32.7 | -31.3
|  |  | 12477 | 9133.8 |  | L:135398 SW345 345 200942 FARM_V_345 345 1 |  |  | 251.9 | 639 | 0.04239
Base Case
|  |  | 12479 | 9139.2 | * | L:136150 CLAY 345 149001 PANNELL3 345 2 |  |  | 914.4 | 1195 | 0.03071 |  | 0.01954 | 576.6 | 755.2
[7 empty] | C:SB:CLAY345_R10 | 3885
[7 empty] | Open 136150 CLAY 345 149001 PANNELL3 345 1 |  |  |  |  | 0.57102 | 0.01948 | 574.8 | 752.8
[7 empty] | Open 136150 CLAY 345 136181 CLAY 115 1 |  |  |  |  | 0.05292 | 0.00085 | 179.2 | 187
|  |  | 12492 | 9193.3 | * | L:136150 CLAY 345 149001 PANNELL3 345 1 |  |  | 913.1 | 1195 | 0.03067 |  | 0.01948 | 574.8 | 753.9
[7 empty] | C:SB:CLAY345_R20 | 3886
[7 empty] | Open 136150 CLAY 345 149001 PANNELL3 345 2 |  |  |  |  | 0.57022 | 0.01954 | 576.6 | 756.3
[7 empty] | Open 136150 CLAY 345 136181 CLAY 115 1 |  |  |  |  | 0.05284 | 0.00085 | 179.2 | 187
|  |  | 12607 | 9496.4 | * | L:130756 STOLE345 345 135398 SW345 345 1 |  |  | 373.5 | 756 | 0.04028 |  | 0.03142 | 252 | 550.3
[7 empty] | C:SB:DUNK230_R1312 | 3835
[7 empty] | Open 135250 DUNKIRK 230 135251 S RIPLEY 230 1 |  |  |  |  | 0.07806 | 0.04979 | 599.8 | 1072.6
[7 empty] | Open 135250 DUNKIRK 230 135413 GRDNVL2 230 2 |  |  |  |  | -0.10299 | -0.02424 | -360.6 | -590.8
[7 empty] | Open 135250 DUNKIRK 230 146000 BALLHILL 230 1 |  |  |  |  | -0.10299 | -0.02408 | -348.3 | -577
[7 empty] | Open 135250 DUNKIRK 230 135273 DUNKIRK1 115 1 |  |  |  |  | 0 | -0.00074 | 34.6 | 27.6
Open 135250 DUNKIRK 230 135273 DUNKIRK1 115 2
|  |  | 12821 | 9569.7 |  | L:130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  | 440.4 | 926 | 0.05074
Base Case
|  |  | 16245 | 9681.3 |  | L:130763 HILSD230 230 200675 26E.TWANDA 230 1 |  |  | 100.8 | 483 | 0.03948
Base Case
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow

## PJM
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 13:50 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_PJM.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_PJM.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes
SOURCE | SINK | 10000 | 1 | -23736.6 | * | L:200004 CNASTONE 500 200013 PEACHBTM 500 1 |  |  | -4608.5 | -2815 | -0.07556 |  | -0.08201 | -4243.1 | -2296.5 |  | 130757 | 200930
[7 empty] | C:200016 3 MILE I 500 912130 X4-020 TAP 500 1 | 80 | [8 empty] | 130763 | 200675
[7 empty] | Open 200016 3 MILE I 500 912130 X4-020 TAP 500 1 |  |  |  |  | 0.44052 | 0.01465 | -829.3 | -1177 |  | 135251 | 200654
|  |  | 3 | -23230.7 |  | L:200004 CNASTONE 500 200013 PEACHBTM 500 1 |  |  | -4243.1 | -2338 | -0.08201 | [5 empty] | 135398 | 200942
[7 empty] | Base Case | [9 empty] | 200003 | 200004
|  |  | 4780 | -8734.1 | * | L:314686 6CLOVER 230 314697 6HALIFAX 230 1 |  |  | 1316.4 | 797 | 0.05947 |  | 0.03294 | 766.2 | 478.4 |  | 200004 | 200013
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590 | [8 empty] | 200011 | 235104
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | -0.2741 | -0.09678 | -2007.5 | -1162.2 |  | 200011 | 235118
|  |  | 4781 | -8221.5 | * | L:304070 6PERSON230 T 230 314697 6HALIFAX 230 1 |  |  | -1213.1 | -712 | -0.06094 |  | -0.03593 | -694.1 | -398.7 |  | 200568 | 200600
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590 | [8 empty] | 200599 | 200600
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | 0.2585 | -0.09678 | -2007.5 | -1211.8 |  | 200599 | 238547
|  |  | 4782 | -7956.8 |  | L:200003 BRIGHTON 500 200004 CNASTONE 500 1 |  |  | -3030.3 | -2490 | -0.0679 | [5 empty] | 200654 | 903645
[7 empty] | Base Case | [9 empty] | 200675 | 200924
|  |  | 4783 | -6715.7 | * | L:200003 BRIGHTON 500 200004 CNASTONE 500 1 |  |  | -3271.1 | -2815 | -0.06791 |  | -0.0679 | -3030.3 | -2574.3 |  | 200706 | 200708
[7 empty] | C:235101 01BEDNGT 500 235103 01BLACKO 500 1 | 1298 | [8 empty] | 200706 | 200924
[7 empty] | Open 235101 01BEDNGT 500 235103 01BLACKO 500 1 |  |  |  |  | 0.15476 | -6e-05 | -1555.9 | -1555.5 |  | 200708 | 208009
|  |  | 4790 | -5788.6 | * | L:242514 05J.FERR 765 242520 05J.FERR 500 1 |  |  | 2625.2 | 1845 | 0.13478 |  | 0.11716 | 2259.6 | 1581.4 |  | 200767 | 200795
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590 | [8 empty] | 200767 | B$0211
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | -0.1821 | -0.09678 | -2007.5 | -1447.3 |  | 200767 | B$0411
|  |  | 4796 | -5331.5 |  | L:242514 05J.FERR 765 242520 05J.FERR 500 1 |  |  | 2259.6 | 1635 | 0.11716 | [5 empty] | 200769 | B$0211
[7 empty] | Base Case | [9 empty] | 200769 | B$0411
|  |  | 4803 | -4828.8 | * | L:304451 6PA-GREENVIL 230 314574 6EVERETS 230 1 |  |  | -628 | -478 | -0.03106 |  | -0.02128 | -425 | -322.2 |  | 200795 | 200810
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590 | [8 empty] | 200819 | 200928
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | 0.10113 | -0.09678 | -2007.5 | -1540.2 |  | 200927 | 200928
|  |  | 4804 | -4786 | * | L:200011 KEYSTONE 500 235104 01CABOT 500 1 |  |  | 2972.1 | 2598 | 0.07817 |  | 0.04469 | 2023 | 1809.1 |  | 200928 | 903645
[7 empty] | C:235116 01YUKON 500 235118 01SOBEND 500 1 | 1334 | [8 empty] | 235105 | 314925
[7 empty] | Open 235116 01YUKON 500 235118 01SOBEND 500 1 |  |  |  |  | -0.51676 | -0.0648 | -1836.7 | -1526.5 |  | 238544 | 239082
|  |  | 4812 | -4479.1 | * | L:242513 05CULLOD 765 242517 05WYOMIN 765 1 |  |  | 4791.7 | 4253 | 0.12027 |  | 0.07875 | 3367.4 | 3014.6 |  | 238547 | 239082
[7 empty] | C:242510 05BAKER 765 242511 05BROADF 765 1 | 1452 | [8 empty] | 242508 | 242513
[7 empty] | Open 242510 05BAKER 765 242511 05BROADF 765 1 |  |  |  |  | 0.49433 | 0.08399 | 2881.3 | 2505.1 |  | 242510 | 242511
|  |  | 4821 | -4317.7 |  | L:304070 6PERSON230 T 230 314697 6HALIFAX 230 1 |  |  | -694.1 | -539 | -0.03593 | [5 empty] | 242511 | 242518
[7 empty] | Base Case | [9 empty] | 242513 | 242517
|  |  | 4873 | -3782.6 | * | L:242511 05BROADF 765 242518 05BROADF 500 4 |  |  | 2377.1 | 1920 | 0.12083 |  | 0.09681 | 1913.7 | 1547.5 |  | 242514 | 242520
[7 empty] | C:242514 05J.FERR 765 242520 05J.FERR 500 1 | 1466 | [8 empty] | 242518 | 360106
[7 empty] | Open 242514 05J.FERR 765 242520 05J.FERR 500 1 |  |  |  |  | 0.20506 | 0.11716 | 2259.6 | 1816.5 |  | 242520 | 306719
|  |  | 9831 | -3244.5 | * | L:200927 26FOURMILE 115 200928 26FOURMILE 230 6F |  |  | -439.6 | -323 | -0.03594 |  | -0.00568 | -152.3 | -133.9 |  | 304070 | 314697
[7 empty] | C:200819 26ERIE SE 230 200928 26FOURMILE 230 1F | 185 | [8 empty] | 304183 | 314935
[7 empty] | Open 200819 26ERIE SE 230 200928 26FOURMILE 230 1F |  |  |  |  | 0.68496 | -0.04417 | -419.4 | -276.1 |  | 304451 | 314574
|  |  | 14062 | -2942 | * | L:238544 02ASH_3 138 239082 02S8-ATT 345 8 |  |  | -519.2 | -423 | -0.03271 |  | -0.00869 | -228.7 | -203.2 |  | 314569 | 314574
[7 empty] | C:238547 02AT 345 239036 02PERRY 345 1 | 1381 | [8 empty] | 314686 | 314697
[7 empty] | Open 238547 02AT 345 239036 02PERRY 345 1 |  |  |  |  | -0.41284 | 0.0582 | 703.7 | 532.4 |  | 314903 | 314924
|  |  | 14131 | -2822.9 | * | L:314569 6EARLEYS 230 314574 6EVERETS 230 1 |  |  | 692.8 | 608 | 0.03003 |  | 0.01996 | 484 | 427.7 |  | 314914 | 314918
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590 | [8 empty] | 342835 | 342838
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | -0.10399 | -0.09678 | -2007.5 | -1734.3
|  |  | 14265 | -2245.7 | * | L:242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  | 2619.7 | 2317 | 0.13478 |  | 0.11716 | 2254.1 | 1991
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2590
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | -0.1821 | -0.09678 | -2007.5 | -1790.2
|  |  | 14276 | -2184.4 |  | L:135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  | 596.8 | 488 | 0.04979
Base Case
|  |  | 14288 | -2104.1 |  | L:242511 05BROADF 765 242518 05BROADF 500 4 |  |  | 1913.7 | 1710 | 0.09681
Base Case
|  |  | 14304 | -1897.8 | * | L:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  | 2348.3 | 2119 | 0.12083 |  | 0.09681 | 1884.9 | 1701.2
[7 empty] | C:242514 05J.FERR 765 242520 05J.FERR 500 1 | 1466
[7 empty] | Open 242514 05J.FERR 765 242520 05J.FERR 500 1 |  |  |  |  | 0.20506 | 0.11716 | 2259.6 | 2037.3
|  |  | 14314 | -1799.7 |  | L:200928 26FOURMILE 230 903645 W3-099 TAP 230 1 |  |  | -577.7 | -488 | -0.04986
Base Case
|  |  | 14317 | -1654.7 |  | L:200654 26ERIE E 230 903645 W3-099 TAP 230 1 |  |  | 570.5 | 488 | 0.04986
Base Case
|  |  | 14327 | -1415.4 | * | L:135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  | 678.1 | 607 | 0.05024 |  | 0.04979 | 596.8 | 526.3
[7 empty] | C:200595 26WAYNE 345 200826 26HANDSMLK 345 1 | 146
[7 empty] | Open 200595 26WAYNE 345 200826 26HANDSMLK 345 1 |  |  |  |  | -0.12751 | -0.00354 | -638 | -633
|  |  | 14332 | -1333.3 | * | L:200928 26FOURMILE 230 903645 W3-099 TAP 230 1 |  |  | -659.1 | -592 | -0.05031 |  | -0.04986 | -577.7 | -511.3
[7 empty] | C:200595 26WAYNE 345 200826 26HANDSMLK 345 1 | 146
[7 empty] | Open 200595 26WAYNE 345 200826 26HANDSMLK 345 1 |  |  |  |  | 0.12751 | -0.00354 | -638 | -633.3
|  |  | 14336 | -1189.6 | * | L:200654 26ERIE E 230 903645 W3-099 TAP 230 1 |  |  | 651.8 | 592 | 0.05031 |  | 0.04986 | 570.5 | 511.2
[7 empty] | C:200595 26WAYNE 345 200826 26HANDSMLK 345 1 | 146
[7 empty] | Open 200595 26WAYNE 345 200826 26HANDSMLK 345 1 |  |  |  |  | -0.12751 | -0.00354 | -638 | -633.8
|  |  | 14396 | -393.6 |  | L:242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  | 2254.1 | 2208 | 0.11716
Base Case
|  |  | 37342 | 509.9 | * | L:200819 26ERIE SE 230 200928 26FOURMILE 230 1F |  |  | -558.8 | -584 | -0.04938 |  | -0.04417 | -419.4 | -441.9
[7 empty] | C:200927 26FOURMILE 115 200928 26FOURMILE 230 6F | 2707
[7 empty] | Open 200927 26FOURMILE 115 200928 26FOURMILE 230 6F |  |  |  |  | 0.9153 | -0.00568 | -152.3 | -155.2
|  |  | 42582 | 789.2 | * | L:200706 26N.MESHPN 230 200708 26OXBOW 230 1 |  |  | 572.2 | 617 | 0.05679 |  | 0.05066 | 435 | 475
[7 empty] | C:200857 26MARSHALL 230 200909 26LOBO+ 230 1 | 190
[7 empty] | Open 200857 26MARSHALL 230 200909 26LOBO+ 230 1 |  |  |  |  | 0.38893 | 0.01576 | 352.8 | 365.2
|  |  | 42665 | 849.4 |  | L:200706 26N.MESHPN 230 200708 26OXBOW 230 1 |  |  | 435 | 478 | 0.05066
Base Case
|  |  | 44711 | 935.8 |  | L:314686 6CLOVER 230 314697 6HALIFAX 230 1 |  |  | 766.2 | 797 | 0.03294
Base Case
|  |  | 47158 | 1100.3 | * | L:200708 26OXBOW 230 208009 LACK 230 1 |  |  | 560.4 | 624 | 0.05776 |  | 0.05157 | 421.8 | 478.5
[7 empty] | C:200857 26MARSHALL 230 200909 26LOBO+ 230 1 | 190
[7 empty] | Open 200857 26MARSHALL 230 200909 26LOBO+ 230 1 |  |  |  |  | 0.39303 | 0.01576 | 352.8 | 370.1
|  |  | 47519 | 1381 |  | L:200708 26OXBOW 230 208009 LACK 230 1 |  |  | 421.8 | 493 | 0.05157
Base Case
|  |  | 47584 | 1501.5 | * | L:200767 26HOMER CT 230 200795 26SHELOCTA 230 1 |  |  | 849.7 | 917 | 0.04481 |  | 0.03888 | 551.8 | 610.2
[7 empty] | C:200769 26HOMER CY 345 235129 01ARMSTRONG 345 1F | 180
[7 empty] | Open 200769 26HOMER CY 345 235129 01ARMSTRONG 345 1F |  |  |  |  | 0.34164 | 0.01735 | 871.9 | 897.9
|  |  | 47609 | 1553.4 |  | L:200819 26ERIE SE 230 200928 26FOURMILE 230 1F |  |  | -419.4 | -488 | -0.04417
Base Case
|  |  | 47625 | 1604.2 | * | L:242510 05BAKER 765 242511 05BROADF 765 1 |  |  | 4277.9 | 4465 | 0.11665 |  | 0.08399 | 2881.3 | 3016
[7 empty] | C:242513 05CULLOD 765 242517 05WYOMIN 765 1 | 1463
[7 empty] | Open 242513 05CULLOD 765 242517 05WYOMIN 765 1 |  |  |  |  | 0.41473 | 0.07875 | 3367.4 | 3493.7
|  |  | 50194 | 2417.8 |  | L:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  | 1884.9 | 2119 | 0.09681
Base Case
|  |  | 52307 | 2700.8 | * | L:200706 26N.MESHPN 230 200924 26CANYON 230 1F |  |  | -507 | -617 | -0.04071 |  | -0.03484 | -375.6 | -469.7
[7 empty] | C:200857 26MARSHALL 230 200909 26LOBO+ 230 1 | 190
[7 empty] | Open 200857 26MARSHALL 230 200909 26LOBO+ 230 1 |  |  |  |  | -0.37261 | 0.01576 | 352.8 | 395.4
|  |  | 52477 | 3108.8 | * | L:200675 26E.TWANDA 230 200924 26CANYON 230 1F |  |  | 539.6 | 666 | 0.04064 |  | 0.03477 | 408.2 | 516.3
[7 empty] | C:200857 26MARSHALL 230 200909 26LOBO+ 230 1 | 190
[7 empty] | Open 200857 26MARSHALL 230 200909 26LOBO+ 230 1 |  |  |  |  | 0.37261 | 0.01576 | 352.8 | 401.8
|  |  | 52523 | 3226.5 |  | L:200706 26N.MESHPN 230 200924 26CANYON 230 1F |  |  | -375.6 | -488 | -0.03484
Base Case
|  |  | 52848 | 3538.6 | * | L:200011 KEYSTONE 500 235118 01SOBEND 500 1 |  |  | 2286.2 | 2598 | 0.08812 |  | 0.0648 | 1230.5 | 1459.8
[7 empty] | C:200011 KEYSTONE 500 235104 01CABOT 500 1 | 51
[7 empty] | Open 200011 KEYSTONE 500 235104 01CABOT 500 1 |  |  |  |  | 0.52183 | 0.04469 | 2023 | 2181.1
|  |  | 62117 | 3819.4 | * | L:235105 01DOUBS 500 314925 8PL VIEW 500 1 |  |  | 2070.4 | 2323 | 0.06613 |  | 0.04846 | 1724 | 1909.1
[7 empty] | C:200019 BURCHES 500 314922 8POSSUM 500 1 | 89
[7 empty] | Open 200019 BURCHES 500 314922 8POSSUM 500 1 |  |  |  |  | 0.2935 | 0.06019 | 1180.3 | 1410.2
|  |  | 62222 | 3855.3 | * | L:130763 HILSD230 230 200675 26E.TWANDA 230 1 |  |  | 378.8 | 531 | 0.03948 |  | 0.03948 | 100.8 | 253
[7 empty] | C:200675 26E.TWANDA 230 907461 X1-109 C 230 1 | 153
Open 200675 26E.TWANDA 230 907461 X1-109 C 230 1
|  |  | 66661 | 3963.3 |  | L:200675 26E.TWANDA 230 200924 26CANYON 230 1F |  |  | 408.2 | 546 | 0.03477
Base Case
|  |  | 66853 | 4270.5 | * | L:200769 26HOMER CY 345 B$0211 1.00 N |  |  | 574.1 | 807 | 0.05454 |  | 0.03129 | 314.2 | 447.8
[7 empty] | C:3Wnd: OPEN B$0411 S | 176
[7 empty] | Open 200767 26HOMER CT 230 B$0411 1.00 S |  |  |  |  | -0.76234 | -0.03053 | -327.4 | -457.8
Open 200769 26HOMER CY 345 B$0411 1.00 S
Open 202641 26HOMERCITYS23.0 B$0411 1.00 S
|  |  | 66874 | 4505 | * | L:200769 26HOMER CY 345 B$0411 1.00 S |  |  | 579.8 | 824 | 0.05421 |  | 0.03048 | 348.6 | 485.9
[7 empty] | C:3Wnd: OPEN B$0211 N | 175
[7 empty] | Open 200767 26HOMER CT 230 B$0211 1.00 N |  |  |  |  | -0.75815 | -0.03135 | -288.4 | -429.6
Open 200769 26HOMER CY 345 B$0211 1.00 N
Open 202640 26HOMERCITYN23.0 B$0211 1.00 N
|  |  | 66881 | 4607.5 |  | L:200767 26HOMER CT 230 200795 26SHELOCTA 230 1 |  |  | 551.8 | 731 | 0.03888
Base Case
|  |  | 66892 | 4737.7 | * | L:200767 26HOMER CT 230 B$0211 1.00 N |  |  | -548.3 | -807 | -0.0546 |  | -0.03135 | -288.4 | -436.9
[7 empty] | C:3Wnd: OPEN B$0411 S | 176
[7 empty] | Open 200767 26HOMER CT 230 B$0411 1.00 S |  |  |  |  | 0.76234 | -0.03053 | -327.4 | -472
Open 200769 26HOMER CY 345 B$0411 1.00 S
Open 202641 26HOMERCITYS23.0 B$0411 1.00 S
|  |  | 66895 | 4748.5 | * | L:342835 7N CLARK 345 342838 7SPURLOCK 345 1 |  |  | -999.3 | -1151 | -0.03195 |  | -0.02498 | -861.4 | -980.1
[7 empty] | C:242511 05BROADF 765 242518 05BROADF 500 4 | 1458
[7 empty] | Open 242511 05BROADF 765 242518 05BROADF 500 4 |  |  |  |  | -0.07202 | 0.09681 | 1913.7 | 2373.4
|  |  | 66902 | 4891.7 | * | L:200767 26HOMER CT 230 B$0411 1.00 S |  |  | -558.5 | -824 | -0.05427 |  | -0.03053 | -327.4 | -476.7
[7 empty] | C:3Wnd: OPEN B$0211 N | 175
[7 empty] | Open 200767 26HOMER CT 230 B$0211 1.00 N |  |  |  |  | 0.75815 | -0.03135 | -288.4 | -441.8
Open 200769 26HOMER CY 345 B$0211 1.00 N
Open 202640 26HOMERCITYN23.0 B$0211 1.00 N
|  |  | 66958 | 6350.9 | * | L:200795 26SHELOCTA 230 200810 26KEYSTONE 230 1 |  |  | 612.3 | 917 | 0.04798 |  | 0.03856 | 356.6 | 601.5
[7 empty] | C:200005 CONEM-GH 500 200011 KEYSTONE 500 1 | 27
[7 empty] | Open 200005 CONEM-GH 500 200011 KEYSTONE 500 1 |  |  |  |  | 0.22451 | 0.04195 | 1138.9 | 1405.3
|  |  | 67003 | 6632.3 | * | L:242508 05AMOS 765 242513 05CULLOD 765 1 |  |  | 3599.1 | 4253 | 0.09859 |  | 0.04676 | 2035.3 | 2345.4
[7 empty] | C:242513 05CULLOD 765 242923 05GAVIN 765 1 | 1464
[7 empty] | Open 242513 05CULLOD 765 242923 05GAVIN 765 1 |  |  |  |  | -0.70776 | -0.07323 | -2209.5 | -2695.2
|  |  | 71605 | 6980.8 | * | L:135398 SW345 345 200942 FARM_V_345 345 1 |  |  | 391.7 | 769 | 0.05405 |  | 0.04239 | 251.9 | 547.7
[7 empty] | C:135251 S RIPLEY 230 200654 26ERIE E 230 1 | 2545
[7 empty] | Open 135251 S RIPLEY 230 200654 26ERIE E 230 1 |  |  |  |  | 0.23429 | 0.04979 | 596.8 | 944.4
|  |  | 72499 | 7410.9 | * | L:130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  | 537.1 | 927 | 0.05261 |  | 0.05074 | 440.4 | 816.5
[7 empty] | C:200004 CNASTONE 500 200013 PEACHBTM 500 1 | 21
[7 empty] | Open 200004 CNASTONE 500 200013 PEACHBTM 500 1 |  |  |  |  | -0.02279 | -0.08201 | -4243.1 | -4850.9
|  |  | 76491 | 8232.5 | * | L:314903 8CHCKAHM 500 314924 8SURRY 500 1 |  |  | 1449.2 | 1924 | 0.05767 |  | 0.03598 | 1042.8 | 1338.9
[7 empty] | C:314902 8CARSON 500 314914 8MDLTHAN 500 1 | 2462
[7 empty] | Open 314902 8CARSON 500 314914 8MDLTHAN 500 1 |  |  |  |  | -0.30698 | -0.07068 | -1324 | -1905.9
|  |  | 76512 | 8428.6 | * | L:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  | -2425.6 | -3424 | -0.11846 |  | -0.09678 | -2007.5 | -2823.2
[7 empty] | C:242514 05J.FERR 765 242520 05J.FERR 500 1 | 1466
[7 empty] | Open 242514 05J.FERR 765 242520 05J.FERR 500 1 |  |  |  |  | -0.18501 | 0.11716 | 2259.6 | 3247.1
|  |  | 76519 | 8552.6 | * | L:200568 26ERIE SO. 230 200600 26ERIE SO 345 5 |  |  | 368.2 | 776 | 0.04769 |  | 0.02536 | 183.5 | 400.4
[7 empty] | C:200600 26ERIE SO 345 200819 26ERIE SE 230 8 | 149
[7 empty] | Open 200600 26ERIE SO 345 200819 26ERIE SE 230 8 |  |  |  |  | -0.78438 | -0.02846 | -235.5 | -478.9
|  |  | 76534 | 8731.1 |  | L:242513 05CULLOD 765 242517 05WYOMIN 765 1 |  |  | 3367.4 | 4055 | 0.07875
Base Case
|  |  | 76560 | 9133.8 |  | L:135398 SW345 345 200942 FARM_V_345 345 1 |  |  | 251.9 | 639 | 0.04239
Base Case
|  |  | 76591 | 9251.7 |  | L:200599 26ERIE W 345 238547 02AT 345 1 |  |  | 941.2 | 1560 | 0.06689
Base Case
|  |  | 76664 | 9324 | * | L:314914 8MDLTHAN 500 314918 8NO ANNA 500 1 |  |  | -1741.7 | -2598 | -0.09184 |  | -0.06796 | -1457.7 | -2091.4
[7 empty] | C:314908 8ELMONT 500 314911 8LDYSMTH 500 1 | 2477
[7 empty] | Open 314908 8ELMONT 500 314911 8LDYSMTH 500 1 |  |  |  |  | 0.37629 | -0.06345 | -754.7 | -1346.4
|  |  | 77029 | 9379.8 | * | L:200599 26ERIE W 345 200600 26ERIE SO 345 1 |  |  | -616.8 | -1139 | -0.05567 |  | -0.05382 | -417.2 | -922
[7 empty] | C:200595 26WAYNE 345 200599 26ERIE W 345 1 | 145
[7 empty] | Open 200595 26WAYNE 345 200599 26ERIE W 345 1 |  |  |  |  | -0.35674 | 0.00517 | 559.7 | 608.2
|  |  | 81076 | 9437.7 | * | L:238547 02AT 345 239082 02S8-ATT 345 1 |  |  | 519.2 | 828 | 0.03271 |  | 0.00869 | 228.7 | 310.7
[7 empty] | C:238547 02AT 345 239036 02PERRY 345 1 | 1381
[7 empty] | Open 238547 02AT 345 239036 02PERRY 345 1 |  |  |  |  | 0.41284 | 0.0582 | 703.7 | 1252.9
|  |  | 81520 | 9569.7 |  | L:130757 WATRC345 345 200930 26MAINESBURG 345 1 |  |  | 440.4 | 926 | 0.05074
Base Case
|  |  | 85884 | 9681.3 |  | L:130763 HILSD230 230 200675 26E.TWANDA 230 1 |  |  | 100.8 | 483 | 0.03948
Base Case
|  |  | 85925 | 9709 |  | L:200795 26SHELOCTA 230 200810 26KEYSTONE 230 1 |  |  | 356.6 | 731 | 0.03856
Base Case
|  |  | 85968 | 9790.2 |  | L:200769 26HOMER CY 345 B$0411 1.00 S |  |  | 348.6 | 647 | 0.03048
Base Case
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow

## SERC
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 14:02 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_SERC.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_SERC.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes
SOURCE | SINK | 10000 | 122 | -9615.3 | * | L:340624 5BRTAP 161 360043 5PARADISE FP 161 1 |  |  | 827.1 | 446 | 0.03964 |  | 0.03628 | 712.3 | 363.4 |  | 242518 | 360106
[7 empty] | C:360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 | 3300 | [8 empty] | 242520 | 306719
[7 empty] | Open 360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  |  |  | 0.0687 | 0.04879 | 1671.7 | 1202.6 |  | 304070 | 314697
|  |  | 150 | -8221.5 | * | L:304070 6PERSON230 T 230 314697 6HALIFAX 230 1 |  |  | -1213.1 | -712 | -0.06094 |  | -0.03593 | -694.1 | -398.7 | DEP/DVP | 304183 | 314935
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2074 | [7 empty] | Valid - No OpGuide | 304451 | 314574
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | 0.2585 | -0.09678 | -2007.5 | -1211.8 |  | 306007 | 306008
|  |  | 2638 | -7338.3 |  | L:340624 5BRTAP 161 360043 5PARADISE FP 161 1 |  |  | 712.3 | 446 | 0.03628 | [5 empty] | 306008 | 309002
[7 empty] | Base Case | [9 empty] | 306008 | 380011
|  |  | 5400 | -6003.4 | * | L:306008 8OCONEE 500 380011 8S HALL 500 1 |  |  | 3235.7 | 2598 | 0.10622 |  | 0.08851 | 2706.7 | 2175.3 | DEC/SOCO | 306113 | 309002
[7 empty] | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | 1232 | [7 empty] | Valid - No OpGuide | 306337 | 306546
[7 empty] | Open 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 |  |  |  |  | -0.22901 | -0.07733 | -2310.1 | -1845.8 |  | 306540 | 306546
|  |  | 5401 | -5988.8 | * | L:324072 8PINEVL 500 324112 7PINEVIL 345 1 |  |  | -824.7 | -580 | -0.04085 |  | -0.02516 | -519.1 | -368.4 |  | 306712 | 306716
[7 empty] | C:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 | 5024 | [8 empty] | 306712 | 306716
[7 empty] | Open 242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  |  |  | -0.16209 | 0.09681 | 1884.9 | 1305.2 |  | 324072 | 324073
|  |  | 5462 | -4828.8 | * | L:304451 6PA-GREENVIL 230 314574 6EVERETS 230 1 |  |  | -628 | -478 | -0.03106 |  | -0.02128 | -425 | -322.2 | DEP/DVP | 324072 | 324112
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2074 | [7 empty] | Valid - No OpGuide | 324073 | 360102
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | 0.10113 | -0.09678 | -2007.5 | -1540.2 |  | 324100 | 324102
|  |  | 5474 | -4317.7 |  | L:304070 6PERSON230 T 230 314697 6HALIFAX 230 1 |  |  | -694.1 | -539 | -0.03593 |  |  |  |  | DEP/DVP | 336562 | 336839
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide | 340624 | 360043
|  |  | 5541 | -4017.6 | * | L:380011 8S HALL 500 382035 6S HALL LS 230 1 |  |  | 2285 | 2016 | 0.06694 |  | 0.02439 | 1466.7 | 1368.7 | SOCO | 346992 | 360002
[7 empty] | C:380003 8NORCROSS 500 380011 8S HALL 500 1 | 1190 | [7 empty] | Valid Limit | 360001 | 360002
[7 empty] | Open 380003 8NORCROSS 500 380011 8S HALL 500 1 |  |  |  |  | -0.6636 | -0.06412 | -1233.1 | -975.5 |  | 360001 | 360015
|  |  | 5714 | -3211.8 | * | L:306337 8NEWPORT 500 306546 8MCGUIRE 500 1 |  |  | -1454.6 | -1299 | -0.04844 |  | -0.03875 | -997.6 | -873.1 | DEC | 360015 | 360016
[7 empty] | C:306540 6MCGUIRE 230 306546 8MCGUIRE 500 A1 | 526 | [7 empty] | Valid - No OpGuide | 360015 | 360040
[7 empty] | Open 306540 6MCGUIRE 230 306546 8MCGUIRE 500 A1 |  |  |  |  | 0.4412 | -0.02196 | -1035.8 | -965.2 |  | 360065 | 360081
|  |  | 5762 | -2594.7 |  | L:306008 8OCONEE 500 380011 8S HALL 500 1 |  |  | 2706.7 | 2477 | 0.08851 |  |  |  |  | DEC/SOCO | 360081 | 360085
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide | 360081 | 360110
|  |  | 5809 | -2245.7 | * | L:242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  | 2619.7 | 2317 | 0.13478 |  | 0.11716 | 2254.1 | 1991 | DEC/AEP | 360081 | 360662
[7 empty] | C:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 | 2074 | [7 empty] | Valid - No OpGuide | 360085 | 360110
[7 empty] | Open 304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  |  |  | -0.1821 | -0.09678 | -2007.5 | -1790.2 |  | 360097 | 360102
|  |  | 5874 | -1888.4 | * | L:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  | 2347.2 | 2119 | 0.12083 |  | 0.09681 | 1884.9 | 1702.1 |  | 360662 | 382499
[7 empty] | C:242520 05J.FERR 500 306719 8ANTIOCH 500 1 | 2271 | [8 empty] | 380003 | 380011
[7 empty] | Open 242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  |  |  | 0.20506 | 0.11716 | 2254.1 | 2032.9 |  | 380011 | 382035
|  |  | 15186 | -919.1 | * | L:324100 7ALCALDE 345 324102 7BROWN N 345 1 |  |  | -984.4 | -956 | -0.0309 |  | -0.02181 | -704.2 | -684.2 |  | 380013 | 380018
[7 empty] | C:324112 7PINEVIL 345 325074 7W.GARRKU 345 1 | 696 | [8 empty] | 380014 | 400356
[7 empty] | Open 324112 7PINEVIL 345 325074 7W.GARRKU 345 1 |  |  |  |  | 0.44979 | -0.02021 | -622.9 | -604.3 |  | 380015 | 400356
|  |  | 15402 | -666.6 | * | L:306008 8OCONEE 500 309002 8KATRTRT 500 Z1 |  |  | -1690 | -1663 | -0.04054 |  | -0.03718 | -1443.6 | -1418.8 | DEC | 380021 | 382499
[7 empty] | C:306113 8JOCASSE 500 307690 6JOCASSE BK 230 1 | 445 | [7 empty] | Valid - No OpGuide | 380025 | 380088
[7 empty] | Open 306113 8JOCASSE 500 307690 6JOCASSE BK 230 1 |  |  |  |  | -0.80871 | 0.00416 | 304.7 | 301.9 |  | 382035 | 382766
|  |  | 15525 | -393.6 |  | L:242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  | 2254.1 | 2208 | 0.11716 |  |  |  |  | DEC/AEP
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide
|  |  | 15601 | -178.3 | * | L:306712 6ANTIOCH 230 306716 6MITCH R 230 2 |  |  | 837.1 | 830 | 0.03975 |  | 0.01808 | 627 | 623.7 | DEC
[7 empty] | C:306719 8ANTIOCH 500 309035 8ROCKSPGRTRT 500 1 | 557 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 306719 8ANTIOCH 500 309035 8ROCKSPGRTRT 500 1 |  |  |  |  | 0.26972 | 0.08033 | 779.1 | 764.8
|  |  | 15632 | -67.7 | * | L:360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 |  |  | 2604.8 | 2598.1 | 0.09886 |  | 0.07565 | 1895.2 | 1890.1
[7 empty] | C:306008 8OCONEE 500 380011 8S HALL 500 1 | 421
[7 empty] | Open 306008 8OCONEE 500 380011 8S HALL 500 1 |  |  |  |  | 0.26217 | 0.08851 | 2706.7 | 2700.7
|  |  | 15677 | 50.5 | * | L:306712 6ANTIOCH 230 306716 6MITCH R 230 1 |  |  | 838 | 840 | 0.03979 |  | 0.0181 | 627.6 | 628.5 | DEC
[7 empty] | C:306719 8ANTIOCH 500 309035 8ROCKSPGRTRT 500 1 | 557 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 306719 8ANTIOCH 500 309035 8ROCKSPGRTRT 500 1 |  |  |  |  | 0.27001 | 0.08033 | 779.1 | 783.1
|  |  | 25435 | 552.2 | * | L:306007 6OCONEE 230 306008 8OCONEE 500 A1 |  |  | 1308.4 | 1326.5 | 0.03283 |  | 0.00864 | 366.8 | 371.5 | DEC
[7 empty] | C:306113 8JOCASSE 500 309002 8KATRTRT 500 1 | 447 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 306113 8JOCASSE 500 309002 8KATRTRT 500 1 |  |  |  |  | 0.65061 | 0.03718 | 1447.3 | 1467.8
|  |  | 26081 | 1993 | * | L:360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  | 1849.1 | 1958.9 | 0.05511 |  | 0.04879 | 1671.7 | 1768.9
[7 empty] | C:300035 8NEWMAD 500 338187 8DELL% 500 1 | 2018
[7 empty] | Open 300035 8NEWMAD 500 338187 8DELL% 500 1 |  |  |  |  | 0.15434 | 0.04097 | 1149.1 | 1230.8
|  |  | 28604 | 2417.8 |  | L:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  | 1884.9 | 2119 | 0.09681
Base Case
|  |  | 31216 | 2849.2 | * | L:360662 8BRADLEY TN 500 382499 8CONASAUGA 500 1 |  |  | 2491.3 | 2783 | 0.10238 |  | 0.07733 | 1725.3 | 1945.6 | SOCO/TVA
[7 empty] | C:306008 8OCONEE 500 380011 8S HALL 500 1 | 421 | [7 empty] | Valid Limit
[7 empty] | Open 306008 8OCONEE 500 380011 8S HALL 500 1 |  |  |  |  | 0.28301 | 0.08851 | 2706.7 | 2958.9
|  |  | 31238 | 2953.9 | * | L:360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 |  |  | 1614.9 | 1732.1 | 0.03969 |  | 0.03334 | 1436.9 | 1535.4
[7 empty] | C:300035 8NEWMAD 500 338187 8DELL% 500 1 | 2018
[7 empty] | Open 300035 8NEWMAD 500 338187 8DELL% 500 1 |  |  |  |  | 0.15485 | 0.04097 | 1149.1 | 1270.2
|  |  | 31240 | 2958.4 | * | L:306540 6MCGUIRE 230 306546 8MCGUIRE 500 A1 |  |  | -1477.7 | -1593.4 | -0.03912 |  | -0.02196 | -1035.8 | -1100.7 | DEC
[7 empty] | C:306337 8NEWPORT 500 306546 8MCGUIRE 500 1 | 488 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 306337 8NEWPORT 500 306546 8MCGUIRE 500 1 |  |  |  |  | 0.44295 | -0.03875 | -997.6 | -1112.2
|  |  | 31248 | 3039 | * | L:360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1 |  |  | -2268.9 | -2575.6 | -0.10094 |  | -0.06281 | -1344.9 | -1535.7
[7 empty] | C:360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1 | 3525
[7 empty] | Open 360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1 |  |  |  |  | -0.72128 | 0.05286 | 1281.1 | 1441.7
|  |  | 31275 | 3446.7 | * | L:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 |  |  | -3076.1 | -3429 | -0.10238 |  | -0.07733 | -2310.1 | -2576.6 | SOCO
[7 empty] | C:306008 8OCONEE 500 380011 8S HALL 500 1 | 421 | [7 empty] | Valid Limit
[7 empty] | Open 306008 8OCONEE 500 380011 8S HALL 500 1 |  |  |  |  | -0.28301 | 0.08851 | 2706.7 | 3011.8
|  |  | 31278 | 3462 | * | L:324072 8PINEVL 500 324073 8POCKETN 500 1 |  |  | 821.6 | 963 | 0.04085 |  | 0.02516 | 516 | 603.1
[7 empty] | C:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 | 5024
[7 empty] | Open 242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  |  |  | 0.16209 | 0.09681 | 1884.9 | 2220.1
|  |  | 31288 | 3648 | * | L:360085 8WBNP #1 500 360110 8HIWASSEE TN 500 1 |  |  | 2241.6 | 2598.1 | 0.09772 |  | 0.05286 | 1281.1 | 1473.9
[7 empty] | C:360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1 | 3505
[7 empty] | Open 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1 |  |  |  |  | -0.71425 | -0.06281 | -1344.9 | -1574
|  |  | 31297 | 3902.7 | * | L:380003 8NORCROSS 500 380011 8S HALL 500 1 |  |  | -2376.5 | -2701 | -0.08314 |  | -0.06412 | -1233.1 | -1483.3 | SOCO
[7 empty] | C:380011 8S HALL 500 382035 6S HALL LS 230 1 | 1210 | [7 empty] | Valid Limit
[7 empty] | Open 380011 8S HALL 500 382035 6S HALL LS 230 1 |  |  |  |  | -0.77962 | 0.02439 | 1466.7 | 1561.9
|  |  | 31324 | 4448 | * | L:360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 |  |  | -1468 | -1732.1 | -0.05937 |  | -0.03658 | -787.2 | -949.9
[7 empty] | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | 1232
[7 empty] | Open 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 |  |  |  |  | 0.29471 | -0.07733 | -2310.1 | -2654.1
|  |  | 31354 | 4917.8 | * | L:380025 8MCGRAU FORD 500 380088 6MCGRAU F LS 230 1 |  |  | 1775.3 | 2016 | 0.04894 |  | 0.01331 | 1115.7 | 1181.1 | SOCO
[7 empty] | C:380020 8BOWEN 500 380021 8MOSTELLER 500 1 | 1229 | [7 empty] | Valid Limit
[7 empty] | Open 380020 8BOWEN 500 380021 8MOSTELLER 500 1 |  |  |  |  | -0.55662 | -0.06403 | -1185 | -1499.9
|  |  | 31444 | 5479.6 |  | L:306113 8JOCASSE 500 309002 8KATRTRT 500 1 |  |  | 1447.3 | 1651 | 0.03718 |  |  |  |  | DEC
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide
|  |  | 31526 | 5668.7 | * | L:380015 8THALMANN 500 400356 DUVAL 500 1 |  |  | 1926.9 | 2598 | 0.11838 |  | 0.07567 | 1163.1 | 1592 | SOCO/FL
[7 empty] | C:380014 8HATCH 500 400356 DUVAL 500 1 | 2700 | [7 empty] | Valid Limit
[7 empty] | Open 380014 8HATCH 500 400356 DUVAL 500 1 |  |  |  |  | 0.73898 | 0.05779 | 1033.7 | 1361.3
|  |  | 34978 | 5886.8 |  | L:360015 8MARSHALL KY 500 360040 8CUMBERLAND 500 1 |  |  | 1671.7 | 1958.9 | 0.04879
Base Case
|  |  | 38433 | 5900.5 |  | L:306008 8OCONEE 500 309002 8KATRTRT 500 Z1 |  |  | -1443.6 | -1663 | -0.03718 |  |  |  |  | DEC
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide
|  |  | 41444 | 6204.4 |  | L:306337 8NEWPORT 500 306546 8MCGUIRE 500 1 |  |  | -997.6 | -1238 | -0.03875 |  |  |  |  | DEC
[7 empty] | Base Case | [8 empty] | Valid - No OpGuide
|  |  | 41615 | 6481.6 | * | L:336562 8FRANKLIN% 500 336839 8R.BRASWELL% 500 1 |  |  | -1489.9 | -1732 | -0.03735 |  | -0.02364 | -525.4 | -678.6
[7 empty] | C:336562 8FRANKLIN% 500 336820 8GGNS% 500 1 | 944
[7 empty] | Open 336562 8FRANKLIN% 500 336820 8GGNS% 500 1 |  |  |  |  | 0.69007 | -0.01987 | -1397.7 | -1526.4
|  |  | 41687 | 6820.8 | * | L:324073 8POCKETN 500 360102 8PHIPPS B NP 500 1 |  |  | 994.4 | 1386 | 0.05741 |  | 0.03506 | 559.2 | 798.3
[7 empty] | C:242518 05BROADF 500 360106 8SULLIVAN TN 500 1 | 5024
[7 empty] | Open 242518 05BROADF 500 360106 8SULLIVAN TN 500 1 |  |  |  |  | 0.2309 | 0.09681 | 1884.9 | 2545.2
|  |  | 41746 | 7075.6 |  | L:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  | 933.8 | 1200 | 0.03763
Base Case
|  |  | 41882 | 7515.4 | * | L:380014 8HATCH 500 400356 DUVAL 500 1 |  |  | 1792.6 | 2598 | 0.10717 |  | 0.05779 | 1033.7 | 1468 | SOCO/FL
[7 empty] | C:380015 8THALMANN 500 400356 DUVAL 500 1 | 2701 | [7 empty] | Valid Limit
[7 empty] | Open 380015 8THALMANN 500 400356 DUVAL 500 1 |  |  |  |  | 0.65249 | 0.07567 | 1163.1 | 1731.8
|  |  | 42169 | 7701.5 | * | L:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 |  |  | 1023.9 | 1319 | 0.03832 |  | 0.03763 | 933.8 | 1223.5
[7 empty] | C:360001 8SHAWNEE FP 500 360693 5SHAWNEE B12 161 12 | 3269
[7 empty] | Open 360001 8SHAWNEE FP 500 360693 5SHAWNEE B12 161 12 |  |  |  |  | -0.13053 | -0.00534 | -690.1 | -731.2
|  |  | 46703 | 7829.1 | * | L:360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1 |  |  | -1706.3 | -2598.1 | -0.11391 |  | -0.10167 | -1332.2 | -2128.1
[7 empty] | C:306008 8OCONEE 500 380011 8S HALL 500 1 | 421
[7 empty] | Open 306008 8OCONEE 500 380011 8S HALL 500 1 |  |  |  |  | -0.13824 | 0.08851 | 2706.7 | 3399.7
|  |  | 47057 | 8437.2 | * | L:304183 8WAKE 500 TT 500 314935 8BRUNSWICK 500 1 |  |  | -2424.5 | -3424 | -0.11846 |  | -0.09678 | -2007.5 | -2824.1 | DEP/DVP
[7 empty] | C:242520 05J.FERR 500 306719 8ANTIOCH 500 1 | 2271 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 242520 05J.FERR 500 306719 8ANTIOCH 500 1 |  |  |  |  | -0.18501 | 0.11716 | 2254.1 | 3242.6
|  |  | 47180 | 8652.8 | * | L:306113 8JOCASSE 500 309002 8KATRTRT 500 1 |  |  | 1667.5 | 2053 | 0.04455 |  | 0.03718 | 1447.3 | 1769 | DEC
[7 empty] | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | 1232 | [7 empty] | Valid - No OpGuide
[7 empty] | Open 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 |  |  |  |  | -0.09533 | -0.07733 | -2310.1 | -2979.3
|  |  | 49478 | 8852.8 |  | L:360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 |  |  | 1436.9 | 1732.1 | 0.03334
Base Case
|  |  | 52777 | 9239.3 | * | L:360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11 |  |  | -1098.7 | -1382.6 | -0.03073 |  | -0.028 | -746.8 | -1005.5
[7 empty] | C:360001 8SHAWNEE FP 500 360693 5SHAWNEE B12 161 12 | 3269
[7 empty] | Open 360001 8SHAWNEE FP 500 360693 5SHAWNEE B12 161 12 |  |  |  |  | 0.50993 | -0.00534 | -690.1 | -739.5
|  |  | 53813 | 9287 | * | L:360015 8MARSHALL KY 500 360016 5MARSHALL KY 161 1 |  |  | -1031.2 | -1344 | -0.03368 |  | -0.01544 | -245.3 | -388.7
[7 empty] | C:360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 | 3268
[7 empty] | Open 360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 |  |  |  |  | -0.54696 | 0.03334 | 1436.9 | 1746.6
|  |  | 54958 | 9291.3 |  | L:360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 |  |  | 1895.2 | 2598.1 | 0.07565
Base Case
|  |  | 56783 | 9328.7 | * | L:360081 8SEQUOYAH NP 500 360110 8HIWASSEE TN 500 1 |  |  | -1738.1 | -2575.6 | -0.08977 |  | -0.04735 | -829.8 | -1271.4
[7 empty] | C:360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1 | 3505
[7 empty] | Open 360081 8SEQUOYAH NP 500 360085 8WBNP #1 500 1 |  |  |  |  | 0.67544 | -0.06281 | -1344.9 | -1930.8
|  |  | 57081 | 9405.9 | * | L:380013 8BONAIRE 500 380018 8SCHERER 500 1 |  |  | -1880.3 | -2439 | -0.05939 |  | -0.04562 | -1583.4 | -2012.6 | SOCO/FL
[7 empty] | C:380015 8THALMANN 500 382158 8MCCALL RD 500 1 | 1218 | [7 empty] | Valid Limit
[7 empty] | Open 380015 8THALMANN 500 382158 8MCCALL RD 500 1 |  |  |  |  | 0.24782 | -0.05557 | -1198.1 | -1720.7
|  |  | 57256 | 8934.9 |  | L:360662 8BRADLEY TN 500 382499 8CONASAUGA 500 1 |  |  | 1904 | 2598 | 0.07768
Base Case
|  |  | 57281 | 8992.2 | * | L:360015 8MARSHALL KY 500 360016 5MARSHALL KY 161 1 |  |  | -1040.9 | -1344 | -0.03371 |  | -0.01544 | -247 | -385.9
[7 empty] | C:360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 | 3268
[7 empty] | Open 360001 8SHAWNEE FP 500 360015 8MARSHALL KY 500 1 |  |  |  |  | -0.54696 | 0.03339 | 1451.5 | 1751.8
|  |  | 57357 | 9442.3 | * | L:382035 6S HALL LS 230 382766 6S HALL B1 230 Z1 |  |  | 1296.9 | 1659 | 0.03835 |  | 0.01417 | 802.2 | 936 | SOCO/FL
[7 empty] | C:380003 8NORCROSS 500 380011 8S HALL 500 1 | 1190 | [7 empty] | Valid Limit
[7 empty] | Open 380003 8NORCROSS 500 380011 8S HALL 500 1 |  |  |  |  | -0.376 | -0.06429 | -1315.7 | -1922.8
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow

## SPP
FCITC Single Study
PSS(R)MUST 11.1 -- Managing and Utilizing System Transmission -- MON, NOV 17 2014 14:03 <FC2001.1>
2023 RTEP SUMMER PEAK CASE
CEII DO NOT RELEASE.
Case.File M:\EIPC\2014\Cases\HeatWave_Drought\Pass2_10-28-2014\S23_EIPC_HeatWaveDrought_10-28-2014_20000MW-Pass2_v33.sav
Subsys.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S.sub
Monit.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_SPP.mon
Contin.File M:\EIPC\2014\RunFiles\HeatWave_Drought\HeatWave_Drought_23S_SPP.con
Exclud.File none
From | To | Transfer Level | N | FCITC | Flag | Limiting Constraint | Contingency | Ncon | PreShift | Rating | TDF | LODF | PTDF | Base Case Init | Base Case Final | Notes | Limiting Constraint
SOURCE | SINK | 10000 | 1 | -63.3 | * | L:532772 STRANGR7 345 542982 IATAN 7 345 1 |  |  | -1196.9 | -1195 | -0.03025 |  | -0.02639 | -1110.3 | -1108.7 |  | 532772 | 542982
[7 empty] | C:541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 551
[7 empty] | Open 541200 PHILL 7 345 541201 SIBLEY 7 345 1 |  |  |  |  | 0.19272 | -0.02005 | -449.2 | -447.9
Note on A12: PTI: Exporting Subsystem
Note on B12: PTI: Importing Subsystem
Note on C12: PTI: Maximum Test Level
Note on D12: PTI: Number of violations
Note on E12: PTI: First Contingency Incremental Transfer Capability
Note on F12: PTI: *-repeated n times, R- removed at reported test level
Note on G12: PTI: Branch, Flowgate or Interface
Note on H12: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I12: PTI: Contingency Index
Note on J12: PTI: MW Flow before the transfer
Note on K12: PTI: Rating (Base case or Contingent)
Note on L12: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on M12: PTI: Line Outage Distribution Factor (single branch outages only)
Note on N12: PTI: Power Transfer Distribution Factor(Base Case )
Note on O12: PTI: Pre-Shift Base Case Flow
Note on P12: PTI: PostShift BaseCase MW Flow
Note on S12: PTI: Branch, Flowgate or Interface

## ALL_With_Areas
FRCC | [10 empty] | Region | KV range | [7 empty] | Total | Tie Lines
380015 | 400356 | [7 empty] | Transformer | Area Ties |  | 765 | 500 | 345 | 230 | 161 | 138 | 115 | xfr |  | Regional Tie Line | Intra-Regional Line
380014 | 400356 |  | From Bus | Area | kV | To Bus | Area | kV |  |  | FRCC | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0
|  | FRCC | 380015 | 346 | 500 | 400356 | 401 | 500 |  | Regional Tie Line | MISO | 0 | 1 | 11 | 0 | 1 | 0 | 0 | 0 | 13 | 1 | 6
MISO |  | FRCC | 380014 | 346 | 500 | 400356 | 401 | 500 |  | Regional Tie Line | NPCC | 0 | 0 | 9 | 11 | 0 | 0 | 0 | 2 | 22 | 4 | 18
340624 | 360043 |  | From Bus | Area | kV | To Bus | Area | kV |  |  | PJM | 3 | 10 | 6 | 15 | 0 | 0 | 0 | 5 | 39 | 9 | 30
340624 | 360043 | MISO | 300038 | 330 | 345 | 344974 | 356 | 345 |  | #N/A | NON-RTO SERC | 0 | 24 | 2 | 5 | 1 | 0 | 0 | 7 | 39 | 9 | 30
300041 | 344154 | MISO | 300041 | 330 | 345 | 344154 | 356 | 345 |  | #N/A | SPP | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
346895 | 348151 | MISO | 300041 | 330 | 345 | 344327 | 356 | 345 |  | #N/A | [10 empty] | 22.73% | 77.27%
300038 | 344974 | MISO | 336562 | 326 | 500 | 336839 | 326 | 500 |  | Intra-Regional_Line
344974 | 345773 | MISO | 340624 | 314 | 161 | 360043 | 347 | 161 |  | Regional_Tie_Line
346895 | 348151 | MISO | 344224 | 356 | 345 | 344327 | 356 | 345 |  | Intra-Regional_Line
345667 | 345668 | MISO | 344974 | 356 | 345 | 345773 | 356 | 345 |  | Intra-Regional Line
344974 | 345773 | MISO | 345667 | 356 | 345 | 345668 | 356 | 345 |  | Intra-Regional Line
348493 | 348827 | MISO | 346895 | 357 | 345 | 348151 | 357 | 345 |  | Intra-Regional Line
347830 | 348493 | MISO | 346992 | 357 | 345 | 348827 | 357 | 345 |  | Intra-Regional Line
300038 | 344974 | MISO | 346992 | 357 | 345 | 360002 | 347 | 345 |  | Regional Tie Line
346992 | 360002 | MISO | 347830 | 357 | 345 | 348493 | 357 | 345 |  | Intra-Regional Line
348493 | 348827 | MISO | 348493 | 357 | 345 | 348827 | 357 | 345 |  | Intra-Regional Line
300038 | 344974 |  | From Bus | Area | kV | To Bus | Area | kV
346992 | 348827 | NPCC | 130753 | 102 | 345 | 130755 | 102 | 345 |  | Intra-Regional Line
336562 | 336839 | NPCC | 130755 | 102 | 345 | 130757 | 102 | 345 |  | Intra-Regional Line
346992 | 360002 | NPCC | 130755 | 102 | 345 | 130839 | 102 | 115 | xfr | Intra-Regional Line
344224 | 344327 | NPCC | 130755 | 102 | 345 | 131157 | 102 | 345 |  | Intra-Regional Line
300041 | 344327 | NPCC | 130756 | 102 | 345 | 135398 | 102 | 345 |  | Intra-Regional Line
347830 | 348493 | NPCC | 130757 | 102 | 345 | 130768 | 102 | 230 | xfr | Intra-Regional Line
|  | NPCC | 130757 | 102 | 345 | 200930 | 10 | 345 |  | Regional Tie Line
NPCC |  | NPCC | 130762 | 102 | 230 | 130767 | 102 | 230 |  | Intra-Regional Line
130762 | 130767 | NPCC | 130762 | 102 | 230 | 135413 | 102 | 230 |  | Intra-Regional Line
135415 | 147842 | NPCC | 130763 | 102 | 230 | 200675 | 10 | 230 |  | Regional Tie Line
135415 | 147842 | NPCC | 130768 | 102 | 230 | 130876 | 102 | 230 |  | Intra-Regional Line
130755 | 130839 | NPCC | 131157 | 102 | 345 | 136153 | 102 | 345 |  | Intra-Regional Line
135250 | 135251 | NPCC | 135250 | 102 | 230 | 135251 | 102 | 230 |  | Intra-Regional Line
135251 | 200654 | NPCC | 135250 | 102 | 230 | 135413 | 102 | 230 |  | Intra-Regional Line
135250 | 135251 | NPCC | 135250 | 102 | 230 | 146000 | 102 | 230 |  | Intra-Regional Line
135250 | 135413 | NPCC | 135251 | 102 | 230 | 200654 | 10 | 230 |  | Regional Tie Line
135251 | 200654 | NPCC | 135398 | 102 | 345 | 200942 | 10 | 345 |  | Regional Tie Line
135413 | 146000 | NPCC | 135413 | 102 | 230 | 146000 | 102 | 230 |  | Intra-Regional Line
135250 | 146000 | NPCC | 135415 | 102 | 230 | 147842 | 102 | 230 |  | Intra-Regional Line
130762 | 135413 | NPCC | 135415 | 102 | 230 | 147842 | 102 | 230 |  | Intra-Regional Line
130768 | 130876 | NPCC | 136150 | 102 | 345 | 149001 | 102 | 345 |  | Intra-Regional Line
131157 | 136153 | NPCC | 136150 | 102 | 345 | 149001 | 102 | 345 |  | Intra-Regional Line
135398 | 200942 |  | From Bus | Area | kV | To Bus | Area | kV
130755 | 131157 | PJM | 130757 | 102 | 345 | 200930 | 10 | 345 |  | Regional Tie Line
130755 | 130757 | PJM | 130763 | 102 | 230 | 200675 | 10 | 230 |  | Regional Tie Line
130763 | 200675 | PJM | 135251 | 102 | 230 | 200654 | 10 | 230 |  | Regional Tie Line
130757 | 200930 | PJM | 135398 | 102 | 345 | 200942 | 10 | 345 |  | Regional Tie Line
130755 | 130757 | PJM | 200003 | 10 | 500 | 200004 | 10 | 500 |  | Intra-Regional Line
130757 | 130768 | PJM | 200004 | 10 | 500 | 200013 | 10 | 500 |  | Intra-Regional Line
130753 | 130755 | PJM | 200011 | 10 | 500 | 235104 | 10 | 500 |  | Intra-Regional Line
135398 | 200942 | PJM | 200011 | 10 | 500 | 235118 | 10 | 500 |  | Intra-Regional Line
136150 | 149001 | PJM | 200568 | 10 | 230 | 200600 | 10 | 345 | xfr | Intra-Regional Line
136150 | 149001 | PJM | 200599 | 10 | 345 | 200600 | 10 | 345 |  | Intra-Regional Line
130756 | 135398 | PJM | 200599 | 10 | 345 | 238547 | 10 | 345 |  | Intra-Regional Line
130757 | 200930 | PJM | 200654 | 10 | 230 | 903645 | 10 | 230 |  | Intra-Regional Line
130763 | 200675 | PJM | 200675 | 10 | 230 | 200924 | 10 | 230 |  | Intra-Regional Line
|  | PJM | 200706 | 10 | 230 | 200708 | 10 | 230 |  | Intra-Regional Line
PJM |  | PJM | 200706 | 10 | 230 | 200924 | 10 | 230 |  | Intra-Regional Line
200004 | 200013 | PJM | 200708 | 10 | 230 | 208009 | 10 | 230 |  | Intra-Regional Line
200004 | 200013 | PJM | 200767 | 10 | 230 | 200795 | 10 | 230 |  | Intra-Regional Line
314686 | 314697 | PJM | 200795 | 10 | 230 | 200810 | 10 | 230 |  | Intra-Regional Line
304070 | 314697 | PJM | 200819 | 10 | 230 | 200928 | 10 | 230 |  | Intra-Regional Line
200003 | 200004 | PJM | 200927 | 10 | 115 | 200928 | 10 | 230 | xfr | Intra-Regional Line
200003 | 200004 | PJM | 200928 | 10 | 230 | 903645 | 10 | 230 |  | Intra-Regional Line
242514 | 242520 | PJM | 235105 | 10 | 500 | 314925 | 345 | 500 |  | Intra-Regional Line
242514 | 242520 | PJM | 238544 | 10 | 138 | 239082 | 10 | 345 | xfr | Intra-Regional Line
304451 | 314574 | PJM | 238547 | 10 | 345 | 239082 | 10 | 345 |  | Intra-Regional Line
200011 | 235104 | PJM | 242508 | 10 | 765 | 242513 | 10 | 765 |  | Intra-Regional Line
242513 | 242517 | PJM | 242510 | 10 | 765 | 242511 | 10 | 765 |  | Intra-Regional Line
304070 | 314697 | PJM | 242511 | 10 | 765 | 242518 | 10 | 500 | xfr | Intra-Regional Line
242511 | 242518 | PJM | 242513 | 10 | 765 | 242517 | 10 | 765 |  | Intra-Regional Line
200927 | 200928 | PJM | 242514 | 10 | 765 | 242520 | 10 | 500 | xfr | Intra-Regional Line
238544 | 239082 | PJM | 242518 | 10 | 500 | 360106 | 347 | 500 |  | Regional Tie Line
314569 | 314574 | PJM | 242520 | 10 | 500 | 306719 | 342 | 500 |  | Regional Tie Line
242520 | 306719 | PJM | 304070 | 340 | 230 | 314697 | 345 | 230 |  | Regional Tie Line
135251 | 200654 | PJM | 304183 | 340 | 500 | 314935 | 345 | 500 |  | Regional Tie Line
242511 | 242518 | PJM | 304451 | 340 | 230 | 314574 | 345 | 230 |  | Regional Tie Line
242518 | 360106 | PJM | 314569 | 345 | 230 | 314574 | 345 | 230 |  | Intra-Regional Line
200928 | 903645 | PJM | 314686 | 345 | 230 | 314697 | 345 | 230 |  | Intra-Regional Line
200654 | 903645 | PJM | 314903 | 345 | 500 | 314924 | 345 | 500 |  | Intra-Regional Line
135251 | 200654 | PJM | 314914 | 345 | 500 | 314918 | 345 | 500 |  | Intra-Regional Line
200928 | 903645 | PJM | 342835 | 10 | 345 | 342838 | 10 | 345 |  | Intra-Regional Line
200654 | 903645 |  | From Bus | Area | kV | To Bus | Area | kV
242520 | 306719 | Non-RTO SERC | 242518 | 10 | 500 | 360106 | 347 | 500 |  | Regional Tie Line
200819 | 200928 | Non-RTO SERC | 242520 | 10 | 500 | 306719 | 342 | 500 |  | Regional Tie Line
200706 | 200708 | Non-RTO SERC | 304070 | 340 | 230 | 314697 | 345 | 230 |  | Regional Tie Line
200706 | 200708 | Non-RTO SERC | 304183 | 340 | 500 | 314935 | 345 | 500 |  | Regional Tie Line
314686 | 314697 | Non-RTO SERC | 304451 | 340 | 230 | 314574 | 345 | 230 |  | Regional Tie Line
200708 | 208009 | Non-RTO SERC | 306007 | 342 | 230 | 306008 | 342 | 500 | xfr | Intra-Regional Line
200708 | 208009 | Non-RTO SERC | 306008 | 342 | 500 | 309002 | 342 | 500 |  | Intra-Regional Line
200767 | 200795 | Non-RTO SERC | 306008 | 342 | 500 | 380011 | 346 | 500 |  | Intra-Regional Line
200819 | 200928 | Non-RTO SERC | 306113 | 342 | 500 | 309002 | 342 | 500 |  | Intra-Regional Line
242510 | 242511 | Non-RTO SERC | 306337 | 342 | 500 | 306546 | 342 | 500 |  | Intra-Regional Line
242518 | 360106 | Non-RTO SERC | 306540 | 342 | 230 | 306546 | 342 | 500 | xfr | Intra-Regional Line
200706 | 200924 | Non-RTO SERC | 306712 | 342 | 230 | 306716 | 342 | 230 |  | Intra-Regional Line
200675 | 200924 | Non-RTO SERC | 306712 | 342 | 230 | 306716 | 342 | 230 |  | Intra-Regional Line
200706 | 200924 | Non-RTO SERC | 324072 | 363 | 500 | 324073 | 363 | 500 |  | Intra-Regional Line
200011 | 235118 | Non-RTO SERC | 324072 | 363 | 500 | 324112 | 363 | 345 | xfr | Intra-Regional Line
235105 | 314925 | Non-RTO SERC | 324073 | 363 | 500 | 360102 | 347 | 500 |  | Intra-Regional Line
130763 | 200675 | Non-RTO SERC | 324100 | 363 | 345 | 324102 | 363 | 345 |  | Intra-Regional Line
200675 | 200924 | Non-RTO SERC | 336562 | 326 | 500 | 336839 | 326 | 500 |  | Intra-Regional Line
200767 | 200795 | Non-RTO SERC | 340624 | 314 | 161 | 360043 | 347 | 161 |  | Regional Tie Line
342835 | 342838 | Non-RTO SERC | 346992 | 357 | 345 | 360002 | 347 | 345 |  | Regional Tie Line
200795 | 200810 | Non-RTO SERC | 360001 | 347 | 500 | 360002 | 347 | 345 | xfr | Intra-Regional Line
242508 | 242513 | Non-RTO SERC | 360001 | 347 | 500 | 360015 | 347 | 500 |  | Intra-Regional Line
135398 | 200942 | Non-RTO SERC | 360015 | 347 | 500 | 360016 | 347 | 161 | xfr | Intra-Regional Line
130757 | 200930 | Non-RTO SERC | 360015 | 347 | 500 | 360040 | 347 | 500 |  | Intra-Regional Line
314903 | 314924 | Non-RTO SERC | 360065 | 347 | 500 | 360081 | 347 | 500 |  | Intra-Regional Line
304183 | 314935 | Non-RTO SERC | 360081 | 347 | 500 | 360085 | 347 | 500 |  | Intra-Regional Line
200568 | 200600 | Non-RTO SERC | 360081 | 347 | 500 | 360110 | 347 | 500 |  | Intra-Regional Line
242513 | 242517 | Non-RTO SERC | 360081 | 347 | 500 | 360662 | 347 | 500 |  | Intra-Regional Line
135398 | 200942 | Non-RTO SERC | 360085 | 347 | 500 | 360110 | 347 | 500 |  | Intra-Regional Line
200599 | 238547 | Non-RTO SERC | 360097 | 347 | 500 | 360102 | 347 | 500 |  | Intra-Regional Line
314914 | 314918 | Non-RTO SERC | 360662 | 347 | 500 | 382499 | 346 | 500 |  | Intra-Regional Line
200599 | 200600 | Non-RTO SERC | 380003 | 346 | 500 | 380011 | 346 | 500 |  | Intra-Regional Line
238547 | 239082 | Non-RTO SERC | 380011 | 346 | 500 | 382035 | 346 | 230 | xfr | Intra-Regional Line
130757 | 200930 | Non-RTO SERC | 380013 | 346 | 500 | 380018 | 346 | 500 |  | Intra-Regional Line
130763 | 200675 | Non-RTO SERC | 380014 | 346 | 500 | 400356 | 401 | 500 |  | Regional Tie Line
200795 | 200810 | Non-RTO SERC | 380015 | 346 | 500 | 400356 | 401 | 500 |  | Regional Tie Line
|  | Non-RTO SERC | 380021 | 346 | 500 | 382499 | 346 | 500 |  | Intra-Regional Line
SERC |  | Non-RTO SERC | 380025 | 346 | 500 | 380088 | 346 | 230 | xfr | Intra-Regional Line
340624 | 360043 | Non-RTO SERC | 382035 | 346 | 230 | 382766 | 346 | 230 |  | Intra-Regional Line
304070 | 314697 |  | From Bus | Area | kV | To Bus | Area | kV
340624 | 360043 | SPP | 532772 | 536 | 345 | 542982 | 541 | 345 |  | Intra-Regional Line
306008 | 380011
324072 | 324112
304451 | 314574
304070 | 314697
380011 | 382035
306337 | 306546
306008 | 380011
242520 | 306719
242518 | 360106
324100 | 324102
306008 | 309002
242520 | 306719
306712 | 306716
360081 | 360662
306712 | 306716
306007 | 306008
360015 | 360040
242518 | 360106
360662 | 382499
360001 | 360015
306540 | 306546
360081 | 360085
380021 | 382499
324072 | 324073
360085 | 360110
380003 | 380011
360065 | 360081
380025 | 380088
306113 | 309002
380015 | 400356
360015 | 360040
306008 | 309002
306337 | 306546
336562 | 336839
324073 | 360102
346992 | 360002
380014 | 400356
346992 | 360002
360097 | 360102
304183 | 314935
306113 | 309002
360001 | 360015
360001 | 360002
360015 | 360016
360081 | 360662
360081 | 360110
380013 | 380018
360662 | 382499
360015 | 360016
382035 | 382766
SPP
532772 | 542982

## CODE
#Find Area of a list of busses:
######################################################
Bus = [[380015,400356],[380014,400356]]
region = "FRCC"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################
Bus = [
[300038,344974,],
[300041,344154,],
[300041,344327,],
[336562,336839,],
[340624,360043,],
[344224,344327,],
[344974,345773,],
[345667,345668,],
[346895,348151,],
[346992,348827,],
[346992,360002,],
[347830,348493,],
[348493,348827,]]
region = "MISO"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################
Bus = [
[130753,130755,],
[130755,130757,],
[130755,130839,],
[130755,131157,],
[130756,135398,],
[130757,130768,],
[130757,200930,],
[130762,130767,],
[130762,135413,],
[130763,200675,],
[130768,130876,],
[131157,136153,],
[135250,135251,],
[135250,135413,],
[135250,146000,],
[135251,200654,],
[135398,200942,],
[135413,146000,],
[135415,147842,],
[135415,147842,],
[136150,149001,],
[136150,149001,]]
region = "NPCC"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################
Bus = [
[130757,200930,],
[130763,200675,],
[135251,200654,],
[135398,200942,],
[200003,200004,],
[200004,200013,],
[200011,235104,],
[200011,235118,],
[200568,200600,],
[200599,200600,],
[200599,238547,],
[200654,903645,],
[200675,200924,],
[200706,200708,],
[200706,200924,],
[200708,208009,],
[200767,200795,],
[200767,B$0211,],
[200767,B$0411,],
[200769,B$0211,],
[200769,B$0411,],
[200795,200810,],
[200819,200928,],
[200927,200928,],
[200928,903645,],
[235105,314925,],
[238544,239082,],
[238547,239082,],
[242508,242513,],
[242510,242511,],
[242511,242518,],
[242513,242517,],
[242514,242520,],
[242518,360106,],
[242520,306719,],
[304070,314697,],
[304183,314935,],
[304451,314574,],
[314569,314574,],
[314686,314697,],
[314903,314924,],
[314914,314918,],
[342835,342838,]]
region = "PJM"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################
Bus = [
[242518,360106,],
[242520,306719,],
[304070,314697,],
[304183,314935,],
[304451,314574,],
[306007,306008,],
[306008,309002,],
[306008,380011,],
[306113,309002,],
[306337,306546,],
[306540,306546,],
[306712,306716,],
[306712,306716,],
[324072,324073,],
[324072,324112,],
[324073,360102,],
[324100,324102,],
[336562,336839,],
[340624,360043,],
[346992,360002,],
[360001,360002,],
[360001,360015,],
[360015,360016,],
[360015,360040,],
[360065,360081,],
[360081,360085,],
[360081,360110,],
[360081,360662,],
[360085,360110,],
[360097,360102,],
[360662,382499,],
[380003,380011,],
[380011,382035,],
[380013,380018,],
[380014,400356,],
[380015,400356,],
[380021,382499,],
[380025,380088,],
[382035,382766,]]
region = "Non-RTO SERC"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################
Bus = [[532772,542982]]
region = "SPP"
print " From Bus Area kV To Bus Area kV"
for (fb, tb) in Bus:
ierr, fromArea = psspy.busint(fb,'AREA')
ierr, fromkV = psspy.busdat(fb,'BASE')
ierr, toArea = psspy.busint(tb,'AREA')
ierr, tokV = psspy.busdat(tb,'BASE')
print region,str(fb).rjust(8), str(fromArea).rjust(5), str(fromkV).rjust(6), str(tb).rjust(8), str(toArea).rjust(5), str(tokV).rjust(6)
fromBus = []
toBus = []
######################################################

## AREAS
Source |  | Area
10 | Source | PJM
101 | Source | NPCC
102 | Source | NPCC
103 | Source | NPCC
104 | Source | NPCC
105 | Source | NPCC
106 | Source | NPCC
107 | Source | NPCC
207 | Source | MISO
208 | Source | MISO
210 | Source | MISO
216 | Source | MISO
217 | Source | MISO
218 | Source | MISO
219 | Source | MISO
295 | Source | MISO
314 | Source | MISO
333 | Source | MISO
345 | Source | PJM
356 | Source | MISO
357 | Source | MISO
360 | Source | MISO
361 | Source | MISO
363 | Source | SERC_NON-MISO
600 | Source | MISO
608 | Source | MISO
613 | Source | MISO
615 | Source | MISO
620 | Source | MISO
627 | Source | MISO
633 | Source | MISO
635 | Source | MISO
652 | Source | MISO
661 | Source | MISO
667 | Source | MISO
680 | Source | MISO
694 | Source | MISO
696 | Source | MISO
697 | Source | MISO
698 | Source | MISO
326 | Sink | MISO
327 | Sink | MISO
328 | Sink | MISO
329 | Sink | MISO
331 | Sink | MISO
332 | Sink | MISO
334 | Sink | MISO
335 | Sink | MISO
336 | Sink | MISO
337 | Sink | MISO
338 | Sink | MISO
339 | Sink | MISO
340 | Sink | SERC_NON-MISO
341 | Sink | SERC_NON-MISO
342 | Sink | SERC_NON-MISO
343 | Sink | SERC_NON-MISO
344 | Sink | SERC_NON-MISO
346 | Sink | SERC_NON-MISO
347 | Sink | SERC_NON-MISO
349 | Sink | MISO
350 | Sink | SERC_NON-MISO
351 | Sink | MISO
352 | Sink | SERC_NON-MISO
362 | Sink | SERC_NON-MISO
365 | Sink | SERC_NON-MISO
366 | Sink | SERC_NON-MISO
401 | Sink | FRCC
402 | Sink | FRCC
403 | Sink | FRCC
404 | Sink | FRCC
405 | Sink | FRCC
406 | Sink | FRCC
407 | Sink | FRCC
409 | Sink | FRCC
410 | Sink | FRCC
411 | Sink | FRCC
412 | Sink | FRCC
415 | Sink | FRCC
416 | Sink | FRCC
417 | Sink | FRCC
419 | Sink | FRCC
502 | Sink | MISO
503 | Sink | MISO
504 | Sink | MISO
515 | Sink | SPP-NON-MISO
520 | Sink | SPP-NON-MISO
523 | Sink | SPP-NON-MISO
524 | Sink | SPP-NON-MISO
525 | Sink | SPP-NON-MISO
526 | Sink | SPP-NON-MISO
527 | Sink | SPP-NON-MISO
531 | Sink | SPP-NON-MISO
534 | Sink | SPP-NON-MISO
536 | Sink | SPP-NON-MISO
540 | Sink | SPP-NON-MISO
541 | Sink | SPP-NON-MISO
542 | Sink | SPP-NON-MISO
544 | Sink | SPP-NON-MISO
545 | Sink | SPP-NON-MISO
546 | Sink | SPP-NON-MISO
640 | Sink | SPP-NON-MISO
645 | Sink | SPP-NON-MISO
650 | Sink | SPP-NON-MISO